{"text_format":"1","workbook":"xlsx","n_sheets":36,"sheets":["Read Me","Disclaimer","User Guide","Job Input","Design Input","% Touch Voltage","Soil Depth Factor","Publish Report","Data Entered","Title Page","Report Disclaimer","Report","Source-Num","Source-Name","Source-SWE-Num","Source-SWE-Name","Source-SWA-Num","Source-SWA-Name","Source-EM-Num","Source-EM-Name","Source-WM-Num","Source-WM-Name","Data-General","Data-HV Electrode Resistance","Data-LV Electrode Resistance","Data-Network Contribution","Data-HV to LV Separation SNE","Data-HV to LV Separation CNE","Data-Safety Voltages","Transfer Potential Default","Data-Transfer Voltages","Calculations-Fault Current","Simple Calcs - Fault Current","Ground Current Default","Calculations-IDMT Op Time","Calculations-Surface Area"],"not_rendered":{"charts":0,"images":20,"macros":1,"external_links":0,"defined_names":19,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Read Me","index":0,"n_rows":18,"n_cols":2,"rows_kept":18,"cut":false,"hidden":false,"merged":[[17,1,18,6],[6,0,6,7],[8,1,8,6],[10,1,10,6],[12,1,12,6],[14,1,15,6]]}
[]
[]
[]
[]
[]
[]
["GUIDANCE ON USING THIS CALCULATION TOOL"]
[]
[1,"Complete the 'Job Input' and 'Design Input' tabs."]
[]
[2,"Data should be entered into blue shaded cells only."]
[]
[3,"Resolve any red error messages that may appear."]
[]
[4,"On the 'Publish Report' tab - check there are no outstanding error messages and click on the 'Publish Report' button. "]
[]
[]
[5,"The 'Earthing Report' will be published in pdf format in the same folder as this Excel spreadsheet. "]

{"sheet":"Disclaimer","index":1,"n_rows":50,"n_cols":5,"rows_kept":50,"cut":false,"hidden":false,"merged":[[46,1,46,3],[49,0,49,7],[1,0,1,7],[3,1,5,6],[7,1,9,6],[11,1,12,6],[14,1,15,6],[17,1,22,6],[46,4,46,6]]}
[]
["DISCLAIMER"]
[]
[null,"This spreadsheet calculation tool (Excel Workbook) has been prepared in order to analyse the performance of a proposed earthing system without having to employ specialist consultants or advanced earthing software packages."]
[]
[]
[]
[null,"The tool uses data derived from CDEGS studies of the proposed substation arrangement. It also uses the formulae and guidelines contained within ENA Engineering Recommendation S34 and ENA Technical Specification 41-24."]
[]
[]
[]
[null,"[CDEGS is \"Current Distribution Electromagnetic Interference Grounding and Soil Structure Analysis\" software from Safe Engineering Services & Technologies Ltd]"]
[]
[]
[null,"This spreadsheet calculation tool has been prepared for use on the National Grid Electricity Distribution (NGED) network only. "]
[]
[]
[null,"The spreadsheet calculation tool and the associated data and calculations are provided \"as is\" and for use at your own risk. NGED makes no warranties as to performance, fitness for purpose, or any other warranties, whether expressed or implied. Under no circumstances will NGED be liable for direct, indirect, special, incidental, or consequential damages resulting from the use, misuse, or inability to use the spreadsheet calculation tool and the data and calculations. "]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"This spreadsheet calculation tool is:",null,null,{"$f":"'Data-General'!A2","v":"TP21G_EDT_VERSION 2b"}]
[]
[]
["© National Grid Electricity Distribution 2022"]

{"sheet":"User Guide","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[[0,0,24,8]]}

{"sheet":"Job Input","index":3,"n_rows":36,"n_cols":2,"rows_kept":36,"cut":false,"hidden":false,"merged":[[28,1,28,5],[33,1,34,5],[3,1,3,5],[8,1,8,5],[13,1,13,5],[18,1,18,5],[23,1,23,5]]}
[]
[null,"Select whether this is a NGED or ICP designed project"]
[]
["Job Input 1"]
[null,{"$f":"IF('Data Entered'!B2=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,{"$f":"IF('Data Entered'!B2=\"ICP\",\"Enter the name of the ICP Designer\",\"Enter the name of the NGED Designer\")","v":"Enter the name of the NGED Designer"}]
[]
["Job Input 2"]
[null,{"$f":"IF('Data Entered'!B3=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,{"$f":"IF('Data Entered'!B2=\"ICP\",\"Enter the name of the ICP\",\"Enter the MU of the NGED Designer\")","v":"Enter the MU of the NGED Designer"}]
[]
["Job Input 3"]
[null,{"$f":"IF('Data Entered'!B4=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,{"$f":"IF('Data Entered'!B2=\"ICP\",\"Enter the ICP Job Reference Number\",\"Enter the NGED CROWN Enquiry Number\")","v":"Enter the NGED CROWN Enquiry Number"}]
[]
["Job Input 4"]
[null,{"$f":"IF('Data Entered'!B5=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,"Select the NGED distribution licence area"]
[]
["Job Input 5"]
[null,{"$f":"IF('Data Entered'!B6=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,"Enter the name of the ground-mounted distribution substation"]
[]
["Job Input 6"]
[null,{"$f":"IF('Data Entered'!B7=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,"Enter the site address of the ground-mounted distribution substation"]
[]
["Job Input 7"]
[]
[null,{"$f":"IF('Data Entered'!B8=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]

{"sheet":"Design Input","index":4,"n_rows":560,"n_cols":12,"rows_kept":560,"cut":false,"hidden":false,"merged":[[549,1,549,7],[177,1,177,7],[213,1,213,7],[246,1,246,7],[322,1,322,7],[334,1,334,7],[363,1,363,7],[401,1,401,7],[413,1,413,7],[424,1,424,7],[273,1,273,5],[271,1,271,2],[271,3,271,5],[272,1,272,2],[272,3,272,5],[287,1,287,7],[314,1,314,3],[315,1,315,3],[316,1,316,3],[277,1,277,2],[277,3,277,5],[278,1,278,2],[278,3,278,5],[279,1,279,5],[130,7,131,8],[110,0,113,0],[390,1,390,2],[391,1,391,2],[392,1,392,2],[390,3,390,5],[391,3,391,5],[392,3,392,5],[393,1,393,5],[384,1,384,2],[385,1,385,2],[386,1,386,5],[380,3,380,5],[381,3,381,5],[382,3,382,5],[383,3,383,5],[384,3,384,5],[385,3,385,5],[181,2,181,3],[181,4,181,5],[188,1,188,4],[190,1,190,4],[192,1,192,4],[380,1,380,2],[163,1,163,4],[24,1,24,2],[39,1,39,3],[44,1,44,3],[10,1,10,4],[17,1,17,4],[5,1,5,4],[1,1,1,7],[13,1,13,7],[20,1,20,7],[143,1,143,2],[143,3,143,6],[142,1,142,2],[142,3,142,6],[99,2,99,3],[132,7,132,8],[117,3,117,4],[118,3,118,4],[126,3,126,4],[127,3,127,4],[128,3,128,4],[129,3,129,4],[130,3,130,4],[131,3,131,4],[118,0,132,0],[151,1,151,4],[152,1,152,4],[150,1,150,4],[162,1,162,4],[145,1,145,2],[145,3,145,6],[144,1,144,2],[144,3,144,6],[132,3,132,4],[119,3,119,4],[120,3,120,4],[121,3,121,4],[122,3,122,4],[123,3,123,4],[124,3,124,4],[125,3,125,4],[270,1,270,2],[270,3,270,5],[168,0,169,0],[168,1,168,2],[169,1,169,2],[174,1,174,3],[268,1,268,2],[268,3,268,5],[269,1,269,2],[269,3,269,5],[546,1,546,6],[496,1,496,4],[497,1,497,4],[498,1,498,4],[487,1,487,7],[318,1,318,3],[348,1,348,3],[543,1,543,6],[537,1,537,6],[538,1,538,6],[540,1,540,6],[382,1,382,2],[474,1,474,4],[475,1,475,4],[476,1,476,4],[436,1,436,3],[437,1,437,3],[444,1,444,2],[464,1,464,4],[465,1,465,4],[467,1,467,4],[447,1,447,7],[438,1,438,3],[439,1,439,3],[355,1,355,3],[435,1,435,3],[545,1,545,6],[541,1,541,6],[539,1,539,6],[542,1,542,6],[544,1,544,6],[466,1,466,4],[468,1,468,4],[512,1,512,7],[508,1,508,6],[381,1,381,2],[509,1,509,6],[451,3,451,7],[453,3,454,7],[459,3,459,7],[456,3,457,7],[99,0,103,0],[483,1,483,4],[482,1,482,4],[484,1,484,4],[361,6,361,7],[445,6,445,7],[222,3,223,7],[319,7,319,8],[320,7,320,9],[332,6,332,7],[317,1,317,3],[383,1,383,2],[434,1,434,3],[418,1,418,3],[419,1,419,3],[420,1,420,3],[421,1,421,3],[348,0,355,0],[349,1,349,3],[350,1,350,3],[351,1,351,3],[352,1,352,3],[353,1,353,3],[354,1,354,3]]}
[]
[null,"SUBSTATION FORMAT     [DESIGN STEP A]"]
[]
[null,"Substation format"]
[]
["Design Input 0",null,null,null,null,null,{"$f":"CONCATENATE(\"Standard Earthing Design = TP21G-\",'Data Entered'!E10)","v":"Standard Earthing Design = TP21G-0"},null,null,null,{"$f":"IF(OR('Data Entered'!E10=\"A\",'Data Entered'!E10=\"C\",'Data Entered'!E10=\"E\",'Data Entered'!E10=\"G\"),\"YES\",\"NO\")","v":"NO"},"Freestanding?"]
[null,{"$f":"IF('Data Entered'!B10=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"},null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!G10","v":"YES"},"LV?"]
[]
[null,"Is the ground mounted distribution substation a special design?"]
[]
["Design Input 1"]
[null,{"$f":"IF('Data Entered'!B11=0,\"**Compulsory Field**\",IF('Data Entered'!B11=\"NO\",\"\",\"This earthing design tool is NOT appropriate for a special design\"))","v":"**Compulsory Field**"}]
[]
[null,"PRELIMINARY ASSESSMENT     [DESIGN STEP B]"]
[]
[null,"Is the ground mounted distribution substation within 20m of a problematic location?"]
[null,null,null,null,null,null,{"$f":"IF('Data Entered'!B12=\"NO\",\"\",\"Employ Earthing Specialist to carry out design if\")","v":"Employ Earthing Specialist to carry out design if"}]
["Design Input 2",null,null,null,null,null,{"$f":"IF('Data Entered'!B12=\"NO\",\"\",\"actual separation distance does not exceed\")","v":"actual separation distance does not exceed"}]
[null,{"$f":"IF('Data Entered'!B12=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"},null,null,null,null,{"$f":"IF('Data Entered'!B12=\"NO\",\"\",\"minimum permitted by at least 5m\")","v":"minimum permitted by at least 5m"}]
[]
[null,"NETWORK DATA     [DESIGN STEP C]"]
[]
[null,"Select methodology?"]
[]
["Design Input 3","Basic"]
[null,{"$f":"IF('Data Entered'!B13=0,\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Select the system voltage"]
[]
["Design Input 4",null,"V"]
[null,{"$f":"IF('Data Entered'!B14=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,"Select method for identifying the source substation"]
[]
["Design Input 5"]
[null,{"$f":"IF(ISBLANK(B35),\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,{"$f":"IF(B35=\"By Name\",\"Select the source substation name from the dropdown list (DO NOT TYPE THE NAME IN)\",IF(B35=\"By Number\",\"Select the source substation number from the dropdown list (DO NOT TYPE THE NUMBER IN)\",\"Select the source substation from the dropdown list\"))","v":"Select the source substation from the dropdown list"}]
[]
["Design Input 6"]
[null,{"$f":"IF(ISBLANK(B40),\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,{"$f":"IF(B35=\"By Name\",\"Source substation number\",IF(B35=\"By Number\",\"Source substation name\",\"Source substation\"))","v":"Source substation"}]
[]
[null,{"$f":"'Data Entered'!D16","v":{"$error":"#N/A"}}]
[]
[]
[null,"Earthing system impedance of source substation (RSOURCE)"]
[]
[null,{"$f":"'Data Entered'!B17","v":0.1},"Ω",{"$f":"IF('Data Entered'!D17=\"Y\",\"Assumed Value\",\"\")","v":{"$error":"#N/A"}}]
[]
[]
[null,"Modify earthing system impedance of source substation?"]
[]
["Design Input 7","NO",null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!B18","v":"NO"},"Modify impedance?"]
[null,{"$f":"IF(AND(ISBLANK(B55),OR('Data Entered'!B13=\"Intermediate\",'Data Entered'!B13=\"Advanced - Fault Level Study\")),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Enter modified earthing system impedance of source substation"]
[]
["Design Input 7A",{"$f":"B50","v":0.1},"Ω"]
[null,{"$f":"IF(AND('Data Entered'!B18=\"YES\",ISBLANK(B60)),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Earth potential rise of source substation"]
[]
[null,{"$f":"'Data Entered'!B19","v":3000},"V",{"$f":"IF('Data Entered'!D19=\"Y\",\"Assumed Value\",\"\")","v":{"$error":"#N/A"}}]
[null,{"$f":"IF(AND('Data Entered'!B48=\"YES\",ISBLANK(B65)),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Modify earth potential rise of source substation?"]
[]
["Design Input 8","NO",null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!B20","v":"NO"},"Modify source EPR?"]
[null,{"$f":"IF(AND(ISBLANK(B70),OR('Data Entered'!B13=\"Intermediate\",'Data Entered'!B13=\"Advanced - Fault Level Study\")),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Enter modified earthing potential rise of source substation"]
[]
["Design Input 8A",{"$f":"B65","v":3000},"V"]
[null,{"$f":"IF(AND('Data Entered'!B20=\"YES\",ISBLANK(B75)),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Clearance time for a 33kV / 66kV / 132kV / 275kV / 400kV fault at source substation"]
[]
[null,{"$f":"'Data Entered'!B21","v":3},"s",{"$f":"IF('Data Entered'!D21=\"Y\",\"Assumed Value\",\"\")","v":{"$error":"#N/A"}}]
[]
[]
[null,"Modify clearance time for a 33kV / 66kV / 132kV / 275kV / 400kV fault at source substation?"]
[]
["Design Input 9","NO",null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!B22","v":"NO"},"Modify clearance time?"]
[null,{"$f":"IF(AND(ISBLANK(B85),OR('Data Entered'!B13=\"Intermediate\",'Data Entered'!B13=\"Advanced - Fault Level Study\")),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Enter modified clearance time for a 33kV / 66kV / 132kV / 275kV / 400kV fault at source substation"]
[]
["Design Input 9A",{"$f":"B80","v":3},"s"]
[null,{"$f":"IF(AND('Data Entered'!B22=\"YES\",ISBLANK(B90)),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"33kV / 66kV / 132kV / 275kV / 400kV fault at source substation cleared by INST, IDMT, or DT earth fault protection?"]
[]
["Design Input 10"]
[null,{"$f":"IF(AND(ISBLANK(B95),OR('Data Entered'!B13=\"Intermediate\",'Data Entered'!B13=\"Advanced - Fault Level Study\")),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Enter the network impedance up to the HV terminals of the ground mounted distribution substation"]
[]
["Design Input 11",null,null,null,"Unit of measurement"]
[null,null,"R","X"]
[null,"Z1",null,null,{"$f":"'Data Entered'!B24","v":0}]
[null,"Z2",null,null,{"$f":"'Data Entered'!B24","v":0}]
[null,"Z0",null,null,{"$f":"'Data Entered'!B24","v":0}]
[null,null,{"$f":"IF(AND('Data Entered'!B13=\"Advanced - Fault Level Study\",OR(ISBLANK(C100),ISBLANK(C102),ISBLANK(C103),ISBLANK(C104),ISBLANK(D102),ISBLANK(D103),ISBLANK(D104))),\"**Compulsory Fields**\",\"\")","v":""}]
[]
[null,"Enter the source substation neutral earthing details"]
[null,null,"TYPE","RATING"]
["Design Input 12","Neutral Earthing",null,{"$f":"IF(ISBLANK(C109),\"\",IF(C109=\"Solid\",3500,IF(C109=\"Resistor\",2000,2400)))","v":""},"A"]
[null,null,{"$f":"IF(AND('Data Entered'!B13=\"Basic\",ISBLANK(C109)),\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
["Design Input 12","NER 1",null,null,"A","Set rating to \"3500\" if type is selected to \"Solid\""]
[null,"NER 2",null,null,"A"]
[null,"NER 3",null,null,"A"]
[null,"NER 4",null,null,"A"]
[null,null,{"$f":"IF(AND('Data Entered'!B13=\"Intermediate\",OR(ISBLANK(C111),ISBLANK(D111))),\"**Compulsory Fields: NER 1**\",\"\")","v":""}]
[]
[null,"Enter the HV circuit details"]
[null,"Source S/S","SECTION","CABLE / LINE TYPE",null,"LENGTH"]
["Design Input 13",null,1,null,null,null,"km",{"$f":"IF(AND(ISBLANK(D119),ISBLANK(D120),ISBLANK(D121),ISBLANK(D122),ISBLANK(D123),ISBLANK(D124),ISBLANK(D125),ISBLANK(D126),ISBLANK(D127),ISBLANK(D128),ISBLANK(D129),ISBLANK(D130),ISBLANK(D131),ISBLANK(D132),ISBLANK(D133)),\"**No cable / line types entered**\",\"\")","v":"**No cable / line types entered**"}]
[null,null,2,null,null,null,"km"]
[null,null,3,null,null,null,"km",{"$f":"IF('Data Entered'!H35=\"TRUE\",\"**No cable connected to GM Dist S/S**\",\"\")","v":"**No cable connected to GM Dist S/S**"}]
[null,null,4,null,null,null,"km"]
[null,null,5,null,null,null,"km",{"$f":"IF(OR(AND(ISTEXT(D119),ISBLANK(F119)),AND(ISTEXT(D120),ISBLANK(F120)),AND(ISTEXT(D121),ISBLANK(F121)),AND(ISTEXT(D122),ISBLANK(F122)),AND(ISTEXT(D123),ISBLANK(F123)),AND(ISTEXT(D124),ISBLANK(F124)),AND(ISTEXT(D125),ISBLANK(F125)),AND(ISTEXT(D126),ISBLANK(F126)),AND(ISTEXT(D127),ISBLANK(F127)),AND(ISTEXT(D128),ISBLANK(F128)),AND(ISTEXT(D129),ISBLANK(F129)),AND(ISTEXT(D130),ISBLANK(F130)),AND(ISTEXT(D131),ISBLANK(F131)),AND(ISTEXT(D132),ISBLANK(F132)),AND(ISTEXT(D133),ISBLANK(F133))),\"**Length value(s) missing**\",\"\")","v":""}]
[null,null,6,null,null,null,"km"]
[null,null,7,null,null,null,"km",{"$f":"IF(OR(AND(ISNUMBER(F119),ISBLANK(D119)),AND(ISNUMBER(F120),ISBLANK(D120)),AND(ISNUMBER(F121),ISBLANK(D121)),AND(ISNUMBER(F122),ISBLANK(D122)),AND(ISNUMBER(F123),ISBLANK(D123)),AND(ISNUMBER(F124),ISBLANK(D124)),AND(ISNUMBER(F125),ISBLANK(D125)),AND(ISNUMBER(F126),ISBLANK(D126)),AND(ISNUMBER(F127),ISBLANK(D127)),AND(ISNUMBER(F128),ISBLANK(D128)),AND(ISNUMBER(F129),ISBLANK(D129)),AND(ISNUMBER(F130),ISBLANK(D130)),AND(ISNUMBER(F131),ISBLANK(D131)),AND(ISNUMBER(F132),ISBLANK(D132)),AND(ISNUMBER(F133),ISBLANK(D133))),\"**Cable / line type value(s) missing**\",\"\")","v":""}]
[null,null,8,null,null,null,"km"]
[null,null,9,null,null,null,"km"]
[null,null,10,null,null,null,"km"]
[null,null,11,null,null,null,"km"]
[null,null,12,null,null,null,"km"]
[null,null,13,null,null,null,"km","Length Of HV Cable Connected To Ground Mounted Distribution S/S"]
[null,null,14,null,null,null,"km"]
[null,null,15,null,null,null,"km",{"$f":"CONCATENATE('Data Entered'!H36,\" km\")","v":"0 km"}]
[null,"Ground Mounted Distribution S/S",null,{"$f":"IF(AND(OR('Data Entered'!B13=\"Basic\",'Data Entered'!B13=\"Intermediate\"),OR(LEFT(H119,2)=\"**\",LEFT(H121,2)=\"**\",LEFT(H123,2)=\"**\",LEFT(H125,2)=\"**\")),\"**Compulsory Fields**\",\"\")","v":"**Compulsory Fields**"}]
[]
[null,"Is the ground mounted distribution substation cable connected ALL THE WAY to the source substation under normal feeding conditions?"]
[]
["Design Input 14",null,null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!B48","v":"YES"},"Cable connected?"]
[null,{"$f":"IF(AND(OR('Data Entered'!B13=\"Advanced - ASC Earthing\",'Data Entered'!B13=\"Advanced - Fault Level Study\"),ISBLANK(B138)),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,{"$f":"IF('Data Entered'!B48=\"YES\",\"Enter details of the predominant HV cable from the ground mounted distribution substation back to the source substation\",IF(OR('Data Entered'!B48=\"NO\",'Data Entered'!B48=0),\"Enter details of the predominant HV cable from the ground mounted distribution substation back to the pole termination\",\"Enter details of the predominant HV cable\"))","v":"Enter details of the predominant HV cable from the ground mounted distribution substation back to the source substation"}]
[]
[null,"GM distribution s/s connection",null,{"$f":"'Data Entered'!B49","v":"All Cable"}]
[null,"Total cable length",null,{"$f":"'Data Entered'!H36","v":0},null,null,null,"km"]
[null,"Total cable length",null,null,null,null,null,"km"]
["Design Input 15","Predominant cable type"]
[null,{"$f":"IF(OR('Data Entered'!B50=0,'Data Entered'!B51=0),\"**Compulsory Fields**\",\"\")","v":"**Compulsory Fields**"},null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Basic\",'Data Entered'!H34=TRUE),AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!H34=TRUE),'Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B13=\"Advanced - ASC Earthing\"),\"\",IF(SUM('Data Entered'!C33:C47)<>'Data Entered'!B51,\"Total cable length differs from circuit details\",\"\"))","v":""}]
[]
[null,"Pole termination details"]
[]
[null,"HV cable length to pole termination ≤ 0.2km?",null,null,null,{"$f":"'Data Entered'!D51","v":"NO"}]
[null,"Pole termination and GM distribution substation HV earth electrodes",null,null,null,{"$f":"'Data Entered'!F51","v":"Separate"},null,"Assumed Value",null,null,{"$f":"IF('Data Entered'!F51=\"Combined\",\"YES\",\"NO\")","v":"NO"},"Combined?"]
[null,"Impedance of separate pole termination HV earth",null,null,null,{"$f":"IF('Data Entered'!F51=\"Separate\",'Data Entered'!H51,\"\")","v":20},"Ω","Assumed Value"]
[]
[]
[null,"Modify details of pole termination"]
[null,null,null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!B52","v":"NO"},"Modification permitted?"]
["Design Input 16","NO",null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!D52","v":"NO"},"Modify details?"]
[null,{"$f":"IF(AND(ISBLANK(B158),OR('Data Entered'!B13=\"Intermediate\",'Data Entered'!B13=\"Advanced - Fault Level Study\")),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Enter details of pole termination"]
[]
["Design Input 16A","Pole termination and GM distribution substation HV earth electrodes",null,null,null,null,null,null,null,null,{"$f":"IF('Data Entered'!F52=\"Combined\",\"YES\",\"NO\")","v":"NO"},"Modified = Combined?"]
[null,"Impedance of pole termination HV earth",null,null,null,20,"Ω"]
[null,{"$f":"IF(OR(AND('Data Entered'!D52=\"YES\",ISBLANK(F163)),AND('Data Entered'!D52=\"YES\",'Data Entered'!F52=\"Separate\",ISBLANK(F164))),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Select the built-up area covered by the local HV & LV network"]
[]
["Design Input 17",null,null,"Unit of measurement"]
[null,null,null,"Area"]
[null,{"$f":"IF(OR(ISBLANK(B169),ISBLANK(B170)),\"**Compulsory Fields**\",\"\")","v":"**Compulsory Fields**"}]
[]
[null,"Select the type of local HV & LV network"]
[]
["Design Input 18"]
[null,{"$f":"IF('Data Entered'!B56=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,"SOIL RESISTIVITY DATA     [DESIGN STEP D]"]
[]
[null,"Soil Resistivity Assistant (Optional)"]
[]
[null,null,"Soil Resistivity (Ωm)",null,"Soil Depth (m)"]
[null,null,"From","To","From","To"]
[null,"Top Soil Layer"]
[null,"Middle Soil Layer",null,null,null,null,"Set middle soil layer values to zero if layer is not present"]
[null,"Bottom Soil Layer "]
[null,null,{"$f":"IF(OR(C184>D184,C185>D185,C186>D186,E184>F184,E185>F185),\"'From' value must be less than 'To' value\",\"\")","v":""}]
[]
[null,"RECOMMENDED resistivity of the upper layer of soil",null,null,null,{"$f":"IF(OR(COUNTBLANK(C184:D186)>0,COUNTBLANK(E184:F185)>0),300,'Data Entered'!D64)","v":300},"Ωm"]
[]
[null,"RECOMMENDED upper layer to lower layer soil resistivity ratio",null,null,null,{"$f":"IF(OR(COUNTBLANK(C184:D186)>0,COUNTBLANK(E184:F185)>0),\"1 : 3\",'Data Entered'!F60)","v":"1 : 3"}]
[]
[null,"RECOMMENDED combined depth of the upper & middle layers of soil",null,null,null,{"$f":"IF(OR(COUNTBLANK(C184:D186)>0,COUNTBLANK(E184:F185)>0),2,'Data Entered'!D65)","v":2},"m"]
[]
[]
[null,"Select the resistivity of the upper layer of soil"]
[]
["Design Input 19",{"$f":"F189","v":300},"Ωm"]
[null,{"$f":"IF('Data Entered'!B67=0,\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Select the upper layer to lower layer soil resistivity ratio",null,null,null,{"$f":"CONCATENATE('Data Entered'!B67,\" Ωm\")","v":"300 Ωm"}]
["Design Input 20",{"$f":"F191","v":"1 : 3"},null,null,null,{"$f":"CONCATENATE(ROUNDUP('Data Entered'!D69,1),\" Ωm\")","v":"900 Ωm"}]
[null,{"$f":"IF('Data Entered'!B68=0,\"**Compulsory Field**\",\"\")","v":""}]
[]
[]
[null,"Resistivity of the lower layer of soil"]
[null,{"$f":"IF(OR(ISBLANK('Data Entered'!B67),ISBLANK('Data Entered'!B68)),\"\",ROUNDUP('Data Entered'!D69,1))","v":900},"Ωm"]
[null,{"$f":"IF('Data Entered'!B68=0,\"\",'Data Entered'!D68)","v":"LOW above HIGH resistivity soil"}]
[]
[null,"Select the combined depth of the upper & middle layers of soil"]
["Design Input 21",{"$f":"F193","v":2},"m"]
[null,{"$f":"IF('Data Entered'!B70=0,\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"SUBSTATION HV ELECTRODE RESISTANCE     [DESIGN STEP E]"]
[]
[null,"Perimeter electrode"]
[]
[null,{"$f":"'Data Entered'!G11","v":"Not Applicable"},null,null,null,null,null,null,null,null,{"$f":"IF(B218=\"Required\",\"YES\",\"NO\")","v":"NO"},"Perimeter electrode?"]
[]
[]
[null,"Dispense with perimeter electrode? "]
[]
["Design Input 22","NO",null,"Selecting \"YES\" is only permissible for an earthing design at an existing site which lacks a perimeter electrode and where a retrofit is not reasonably practicable"]
[null,{"$f":"IF(AND(ISBLANK(B223),'Data Entered'!G11=\"Required\"),\"**Compulsory Field**\",\"\")","v":""}]
[]
[]
[null,"Select dimensions of horizontal electrode 'tail'"]
[]
["Design Input 23",null,"m"]
[null,{"$f":"IF(ISBLANK(B229),\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,"Estimated HV electrode resistance (RE) excluding network contribution"]
[]
[null,{"$f":"'Data Entered'!F72","v":120000},"Ω"]
[null,{"$f":"IF(OR(AND(B30=6600,B234>15,'Data Entered'!B72=200),AND(B30=11000,B234>20,'Data Entered'!B72=200)),\"Employ Earthing Specialist to carry out design\",IF(OR(AND(B30=6600,B234>15),AND(B30=11000,B234>20)),\"Electrode resistance exceeds maximum permitted - Increase length of tail\",\"\"))","v":""}]
[]
[null,"Estimated network contribution to HV electrode resistance (RNC)"]
[]
[null,{"$f":"'Data Entered'!F73","v":0.85000000000000009},"Ω"]
[]
[]
[null,"Overall earthing system impedance (RGMSUB)"]
[]
[null,{"$f":"'Data Entered'!F74","v":0.84999397920931408},"Ω"]
[]
[]
[null,"HV FAULT CURRENT & GROUND RETURN CURRENT     [DESIGN STEP F]"]
[]
[null,"Calculated total earth fault current (IF)"]
[]
[null,{"$f":"'Data Entered'!B75","v":10000},"A"]
[]
[]
[null,"Percentage of fault current flowing into the ground"]
[]
[null,{"$f":"'Data Entered'!B76","v":100},"%IGR"]
[]
[]
[null,"Modify percentage of fault current flowing into the ground?"]
[]
["Design Input 24","NO",null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!B77","v":"NO"}]
[null,{"$f":"IF(AND(ISBLANK(B261),OR('Data Entered'!B13=\"Intermediate\",'Data Entered'!B13=\"Advanced - Fault Level Study\")),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Enter modified percentage of fault current flowing into the ground?"]
[]
["Design Input 24A",{"$f":"B256","v":100},"%IGR"]
[null,{"$f":"IF(AND('Data Entered'!B77=\"YES\",'Data Entered'!D77=0),\"**Compulsory Field**\",\"\")","v":""}]
[null,"The following data should be used with the Earthing Solutions 'Ground Return Current Calculator' (where used) "]
[null,"Tab",null,{"$f":"IF('Data Entered'!B49=\"All Cable\",\"Arrangement 1 all cable circuit\",\"Ar. 2 cable-line or line-cable\")","v":"Arrangement 1 all cable circuit"}]
[null,"Cable type",null,{"$f":"VLOOKUP('Data Entered'!B50,'Data-General'!P2:R41,2,FALSE)","v":{"$error":"#N/A"}}]
[null,"Resistance at Start of Cable Ra",null,{"$f":"IF('Data Entered'!B48=\"YES\",'Data Entered'!F18,IF('Data Entered'!B48=\"NO\",'Data Entered'!H53,\"0\"))","v":0.1},null,null,"Ω"]
[null,"Resistance of Installation Rb",null,{"$f":"'Data Entered'!F74","v":0.84999397920931408},null,null,"Ω"]
[null,"Cable length",null,{"$f":"'Data Entered'!B51","v":0},null,null,"km"]
[null,"Then multiply IGR figure by 100, round up to whole number, and enter the value in Design Input 24A"]
[]
[]
[null,"The following data should be used with the 'Ground Return Current Tables' (where used)"]
[null,"Cable type",null,{"$f":"VLOOKUP('Data Entered'!B50,'Data-General'!P2:R41,3,FALSE)","v":{"$error":"#N/A"}}]
[null,"Cable length",null,{"$f":"IF('Data Entered'!B51<=0.5,0.5,IF('Data Entered'!B51<=1,1,IF('Data Entered'!B51<=2,2,IF('Data Entered'!B51<=5,5,10))))","v":0.5},null,null,"km"]
[null,"Then enter the % figure in Design Input 24A"]
[]
[]
[null,"Calculated fault current flowing into the ground (IGR)"]
[]
[null,{"$f":"'Data Entered'!B78","v":10000},"A"]
[]
[]
[null,"CONDUCTOR & ELECTRODE DIMENSIONS FOR CORROSION, MECHANICAL & THERMAL PERFORMANCE     [DESIGN STEP G]"]
[]
[null,"Earth conductor cross sectional area"]
[]
[null,{"$f":"'Data Entered'!B79","v":70},"mm2"]
[]
[]
[null,"Enter number of parallel conductors used for 'tail' electrode"]
[]
["Design Input 25"]
[null,{"$f":"IF('Data Entered'!B81=0,\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Minimum HV electrode surface area required"]
[]
[null,{"$f":"IF(ISERR('Calculations-Surface Area'!B22),\"\",'Calculations-Surface Area'!B22)","v":307.72348110429317},"mm2"]
[]
[]
[null,"Actual HV earth electrode surface area"]
[]
[null,"Surface area of perimeter electrode",null,null,{"$f":"'Data Entered'!B82","v":0},"mm2"]
[null,"Surface area of 4 x 1.2m earth rods",null,null,{"$f":"'Data Entered'!B83","v":0},"mm2"]
[null,"Surface area of electrode 'tail'",null,null,{"$f":"'Data Entered'!B84","v":0},"mm2"]
[null,"Total surface area",null,null,{"$f":"'Data Entered'!B85","v":0},"mm2"]
[null,"Electrode surface area criteria met",null,null,{"$f":"'Data Entered'!D85","v":"NO"}]
[null,{"$f":"IF(E319=\"YES\",\"\",IF(B297=3,\"Insufficient electrode surface area - Increase length of electrode 'tail'\",\"Insufficient electrode surface area - Increase length of electrode 'tail' or number of 'tail' conductors'\"))","v":"Insufficient electrode surface area - Increase length of electrode 'tail' or number of 'tail' conductors'"},null,null,null,null,null,"Change length of HV electrode tail"]
[null,null,null,null,null,null,null,"Change number of HV electrode tail conductors"]
[]
[null,"EARTH POTENTIAL RISE DUE TO HV FAULT     [DESIGN STEP H]"]
[]
[null,"Calculated earth potential rise (EPR) due to an HV fault"]
[]
[null,{"$f":"'Data Entered'!B86","v":8499.9397920931406},"V"]
[]
[]
[null,"Design EPR due to an HV fault (10% margin)"]
[]
[null,{"$f":"'Data Entered'!B87","v":9349.9337713024561},"V"]
[null,{"$f":"IF(OR(B332<=3000,B332=\"\"),\"\",\"EPR exceeds maximum permitted - Increase length of electrode tail\")","v":"EPR exceeds maximum permitted - Increase length of electrode tail"},null,null,null,null,"Change length of HV electrode tail"]
[]
[null,"HV FAULT CLEARANCE TIME     [DESIGN STEP I]"]
[]
[null,"HV fault clearance time"]
[]
[null,{"$f":"'Data Entered'!B88","v":3},"s"]
[]
[]
[null,"Modify HV fault clearance time?"]
[]
["Design Input 26","NO",null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!B89","v":"NO"}]
[null,{"$f":"IF(AND(ISBLANK(B344),OR('Data Entered'!B13=\"Intermediate\",'Data Entered'!B13=\"Advanced - Fault Level Study\")),\"**Compulsory Field**\",\"\")","v":""}]
[]
[null,"Enter CT ratio and IDMT earth-fault protection settings on HV feeder CB at source substation"]
[]
["Design Input 26A","CB operating time",null,null,{"$f":"'Data Entered'!B90","v":100},"ms"]
[null,"IDMT CT Ratio",null,null,null,"/"]
[null,"IDMT EF current setting"]
[null,"IDMT EF current setting",null,null,{"$f":"'Data Entered'!B95","v":0},"A (Primary Equivalent)",null,{"$f":"IF(OR(E352<E350*0.05,E352>E350*0.75),\"Suspicious result\",\"\")","v":""}]
[null,"IDMT EF time-current characteristic"]
[null,"IDMT EF time multiplier setting"]
[null,"IDMT EF protection operating time",null,null,{"$f":"'Data Entered'!B98","v":0},"ms"]
[null,"Total fault clearance time",null,null,{"$f":"'Data Entered'!B99","v":0.1},"s"]
[null,{"$f":"IF(AND('Data Entered'!B89=\"YES\",OR('Data Entered'!B13=\"Intermediate\",'Data Entered'!B13=\"Advanced - Fault Level Study\"),OR(ISBLANK(E350),ISBLANK(G350),ISBLANK(E351),ISBLANK(F351),ISBLANK(E353),ISBLANK(E354))),\"**Compulsory Fields**\",\"\")","v":""}]
[]
[null,"Design HV fault clearance time (0.4s margin)"]
[]
[null,{"$f":"'Data Entered'!B101","v":3.4},"s"]
[null,{"$f":"IF(OR(B361<=3000,B361=\"\"),\"\",\"EPR exceeds maximum permitted - Increase length of electrode tail\")","v":""},null,null,null,null,"Change length of HV electrode tail"]
[]
[null,"EARTH POTENTIAL RISE DUE TO EHV FAULT (TRANSFER VOLTAGE)     [DESIGN STEP J]"]
[]
[null,"EPR due to an EHV (i.e. 33kV, 66kV, 132kV, 275kV or 400kV) fault at the source substation (i.e. transfer voltage)"]
[]
[null,{"$f":"'Data Entered'!B139","v":0},"V",null,null,null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!B48=\"YES\"),AND('Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B48=\"YES\")),\"NO\",\"NO\")","v":"NO"},"Intermediate or Advanced FLS and cable connected?"]
[]
[]
[null,"Modify transfer voltage?"]
[]
["Design Input 27","NO",null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!B140","v":"NO"}]
[null,{"$f":"IF(OR('Data Entered'!B13=\"Basic\",'Data Entered'!B13=\"Advanced - ASC Earthing\",'Data Entered'!B48=\"NO\"),\"\",IF(ISBLANK(B373),\"**Compulsory Field**\",\"\"))","v":""}]
[]
[null,"Enter modified transfer voltage"]
[]
["Design Input 27A",{"$f":"B368","v":0},"V",{"$f":"IF(B378>3000,\"Transfer voltage exceeds maximum permitted.\",\"\")","v":""}]
[null,{"$f":"IF(AND('Data Entered'!B140=\"YES\",'Data Entered'!B48=\"YES\",ISBLANK(B378)),\"**Compulsory Field**\",\"\")","v":""},null,{"$f":"IF(B378>3000,\"Review accuracy of source s/s EPR and % transfer voltage. Consult NGED Policy Team.\",\"\")","v":""}]
[null,"The following data should be used with the Earthing Solutions 'Transfer Voltage Calculator' (where used) "]
[null,"Tab",null,"TRANSFER POTENTIAL"]
[null,"Cable type",null,{"$f":"VLOOKUP('Data Entered'!B50,'Data-General'!P2:R41,2,FALSE)","v":{"$error":"#N/A"}}]
[null,"Resistance of Source or Primary",null,{"$f":"'Data Entered'!F18","v":0.1},null,null,"Ω"]
[null,"Resistance of Remote Installation",null,{"$f":"'Data Entered'!F74","v":0.84999397920931408},null,null,"Ω"]
[null,"EPRA",null,{"$f":"'Data Entered'!F20/1000","v":3},null,null,"kV"]
[null,"Cable Length",null,{"$f":"'Data Entered'!B51","v":0},null,null,"km"]
[null,"Then multiply 'EPR (kV) at B' figure by 1000 and enter the value in Design Input 27A"]
[]
[]
[null,"The following data should be used with the 'Transfer Voltage Tables' (where used)"]
[null,"Cable type",null,{"$f":"VLOOKUP('Data Entered'!B50,'Data-General'!P2:R41,3,FALSE)","v":{"$error":"#N/A"}}]
[null,"Distribution S/S Earth Resistance RB",null,{"$f":"IF('Data Entered'!F74<=1,\"≤ 1\",IF('Data Entered'!F74<=5,\"≤ 5\",\"> 5\"))","v":"≤ 1"},null,null,"Ω"]
[null,"Cable length",null,{"$f":"IF('Data Entered'!B51<=0.5,0.5,IF('Data Entered'!B51<=1,1,IF('Data Entered'!B51<=2,2,IF('Data Entered'!B51<=5,5,10))))","v":0.5},null,null,"km"]
[null,{"$f":"CONCATENATE(\"Then multiply \",'Data Entered'!F20,\"V by the % and enter the value in Design Input 27A\")","v":"Then multiply 3000V by the % and enter the value in Design Input 27A"}]
[]
[]
[null,"Design EPR due to EHV fault"]
[]
[null,{"$f":"'Data Entered'!F140","v":0}]
[null,{"$f":"IF(OR(B399<=3000,B399=\"\"),\"\",\"EPR exceeds maximum permitted - Refer to NGED Engineering Policy\")","v":""}]
[]
[null,"EHV FAULT CLEARANCE TIME     [DESIGN STEP K]"]
[]
[null,"EHV fault clearance time"]
[]
[null,{"$f":"'Data Entered'!F22","v":3},"s"]
[]
[]
[null,{"$f":"CONCATENATE(\"Design EHV fault clearance time (\",'Data Entered'!D23,\"s margin)\")","v":"Design EHV fault clearance time (0.4s margin)"}]
[]
[null,{"$f":"'Data Entered'!F23","v":3.4},"s"]
[]
[]
[null,"TOUCH VOLTAGE LIMIT FOR DESIGN FAULT CLEARANCE TIMES     [DESIGN STEP L]"]
[]
[null,"Safety limit for touch voltages for HV and EHV fault clearance times"]
[]
[null,null,null,null,"HV Faults","EHV Faults"]
[null,"Standing surface = soil or outdoor concrete",null,null,{"$f":"'Data Entered'!B102","v":156},{"$f":"'Data Entered'!B106","v":156},"V"]
[null,"Standing surface = 100mm tarmac",null,null,{"$f":"'Data Entered'!B104","v":897},{"$f":"'Data Entered'!B108","v":897},"V"]
[null,"Standing surface = indoor concrete",null,null,{"$f":"'Data Entered'!B103","v":198},{"$f":"'Data Entered'!B107","v":198},"V"]
[null,"Standing surface = stance grating",null,null,{"$f":"'Data Entered'!B105","v":11012},{"$f":"'Data Entered'!B109","v":11012},"V"]
[]
[]
[null,"ENSURE SAFETY INSIDE & AROUND THE EXTERIOR OF THE SUBSTATION     [DESIGN STEP M]"]
[]
[null,"Maximum touch voltage for the substation as a percentage of the EPR (%TOUCH)"]
[]
[null,{"$f":"'Data Entered'!B110","v":21},"%TOUCH"]
[]
[]
[null,"Calculated touch voltage for the substation"]
[]
[null,null,null,null,"HV Faults","EHV Faults"]
[null,"EPR",null,null,{"$f":"'Data Entered'!B87","v":9349.9337713024561},{"$f":"'Data Entered'!F140","v":0}]
[null,"VTOUCH",null,null,{"$f":"'Data Entered'!B111","v":1963.4860919735158},{"$f":"'Data Entered'!H111","v":0},"V"]
[null,"VTOUCH ≤ Safety limit for soil or outdoor concrete",null,null,{"$f":"'Data Entered'!B112","v":"NO"},{"$f":"'Data Entered'!H112","v":"YES"}]
[null,"VTOUCH ≤ Safety limit for 100mm tarmac",null,null,{"$f":"'Data Entered'!B113","v":"NO"},{"$f":"'Data Entered'!H113","v":"YES"}]
[null,"VTOUCH ≤ Safety limit for indoor concrete",null,null,{"$f":"'Data Entered'!B114","v":"NO"},{"$f":"'Data Entered'!H114","v":"YES"}]
[null,"VTOUCH ≤ Safety limit for stance grating",null,null,{"$f":"'Data Entered'!B115","v":"YES"},{"$f":"'Data Entered'!H115","v":"YES"}]
[]
[]
[null,"Select standing surface for substation operator"]
[]
["Design Input 28"]
[null,{"$f":"IF('Data Entered'!B116=0,\"**Compulsory Field**\",IF(OR(AND('Data Entered'!B116=\"Soil or outdoor concrete\",OR(E437=\"NO\",F437=\"NO\")),AND('Data Entered'!B116=\"100mm tarmac\",OR(E438=\"NO\",F438=\"NO\")),AND('Data Entered'!B116=\"Indoor concrete\",OR(E439=\"NO\",F439=\"NO\")),AND('Data Entered'!B116=\"Stance grating\",OR(E440=\"NO\",F440=\"NO\"))),\"Unsafe selection - Change ground surface covering or increase length of HV electrode tail\",\"\"))","v":"**Compulsory Field**"},null,null,null,null,"Change length of HV electrode tail"]
[]
[null,"ASSESS IMPACT OF HV & EHV FAULTS ON THIRD PARTY PERSONS & EQUIPMENT     [DESIGN STEP N]"]
[]
[null,"Is the LV system neutral earthed at multiple locations?"]
[]
["Design Input 29",null,null,"Select 'YES' for a CNE/TN-C LV network or a mixed SNE/TN-S and CNE/TN-C LV network."]
[null,{"$f":"IF(AND('Data Entered'!G10=\"YES\",'Data Entered'!B117=\"\"),\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[null,null,null,"Select 'YES' for an SNE/TN-S LV network which is backfeedable from an adjacent substation or has been modified to make it suitable for providing PME supplies."]
[]
[]
[null,null,null,"Select 'NO' for an SNE/TN-S network which is not backfeedable from an adjacent substation and has not been modified to make it suitable for PME connections."]
[]
[]
[null,null,null,"Select 'NO' for a PNB LV network."]
[]
[null,"Is the EPR due to an HV or EHV fault less than the safety limit for LV Customers?"]
[]
[null,null,null,null,null,"HV Faults","EHV Faults"]
[null,"EPR",null,null,null,{"$f":"'Data Entered'!B87","v":9349.9337713024561},{"$f":"'Data Entered'!F140","v":0},"V"]
[null,"Safety limit for LV Customers - single LV neutral earth",null,null,null,{"$f":"'Data Entered'!B118","v":156},{"$f":"'Data Entered'!B128","v":156},"V"]
[null,"EPR ≤ Safety limit for LV Customers - single LV neutral earth",null,null,null,{"$f":"'Data Entered'!B119","v":"NO"},{"$f":"'Data Entered'!B129","v":"YES"}]
[null,"Safety limit for LV Customers - multiple LV neutral earths",null,null,null,{"$f":"'Data Entered'!B120","v":312},{"$f":"'Data Entered'!B130","v":312},"V"]
[null,"EPR ≤ Safety limit for LV Customers - multiple LV neutral earths",null,null,null,{"$f":"'Data Entered'!B121","v":"NO"},{"$f":"'Data Entered'!B131","v":"YES"}]
[]
[]
[null,"Is the EPR due to an HV or EHV fault less than the limit for LV Customer's telecommunication equipment?"]
[]
[null,null,null,null,null,"HV Faults","EHV Faults"]
[null,"EPR",null,null,null,{"$f":"'Data Entered'!B87","v":9349.9337713024561},{"$f":"'Data Entered'!F140","v":0},"V"]
[null,"Limit for LV Customer's telecommunication equipment",null,null,null,{"$f":"'Data Entered'!B122","v":1150},{"$f":"'Data Entered'!B132","v":1150},"V"]
[null,"EPR ≤ Limit for LV Customer's telecommunication equipment",null,null,null,{"$f":"'Data Entered'!B123","v":"NO"},{"$f":"'Data Entered'!B133","v":"YES"}]
[]
[]
[null,"Is the EPR due to an HV or EHV fault less than the International Telecommunication Union (ITU) limit?"]
[]
[null,null,null,null,null,"HV Faults","EHV Faults"]
[null,"EPR",null,null,null,{"$f":"'Data Entered'!B87","v":9349.9337713024561},{"$f":"'Data Entered'!F140","v":0},"V"]
[null,"International Telecommunication Union (ITU) Limit",null,null,null,{"$f":"'Data Entered'!B124","v":430},{"$f":"'Data Entered'!B134","v":430},"V"]
[null,"EPR ≤ International Telecommunication Union (ITU) Limit",null,null,null,{"$f":"'Data Entered'!B125","v":"NO"},{"$f":"'Data Entered'!B135","v":"YES"}]
[]
[]
[null,"CLASSIFY THIRD PARTY IMPACT     [DESIGN STEP O]"]
[]
[null,"NGED Third Party Impact Classification"]
[]
[null,{"$f":"IF('Data Entered'!B141=\"HEPR\",\"HIGH EPR\",\"LOW EPR\")","v":"HIGH EPR"},null,null,null,null,null,null,null,null,{"$f":"IF('Data Entered'!G10=\"YES\",\"LV\",\"HV\")","v":"LV"},"HV or LV?"]
[null,null,null,null,null,null,null,null,null,null,{"$f":"'Data Entered'!B141","v":"HEPR"},"HEPR or LEPR?"]
[null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND(K492=\"HV\",K493=\"HEPR\"),\"YES\",\"NO\")","v":"NO"},"HV and HEPR?"]
[null,"NGED Third Party Impact Classification means the following stipulations apply: "]
[]
[null,"Combined HV & LV Electrodes",null,null,null,{"$f":"IF(LEFT('Data Entered'!B145,8)=\"COMBINED\",\"PERMITTED\",IF(LEFT('Data Entered'!B145,8)=\"SEPARATE\",\"NOT PERMITTED\",\"NOT APPLICABLE\"))","v":"NOT PERMITTED"}]
[null,"HV Separation Distance",null,null,null,{"$f":"IF('Data Entered'!B141=\"HEPR\",\"REQUIRED\",\"NOT REQUIRED\")","v":"REQUIRED"}]
[null,"Advise HV Customer to consider the risks arising from earth potential rise",null,null,null,{"$f":"IF('Data Entered'!B141=\"HEPR\",\"REQUIRED\",\"NOT REQUIRED\")","v":"REQUIRED"}]
[]
[]
[null,"International Telecommunication Union (ITU) Classification"]
[]
[null,{"$f":"'Data Entered'!D141","v":"HOT"},null,null,null,null,null,null,null,null,{"$f":"IF(AND('Data Entered'!G10=\"NO\",'Data Entered'!D141=\"HOT\"),\"YES\",\"NO\")","v":"NO"},"HV and HOT?"]
[]
[]
[null,"ITU Classification means the following stipulations apply: "]
[]
[null,"Advise HV Customer to notify network provider if they have / are having a telecommunication service installed",null,null,null,null,null,"REQUIRED"]
[null,"None"]
[]
[]
[null,"HV SEPARATION DISTANCE     [DESIGN STEP P]"]
[]
[null,"Minimum HV separation distance to: "]
[null,"   Railway, Tramway, Metallic Pipeline,"]
[null,"   Above or Below Ground Bulk Storage Tanks For Petroleum or Other Flammable Liquids"]
[null,"   Zoo, Stable, Pond/Lake Used For Commercial Fishing,",null,null,null,null,null,null,null,null,{"$f":"IF('Data Entered'!B145=\"COMBINED HV & LV Earth Electrode\",\"YES\",\"NO\")","v":"NO"},"LV and LEPR?"]
[null,"   Outdoor Swimming Pool, Outdoor Paddling Pool, Outdoor Shower,"]
[null,"   Telephone Exchange, "]
[null,"   Customer TT Electrode"]
[]
[null,{"$f":"'Data Entered'!F142","v":40},"m",{"$f":"IF(K523=\"YES\",CONCATENATE(\"Note: theoretical separation distance = \",'Data Entered'!B142,\" m\"),\"\")","v":"Note: theoretical separation distance = 60 m"},null,null,null,null,null,null,{"$f":"IF('Data Entered'!B142>40,\"YES\",\"NO\")","v":"YES"},"Theoretical separation > 40m?"]
[]
[]
[null,"Minimum HV separation distance to LV system whose neutral is earthed at a single-point"]
[]
[null,{"$f":"'Data Entered'!F143","v":40},"m",{"$f":"IF(K518=\"YES\",\"COMBINED HV & LV Earth Electrode\",IF(K528=\"YES\",CONCATENATE(\"Note: theoretical separation distance = \",'Data Entered'!B143,\" m\"),\"\"))","v":""},null,null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!G10=\"YES\",'Data Entered'!B117=\"NO\",'Data Entered'!B143>40),AND('Data Entered'!G10=\"NO\",'Data Entered'!B143>40)),\"YES\",\"NO\")","v":"NO"},"Theoretical separation > 40m?"]
[]
[]
[null,"Minimum HV separation distance to LV system whose neutral is earthed at multiple points"]
[]
[null,{"$f":"'Data Entered'!F144","v":28},"m",{"$f":"IF(K518=\"YES\",\"COMBINED HV & LV Earth Electrode\",IF(K533=\"YES\",CONCATENATE(\"Note: theoretical separation distance = \",'Data Entered'!B144,\" m\"),\"\"))","v":""},null,null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!G10=\"NO\",'Data Entered'!B144>40),AND('Data Entered'!G10=\"YES\",'Data Entered'!B117=\"YES\",'Data Entered'!B144>40)),\"YES\",\"NO\")","v":"NO"},"Theoretical separation > 40m?"]
[]
[]
[null,"Comments"]
[]
[null,"Separation distances in excess of 40m are difficult to achieve and sustain in practice."]
[null,"Carry out the following actions in the order shown:"]
[]
[null,"   1. Review accuracy of underlying design assumptions (especially assumed values) and amend where necessary."]
[null,"           (e.g. Source S/S EPR & fault clearance time, HV fault clearance time, % fault current flowing into ground, % transfer voltage)"]
[]
[null,"   2. Measure actual soil resistivity and use in lieu of assumed value from EMU."]
[]
[null,"   3. Employ Earthing Specialist to carry out design."]
[]
[]
[]
[null,"LV ELECTRODE     [DESIGN STEP Q]"]
[]
[null,"Select length of LV electrode"]
[]
["Design Input 30",null,"m",null,null,null,null,null,null,null,{"$f":"IF('Data Entered'!B145=\"SEPARATE HV & LV Earth Electrodes\",\"HEPR\",\"LEPR\")","v":"HEPR"},"High or low EPR?"]
[null,{"$f":"IF(AND('Data Entered'!B146=0,'Data Entered'!G10=\"Yes\",OR('Data Entered'!B127=\"HEPR\",AND('Data Entered'!B48=\"YES\",'Data Entered'!B137=\"HEPR\"))),\"**Compulsory Field**\",\"\")","v":"**Compulsory Field**"}]
[]
[null,"Estimated LV electrode resistance (RLV)"]
[]
[null,{"$f":"ROUND('Data Entered'!B147,3)","v":6.8639999999999999},"Ω"]
[null,{"$f":"IF(OR(AND(B30=6600,B559>15,B554=200),AND(B30=11000,B559>20,B554=200)),\"Employ Earthing Specialist to carry out design\",IF(OR(AND(B30=6600,B559>15),AND(B30=11000,B559>20)),\"Electrode resistance exceeds maximum permitted - Increase length of LV electrode\",\"\"))","v":""}]

{"sheet":"% Touch Voltage","index":5,"n_rows":30,"n_cols":40,"rows_kept":30,"cut":false,"hidden":true,"merged":[[29,2,29,7],[28,2,28,7],[0,21,0,39],[0,2,0,20],[21,2,21,7],[23,2,23,7],[24,2,24,7],[25,2,25,7],[26,2,26,7],[27,2,27,7],[22,2,22,7]]}
[null,null,"With Perimeter Electrode",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Without Perimeter Electrode"]
[null,"Upper Soil Resitivity",25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25,25]
["ROW NO","Lower Soil Resistivity",2.5,2.778,3.125,3.573,4.1680000000000001,5,6.25,8.3332999999999995,12.5,25,50,75,100,125,150,175,200,225,250,2.5,2.778,3.125,3.573,4.1680000000000001,5,6.25,8.3332999999999995,12.5,25,50,75,100,125,150,175,200,225,250]
[1,"Lower to Upper Ratio",0.1,0.1111,0.125,0.1429,0.16669999999999999,0.2,0.25,0.33329999999999999,0.5,1,2,3,4,5,6,7,8,9,10,0.1,0.1111,0.125,0.1429,0.16669999999999999,0.2,0.25,0.33329999999999999,0.5,1,2,3,4,5,6,7,8,9,10]
[{"$f":"A4+1","v":2},"Unit substation in freestanding GRP or masonry housing",54,53,52,51,50,48,46,43,33,25,17,14,13,12,11,9,8,8,8,56,56,56,55,55,54,53,51,40,35,24,21,20,18,17,17,16,16,16]
[{"$f":"A5+1","v":3},"Unit substation integrated within larger building",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100]
[4,"Padmount substation",69,68,67,66,64,62,59,55,49,42,33,28,26,24,22,21,20,19,18,84,84,83,82,73,71,70,67,63,55,41,37,34,32,30,29,27,26,25]
[5,"LV Connection substation in freestanding GRP or masonry housing",54,53,52,51,50,48,46,43,33,25,17,14,13,12,11,9,8,8,8,56,56,56,55,55,54,53,51,40,35,24,21,20,18,17,17,16,16,16]
[6,"LV Connection substation integrated within larger building",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100]
[7,"HV Connection substation in freestanding GRP or masonry housing",54,53,52,51,50,48,46,43,33,25,17,14,13,12,11,9,8,8,8,56,56,56,55,55,54,53,51,40,35,24,21,20,18,17,17,16,16,16]
[8,"HV Connection substation integrated within larger building",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100]
["COL NO",1,{"$f":"B12+1","v":2},3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,{"$f":"Z12+1","v":26},{"$f":"AA12+1","v":27},{"$f":"AB12+1","v":28},{"$f":"AC12+1","v":29},{"$f":"AD12+1","v":30},{"$f":"AE12+1","v":31},{"$f":"AF12+1","v":32},{"$f":"AG12+1","v":33},{"$f":"AH12+1","v":34},{"$f":"AI12+1","v":35},{"$f":"AJ12+1","v":36},{"$f":"AK12+1","v":37},{"$f":"AL12+1","v":38},{"$f":"AM12+1","v":39}]
[]
[null,null,"U-L Ratio",0.1,0.1111,0.125,0.1429,0.16669999999999999,0.2,0.25,0.33329999999999999,0.5,1,2,3,4,5,6,7,8,9,10]
[null,"COL NO",1,{"$f":"C15+1","v":2},{"$f":"D15+1","v":3},4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20]
[]
[]
[null,null,"S/S Type","Unit substation in freestanding GRP or masonry housing","Unit substation integrated within larger building","Padmount substation","LV Connection substation in freestanding GRP or masonry housing","LV Connection substation integrated within larger building","HV Connection substation in freestanding GRP or masonry housing","HV Connection substation integrated within larger building"]
[null,"ROW NO",1,{"$f":"C19+1","v":2},3,4,5,6,7,8]
[]
[]
[null,"Actual Substation Format",{"$f":"'Data Entered'!B10","v":0}]
[null,"ROW NO",{"$f":"IF(C22=0,2,HLOOKUP(C22,C18:J19,2,FALSE))","v":2}]
[null,"Perimeter Electrode",{"$f":"IF('Data Entered'!D71=\"Required\",\"YES\",\"NO\")","v":"NO"}]
[null,"Upper resistivity",{"$f":"'Data Entered'!B67","v":300}]
[null,"Lower resistivity",{"$f":"'Data Entered'!D69","v":900}]
[null,"U-L ratio",{"$f":"'Data Entered'!B69","v":3}]
[null,"COL NO",{"$f":"HLOOKUP(C27,C14:V15,2,FALSE)","v":13}]
[null,"COL NO CORRECTED",{"$f":"IF(C24=\"YES\",C28,C28+19)","v":32}]
[null,"% Touch Voltage",{"$f":"INDEX(B4:AN11,C23,C29)","v":21}]

{"sheet":"Soil Depth Factor","index":6,"n_rows":27,"n_cols":9,"rows_kept":27,"cut":false,"hidden":true,"merged":[[0,3,0,8]]}
[null,null,null,"Soil Depth (m)"]
["Upper","Lower","U-L Ratio",1,2,4,6,8,10]
[25,{"$f":"A3*C3","v":2.5},0.1,0.76518355945730254,1,1.184856344772546,1.2570830007980847,1.2920989624900241,1.3157422186751795]
[25,2.7775000000000003,0.1111,0.76985236643070243,1,1.1804080014972531,1.2478944876861933,1.2855460020036771,1.3085552607532505]
[25,3.125,0.125,0.77513971626850076,1,1.1750414542774672,1.2411717742430755,1.277651538414297,1.2998833138856476]
[25,3.5724999999999998,0.1429,0.78212709252935786,1,1.1675411565475693,1.2317675800227645,1.2667610560506373,1.2881097137780739]
[25,4.1674999999999995,0.16669999999999999,0.79216150120678352,1,1.157729009158768,1.2213608682448094,1.2545434202324057,1.274779022745073]
[25,5,0.2,0.80577328911667168,1,1.1480441664154357,1.207152547482665,1.2379409104612602,1.2567455532107323]
[25,6.25,0.25,0.82480980072172294,1,1.1351966350242491,1.1881536304502724,1.2157583837083688,1.2325832624635116]
[25,8.3324999999999996,0.33329999999999999,0.85109933774834434,1,1.1123178807947021,1.1562030905077263,1.1789845474613687,1.1929359823399559]
[25,12.5,0.5,0.89881761628146506,1,1.0751040250484076,1.1041898405635893,1.1193507189057801,1.1285378815968361]
[25,25,1,1,1,1,1,1,1]
[25,50,2,1.1167994376757264,1,0.92074742268041243,0.89104967197750706,0.87582005623242742,0.86650656044985941]
[25,75,3,1.1849492460002506,1,0.87812774134257909,0.83301307489870091,0.80985003550691348,0.79579347508250131]
[25,100,4,1.2348655514547286,1,0.84891913914585626,0.79101759095048652,0.76326511048267265,0.74639313617408809]
[25,125,5,1.2704527045270451,1,0.82872828728287284,0.76631266312663127,0.73436234362343611,0.7150121501215011]
[25,150,6,1.2979752579084798,1,0.81353537947861809,0.74585848208552707,0.71127092162150585,0.690338598518899]
[25,175,7,1.3275380189066996,1,0.80164406083025086,0.72992190711056315,0.69330045211672831,0.67114673242909995]
[25,200,8,1.3416311047889995,1,0.78765607712976138,0.71309467362098944,0.67504346451714869,0.65204678362573099]
[25,225,9,1.3577833984824097,1,0.78209550088142865,0.7038016402238062,0.66191461638690874,0.63819268797424689]
[25,250,10,1.3716115357057559,1,0.7749880582756149,0.69430678289945069,0.65319739670408394,0.62834368282780029]
[]
[]
[{"$f":"ROUND('Data Entered'!B69,4)","v":3},"U-L Ratio"]
[{"$f":"'Data Entered'!B70","v":2},"Soil Depth"]
[{"$f":"IF(A25=1,2,IF(A25=2,3,IF(A25=4,4,IF(A25=6,5,IF(A25=8,6,7)))))","v":3},"Soil Depth Col"]
[{"$f":"VLOOKUP(A24,C3:I21,A26,TRUE)","v":1},"Soil Depth Factor"]

{"sheet":"Publish Report","index":7,"n_rows":79,"n_cols":9,"rows_kept":79,"cut":false,"hidden":false,"merged":[[31,1,31,5],[11,1,11,5],[32,1,32,5],[39,1,39,5],[1,1,1,6],[3,1,3,6],[4,1,4,5],[5,1,5,5],[18,1,18,5],[6,1,6,5],[7,1,7,5],[8,1,8,5],[9,1,9,5],[10,1,10,5],[12,1,12,5],[13,1,13,5],[14,1,14,5],[15,1,15,5],[16,1,16,5],[17,1,17,5],[33,1,33,5],[19,1,19,5],[20,1,20,5],[21,1,21,5],[22,1,22,5],[23,1,23,5],[24,1,24,5],[25,1,25,5],[27,1,27,5],[28,1,28,5],[29,1,29,5],[30,1,30,5],[26,1,26,5],[55,1,55,6],[61,1,63,6],[46,1,46,5],[34,1,34,5],[35,1,35,5],[36,1,36,5],[37,1,37,5],[40,1,40,5],[41,1,41,5],[42,1,42,5],[44,1,44,5],[45,1,45,5],[48,1,48,5],[49,1,49,5],[43,1,43,5],[57,1,58,2],[38,1,38,5],[50,1,50,5],[51,1,51,5],[52,1,52,4],[52,5,52,6],[47,1,47,5]]}
[]
[null,"Check all the error messages listed in the table below have been fully resolved.  "]
[]
[null,"ERROR MESSAGES"]
[null,{"$f":"IF('Job Input'!B5=\"**Compulsory Field**\",\"Job Input 1 is incomplete\",\"\")","v":"Job Input 1 is incomplete"},null,null,null,null,"Remedy",null,"Job Input'!$B$4"]
[null,{"$f":"IF('Job Input'!B10=\"**Compulsory Field**\",\"Job Input 2 is incomplete\",\"\")","v":"Job Input 2 is incomplete"},null,null,null,null,"Remedy",null,"Job Input'!$B$9"]
[null,{"$f":"IF('Job Input'!B15=\"**Compulsory Field**\",\"Job Input 3 is incomplete\",\"\")","v":"Job Input 3 is incomplete"},null,null,null,null,"Remedy",null,"Job Input'!$B$14"]
[null,{"$f":"IF('Job Input'!B20=\"**Compulsory Field**\",\"Job Input 4 is incomplete\",\"\")","v":"Job Input 4 is incomplete"},null,null,null,null,"Remedy",null,"Job Input'!$B$19"]
[null,{"$f":"IF('Job Input'!B25=\"**Compulsory Field**\",\"Job Input 5 is incomplete\",\"\")","v":"Job Input 5 is incomplete"},null,null,null,null,"Remedy",null,"Job Input'!$B$24"]
[null,{"$f":"IF('Job Input'!B30=\"**Compulsory Field**\",\"Job Input 6 is incomplete\",\"\")","v":"Job Input 6 is incomplete"},null,null,null,null,"Remedy",null,"Job Input'!$B$29"]
[null,{"$f":"IF('Job Input'!B36=\"**Compulsory Field**\",\"Job Input 7 is incomplete\",\"\")","v":"Job Input 7 is incomplete"},null,null,null,null,"Remedy",null,"Job Input'!$B$34"]
[null,{"$f":"IF('Design Input'!B7=\"**Compulsory Field**\",\"Design Input 0 is incomplete\",\"\")","v":"Design Input 0 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$6"]
[null,{"$f":"IF('Design Input'!B12=\"**Compulsory Field**\",\"Design Input 1 is incomplete\",\"\")","v":"Design Input 1 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$11"]
[null,{"$f":"IF('Design Input'!B12=\"This earthing design tool is NOT appropriate for a special design\",\"This design tool is NOT appropriate for a special design\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$11"]
[null,{"$f":"IF('Design Input'!B19=\"**Compulsory Field**\",\"Design Input 2 is incomplete\",\"\")","v":"Design Input 2 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$18"]
[null,{"$f":"IF('Design Input'!B26=\"**Compulsory Field**\",\"Design Input 3 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$25"]
[null,{"$f":"IF('Design Input'!B31=\"**Compulsory Field**\",\"Design Input 4 is incomplete\",\"\")","v":"Design Input 4 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$30"]
[null,{"$f":"IF('Design Input'!B36=\"**Compulsory Field**\",\"Design Input 5 is incomplete\",\"\")","v":"Design Input 5 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$35"]
[null,{"$f":"IF('Design Input'!B41=\"**Compulsory Field**\",\"Design Input 6 is incomplete\",\"\")","v":"Design Input 6 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$40"]
[null,{"$f":"IF('Design Input'!B56=\"**Compulsory Field**\",\"Design Input 7 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$55"]
[null,{"$f":"IF('Design Input'!B61=\"**Compulsory Field**\",\"Design Input 7A is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$60"]
[null,{"$f":"IF('Design Input'!B71=\"**Compulsory Field**\",\"Design Input 8 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$70"]
[null,{"$f":"IF('Design Input'!B76=\"**Compulsory Field**\",\"Design Input 8A is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$75"]
[null,{"$f":"IF('Design Input'!B86=\"**Compulsory Field**\",\"Design Input 9 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$85"]
[null,{"$f":"IF('Design Input'!B91=\"**Compulsory Field**\",\"Design Input 9A is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$90"]
[null,{"$f":"IF('Design Input'!B96=\"**Compulsory Field**\",\"Design Input 10 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$C$95"]
[null,{"$f":"IF('Design Input'!C105=\"**Compulsory Fields**\",\"Design Input 11 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$C$95"]
[null,{"$f":"IF('Design Input'!C110=\"**Compulsory Field**\",\"Design Input 12 is incomplete\",\"\")","v":"Design Input 12 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$C$102"]
[null,{"$f":"IF('Design Input'!C115=\"**Compulsory Fields: NER 1**\",\"Design Input 12 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$D$110"]
[null,{"$f":"IF('Design Input'!D134=\"**Compulsory Fields**\",\"Design Input 13 is incomplete\",\"\")","v":"Design Input 13 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$129"]
[null,{"$f":"IF('Design Input'!B139=\"**Compulsory Field**\",\"Design Input 14 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$D$137"]
[null,{"$f":"IF('Design Input'!B147=\"**Compulsory Fields**\",\"Design Input 15 is incomplete\",\"\")","v":"Design Input 15 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$D$137"]
[null,{"$f":"IF('Design Input'!B159=\"**Compulsory Field**\",\"Design Input 16 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$149"]
[null,{"$f":"IF('Design Input'!B165=\"**Compulsory Field**\",\"Design Input 16A is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$F$154"]
[null,{"$f":"IF('Design Input'!B171=\"**Compulsory Fields**\",\"Design Input 17 is incomplete\",\"\")","v":"Design Input 17 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$160"]
[null,{"$f":"IF('Design Input'!B176=\"**Compulsory Field**\",\"Design Input 18 is incomplete\",\"\")","v":"Design Input 18 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$166"]
[null,{"$f":"IF('Design Input'!B199=\"**Compulsory Field**\",\"Design Input 19 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$189"]
[null,{"$f":"IF('Design Input'!B203=\"**Compulsory Field**\",\"Design Input 20 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$193"]
[null,{"$f":"IF('Design Input'!B212=\"**Compulsory Field**\",\"Design Input 21 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$202"]
[null,{"$f":"IF('Design Input'!B224=\"**Compulsory Field**\",\"Design Input 22 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$214"]
[null,{"$f":"IF('Design Input'!B230=\"**Compulsory Field**\",\"Design Input 23 is incomplete\",\"\")","v":"Design Input 23 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$220"]
[null,{"$f":"IF('Design Input'!B262=\"**Compulsory Field**\",\"Design Input 24 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$252"]
[null,{"$f":"IF('Design Input'!B267=\"**Compulsory Field**\",\"Design Input 24A is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$257"]
[null,{"$f":"IF('Design Input'!B298=\"**Compulsory Field**\",\"Design Input 25 is incomplete\",\"\")","v":"Design Input 25 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$293"]
[null,{"$f":"IF('Design Input'!B345=\"**Compulsory Field**\",\"Design Input 26 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$335"]
[null,{"$f":"IF('Design Input'!B357=\"**Compulsory Fields**\",\"Design Input 26A is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$E$342"]
[null,{"$f":"IF('Design Input'!B374=\"**Compulsory Field**\",\"Design Input 27 is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$431"]
[null,{"$f":"IF('Design Input'!B379=\"**Compulsory Field**\",\"Design Input 27A is incomplete\",\"\")","v":""},null,null,null,null,"Remedy",null,"Design Input'!$B$436"]
[null,{"$f":"IF('Design Input'!B446=\"**Compulsory Field**\",\"Design Input 28 is incomplete\",\"\")","v":"Design Input 28 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$384"]
[null,{"$f":"IF('Design Input'!B453=\"**Compulsory Field**\",\"Design Input 29 is incomplete\",\"\")","v":"Design Input 29 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$391"]
[null,{"$f":"IF('Design Input'!B555=\"**Compulsory Field**\",\"Design Input 30 is incomplete\",\"\")","v":"Design Input 30 is incomplete"},null,null,null,null,"Remedy",null,"Design Input'!$B$522"]
[]
[null,"Hide \"Publish Report\" button",null,null,null,{"$f":"IF(OR(RIGHT(B5,10)=\"incomplete\",RIGHT(B6,10)=\"incomplete\",RIGHT(B7,10)=\"incomplete\",RIGHT(B8,10)=\"incomplete\",RIGHT(B9,10)=\"incomplete\",RIGHT(B10,10)=\"incomplete\",RIGHT(B11,10)=\"incomplete\",RIGHT(B12,10)=\"incomplete\",RIGHT(B13,10)=\"incomplete\",RIGHT(B14,6)=\"design\",RIGHT(B15,10)=\"incomplete\",RIGHT(B16,10)=\"incomplete\",RIGHT(B17,10)=\"incomplete\",RIGHT(B18,10)=\"incomplete\",RIGHT(B19,10)=\"incomplete\",RIGHT(B20,10)=\"incomplete\",RIGHT(B21,10)=\"incomplete\",RIGHT(B22,10)=\"incomplete\",RIGHT(B23,10)=\"incomplete\",RIGHT(B24,10)=\"incomplete\",RIGHT(B25,10)=\"incomplete\",RIGHT(B26,10)=\"incomplete\",RIGHT(B27,10)=\"incomplete\",RIGHT(B28,10)=\"incomplete\",RIGHT(B29,10)=\"incomplete\",RIGHT(B30,10)=\"incomplete\",RIGHT(B31,10)=\"incomplete\",RIGHT(B32,10)=\"incomplete\",RIGHT(B33,10)=\"incomplete\",RIGHT(B34,10)=\"incomplete\",RIGHT(B35,10)=\"incomplete\",RIGHT(B36,10)=\"incomplete\",RIGHT(B37,10)=\"incomplete\",RIGHT(B38,10)=\"incomplete\",RIGHT(B39,10)=\"incomplete\",RIGHT(B40,10)=\"incomplete\",RIGHT(B41,10)=\"incomplete\",RIGHT(B42,10)=\"incomplete\",RIGHT(B43,10)=\"incomplete\",RIGHT(B44,10)=\"incomplete\",RIGHT(B45,10)=\"incomplete\",RIGHT(B46,10)=\"incomplete\",RIGHT(B47,10)=\"incomplete\",RIGHT(B48,10)=\"incomplete\",RIGHT(B49,10)=\"incomplete\",RIGHT(B50,10)=\"incomplete\",RIGHT(B51,10)=\"incomplete\"),\"YES\",\"NO\")","v":"YES"}]
[]
[]
[null,"Click on the 'Publish Report' button to save the earthing report in pdf format once the \"Job Input\" and \"Design Input\" forms have been fully completed.  "]
[]
[]
[]
[]
[]
[null,"The pdf document will be named \"ER_NGED_[Licence Area]_[Job Reference]_[dd-mm-yyyy-hh-mm-ss].pdf\" and will be located in the same folder as the excel spreadsheet. "]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["FOOTER",null,"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"]
["LICENCE",null,{"$f":"'Data Entered'!D6","v":"WM"}]
["JOB REFERENCE",null,{"$f":"IF(LEN('Data Entered'!B5)>15,LEFT('Data Entered'!B5,15),'Data Entered'!B5)","v":0}]
["DATE",null,"26/03/2020"]
["TIME",null,"17:03:58"]

{"sheet":"Data Entered","index":8,"n_rows":147,"n_cols":11,"rows_kept":147,"cut":false,"hidden":true,"merged":[[9,1,9,2],[48,0,52,0],[32,0,46,0],[16,0,17,0],[18,0,19,0],[27,0,31,0],[20,0,22,0],[23,0,26,0],[53,0,54,0],[67,0,68,0],[71,0,73,0],[87,0,100,0],[74,0,77,0],[78,0,86,0],[56,0,65,0],[113,6,114,6],[101,0,115,0],[137,0,139,0],[140,0,146,0],[101,4,104,4],[105,4,108,4]]}
["Job Input"]
["Job Input 1",{"$f":"'Job Input'!B4","v":0},"NGED or ICP Job?"]
["Job Input 2",{"$f":"'Job Input'!B9","v":0},"Designer Name"]
["Job Input 3",{"$f":"'Job Input'!B14","v":0},"NGED MU or ICP Name"]
["Job Input 4",{"$f":"'Job Input'!B19","v":0},"NGED Enquiry or ICP Reference"]
["Job Input 5",{"$f":"'Job Input'!B24","v":0},"Licence Area",{"$f":"IF(B6=\"South West\",\"SWE\",IF(B6=\"South Wales\",\"SWA\",IF(B6=\"East Midlands\",\"EM\",\"WM\")))","v":"WM"},"Shortform"]
["Job Input 6",{"$f":"'Job Input'!B29","v":0},"GMSUB Name"]
["Job Input 7",{"$f":"'Job Input'!B34","v":0},"GMSUB Address"]
["Design Input"]
["Design Input 0",{"$f":"'Design Input'!B6","v":0},null,"Substation format",{"$f":"IF(B10=0,0,VLOOKUP(B10,'Data-General'!B2:C8,2,FALSE))","v":0},"Substation format code",{"$f":"IF(OR(E10=\"G\",E10=\"H\"),\"NO\",\"YES\")","v":"YES"},"LV?",{"$f":"CONCATENATE(\"TP21G-\",E10)","v":"TP21G-0"},"Associated ST"]
["Design Input 1",{"$f":"'Design Input'!B11","v":0},"Special design?",null,null,null,{"$f":"IF(OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\"),\"Required\",\"Not Applicable\")","v":"Not Applicable"},"Default Perimeter electrode"]
["Design Input 2",{"$f":"'Design Input'!B18","v":0},"Problematic location?",null,null,null,{"$f":"IF(OR(E10=\"B\",E10=\"F\",E10=\"H\"),\"YES\",\"NO\")","v":"NO"},"Insulated HV Tail?"]
["Design Input 3",{"$f":"'Design Input'!B25","v":"Basic"},"Design methodology?",{"$f":"IF(B13=\"Advanced - ASC Earthing\",\"YES\",\"NO\")","v":"NO"},"ASC Earthed Network"]
["Design Input 4",{"$f":"'Design Input'!B30","v":0},"System voltage"]
["Design Input 5",{"$f":"'Design Input'!B35","v":0},"Source substation method",{"$f":"IF(B15=\"By Name\",\"NAME\",\"NUMBER\")","v":"NUMBER"},"Shortform",{"$f":"CONCATENATE(\"SUBSTATION_\",D15,\"_\",D6)","v":"SUBSTATION_NUMBER_WM"},"Concatenate shortforms"]
["Design Input 6",{"$f":"'Design Input'!B40","v":0},"Source substation name/number",{"$f":"IF(D15=\"NUMBER\",VLOOKUP(B16,'Source-Num'!B3:I1990,2,FALSE),VLOOKUP(SUBSTITUTE(B16,\" \",\"\"),'Source-Name'!C3:J1990,2,FALSE))","v":{"$error":"#N/A"}},"Source substation name/number"]
["Design Input 7",{"$f":"IF(B16=0,0.1,IF(D15=\"NUMBER\",VLOOKUP(B16,'Source-Num'!B3:I1990,3,FALSE),IF(D15=\"NAME\",VLOOKUP(SUBSTITUTE(B16,\" \",\"\"),'Source-Name'!C3:J1990,3,FALSE),\"ERROR\")))","v":0.1},"Source earth resistance",{"$f":"IF(D15=\"NUMBER\",VLOOKUP(B16,'Source-Num'!B3:I1990,4,FALSE),VLOOKUP(SUBSTITUTE(B16,\" \",\"\"),'Source-Name'!C3:J1990,4,FALSE))","v":{"$error":"#N/A"}},"Assumed value"]
[null,{"$f":"IF(OR(B13=\"Basic\",B13=\"Advanced - ASC Earthing\"),\"NO\",IF(ISBLANK('Design Input'!B55),\"NO\",'Design Input'!B55))","v":"NO"},"Modify source earth resistance",{"$f":"IF(B18=\"NO\",\"N/A\",'Design Input'!B60)","v":"N/A"},"Value",{"$f":"IF(B18=\"YES\",D18,B17)","v":0.1},"Value used in calculations"]
["Design Input 8",{"$f":"IF(B16=0,3000,IF(D15=\"NUMBER\",VLOOKUP(B16,'Source-Num'!B3:I1990,5,FALSE),VLOOKUP(SUBSTITUTE(B16,\" \",\"\"),'Source-Name'!C3:J1990,5,FALSE)))","v":3000},"Source EPR",{"$f":"IF(D15=\"NUMBER\",VLOOKUP(B16,'Source-Num'!B3:I1990,6,FALSE),VLOOKUP(SUBSTITUTE(B16,\" \",\"\"),'Source-Name'!C3:J1990,6,FALSE))","v":{"$error":"#N/A"}},"Assumed value"]
[null,{"$f":"IF(OR(B13=\"Basic\",B13=\"Advanced - ASC Earthing\"),\"NO\",IF(ISBLANK('Design Input'!B70),\"NO\",'Design Input'!B70))","v":"NO"},"Modify source EPR",{"$f":"IF(B20=\"NO\",\"N/A\",'Design Input'!B75)","v":"N/A"},"Value",{"$f":"IF(B20=\"YES\",D20,B19)","v":3000},"Value used in calculations"]
["Design Input 9",{"$f":"IF(B16=0,3,IF(D15=\"NUMBER\",VLOOKUP(B16,'Source-Num'!B3:I1990,7,FALSE),VLOOKUP(SUBSTITUTE(B16,\" \",\"\"),'Source-Name'!C3:J1990,7,FALSE)))","v":3},"Source clearance time",{"$f":"IF(D15=\"NUMBER\",VLOOKUP(B16,'Source-Num'!B3:I1990,8,FALSE),VLOOKUP(SUBSTITUTE(B16,\" \",\"\"),'Source-Name'!C3:J1990,8,FALSE))","v":{"$error":"#N/A"}},"Assumed value"]
[null,{"$f":"IF(OR(B13=\"Basic\",B13=\"Advanced - ASC Earthing\"),\"NO\",IF(ISBLANK('Design Input'!B85),\"NO\",'Design Input'!B85))","v":"NO"},"Modify clearance time",{"$f":"IF(B22=\"NO\",\"N/A\",'Design Input'!B90)","v":"N/A"},"Value",{"$f":"IF(B13=\"Basic\",B21,IF(B22=\"YES\",D22,B21))","v":3},"Value used in calculations"]
[null,{"$f":"'Design Input'!B95","v":0},"Overcurrent type protection?",{"$f":"IF(OR(B13=\"Basic\",B13=\"Advanced - ASC Earthing\"),0.4,IF(OR(B23=\"YES\",B23=\"UNKNOWN\"),0.4,IF(F22>0.2,0.1,0.2-F22)))","v":0.4},"Design margin",{"$f":"F22+D23","v":3.4},"Design EHV clearance time"]
["Design Input 10",{"$f":"'Design Input'!C100","v":0},"Units"]
[null,{"$f":"IF($B$13=\"Advanced - Fault Level Study\",'Design Input'!C102,0)","v":0},{"$f":"IF($B$13=\"Advanced - Fault Level Study\",'Design Input'!D102,0)","v":0},"Z1"]
[null,{"$f":"IF($B$13=\"Advanced - Fault Level Study\",'Design Input'!C103,0)","v":0},{"$f":"IF($B$13=\"Advanced - Fault Level Study\",'Design Input'!D103,0)","v":0},"Z2"]
[null,{"$f":"IF($B$13=\"Advanced - Fault Level Study\",'Design Input'!C104,0)","v":0},{"$f":"IF($B$13=\"Advanced - Fault Level Study\",'Design Input'!D104,0)","v":0},"Z0"]
["Design Input 11",{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\",$B$13=\"Intermediate\"),0,IF(ISBLANK('Design Input'!C109),0,'Design Input'!C109))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\",$B$13=\"Intermediate\"),0,IF(ISBLANK('Design Input'!D109),0,'Design Input'!D109))","v":""}]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\",$B$13=\"Basic\"),0,IF(ISBLANK('Design Input'!C111),0,'Design Input'!C111))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\",$B$13=\"Basic\"),0,IF(ISBLANK('Design Input'!D111),0,'Design Input'!D111))","v":0},"A"]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\",$B$13=\"Basic\"),0,IF(ISBLANK('Design Input'!C112),0,'Design Input'!C112))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\",$B$13=\"Basic\"),0,IF(ISBLANK('Design Input'!D112),0,'Design Input'!D112))","v":0},"A"]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\",$B$13=\"Basic\"),0,IF(ISBLANK('Design Input'!C113),0,'Design Input'!C113))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\",$B$13=\"Basic\"),0,IF(ISBLANK('Design Input'!D113),0,'Design Input'!D113))","v":0},"A"]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\",$B$13=\"Basic\"),0,IF(ISBLANK('Design Input'!C114),0,'Design Input'!C114))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\",$B$13=\"Basic\"),0,IF(ISBLANK('Design Input'!D114),0,'Design Input'!D114))","v":0},"A","UG or BLANK","Cable Contiguity from GMSUB","Cable Length From GMSUB"]
["Design Input 12",{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D119),0,'Design Input'!D119))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F119),0,'Design Input'!F119))","v":0},"A",{"$f":"IF(LEFT(B33,8)=\"Overhead\",0,1)","v":1},{"$f":"F34*E33","v":1},{"$f":"F33*C33","v":0},{"$f":"AND(E33:E47)","v":true},"All cable?"]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D120),0,'Design Input'!D120))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F120),0,'Design Input'!F120))","v":0},"A",{"$f":"IF(LEFT(B34,8)=\"Overhead\",0,1)","v":1},1,0,{"$f":"OR(LEFT(B33,8)=\"Overhead\",LEFT(B34,8)=\"Overhead\",LEFT(B35,8)=\"Overhead\",LEFT(B36,8)=\"Overhead\",LEFT(B37,8)=\"Overhead\",LEFT(B38,8)=\"Overhead\",LEFT(B39,8)=\"Overhead\",LEFT(B40,8)=\"Overhead\",LEFT(B41,8)=\"Overhead\",LEFT(B42,8)=\"Overhead\",LEFT(B43,8)=\"Overhead\",LEFT(B44,8)=\"Overhead\",LEFT(B45,8)=\"Overhead\",LEFT(B46,8)=\"Overhead\",LEFT(B47,8)=\"Overhead\")","v":false},"Overhead section?"]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D121),0,'Design Input'!D121))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F121),0,'Design Input'!F121))","v":0},"A",1,1,0,{"$f":"IF(G48=0,\"TRUE\",\"FALSE\")","v":"TRUE"},"No cable into GMSUB?"]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D122),0,'Design Input'!D122))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F122),0,'Design Input'!F122))","v":0},"A",1,1,0,{"$f":"G48","v":0},"Total cable length from GMSUB"]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D123),0,'Design Input'!D123))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F123),0,'Design Input'!F123))","v":0},"A",1,{"$f":"F38*E37","v":1},0]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D124),0,'Design Input'!D124))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F124),0,'Design Input'!F124))","v":0},"A",1,{"$f":"F39*E38","v":1},0]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D125),0,'Design Input'!D125))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F125),0,'Design Input'!F125))","v":0},"A",{"$f":"IF(LEFT(B39,8)=\"Overhead\",0,1)","v":1},{"$f":"F40*E39","v":1},{"$f":"F39*C39","v":0}]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D126),0,'Design Input'!D126))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F126),0,'Design Input'!F126))","v":0},"A",1,{"$f":"F41*E40","v":1},0]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D127),0,'Design Input'!D127))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F127),0,'Design Input'!F127))","v":0},"A",1,{"$f":"F42*E41","v":1},0]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D128),0,'Design Input'!D128))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F128),0,'Design Input'!F128))","v":0},"A",1,{"$f":"F43*E42","v":1},0]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D129),0,'Design Input'!D129))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F129),0,'Design Input'!F129))","v":0},"A",{"$f":"IF(LEFT(B43,8)=\"Overhead\",0,1)","v":1},{"$f":"F44*E43","v":1},{"$f":"F43*C43","v":0}]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D130),0,'Design Input'!D130))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F130),0,'Design Input'!F130))","v":0},"A",1,{"$f":"F45*E44","v":1},0]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D131),0,'Design Input'!D131))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F131),0,'Design Input'!F131))","v":0},"A",1,1,0]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D132),0,'Design Input'!D132))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F132),0,'Design Input'!F132))","v":0},"A",1,{"$f":"F47*E46","v":1},0]
[null,{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!D133),0,'Design Input'!D133))","v":0},{"$f":"IF(OR($B$13=\"Advanced - Fault Level Study\",$B$13=\"Advanced - ASC Earthing\"),0,IF(ISBLANK('Design Input'!F133),0,'Design Input'!F133))","v":0},"A",1,{"$f":"E47","v":1},{"$f":"F47*C47","v":0}]
["Design Input 13",{"$f":"IF(OR(AND(B13=\"Basic\",H34=FALSE),AND(B13=\"Intermediate\",H34=FALSE)),\"YES\",IF(OR(AND(B13=\"Basic\",H34=TRUE),AND(B13=\"Intermediate\",H34=TRUE)),\"NO\",IF(ISBLANK('Design Input'!B138),\"YES\",'Design Input'!B138)))","v":"YES"},"Cable connected to source",null,null,"Total",{"$f":"SUM(G33:G47)","v":0}]
["Design Input 14",{"$f":"IF(B48=\"NO\",\"Line then Cable\",\"All Cable\")","v":"All Cable"},"Source to substation connection"]
[null,{"$f":"'Design Input'!D146","v":0},"Predominant cable type"]
[null,{"$f":"IF(OR(B13=\"Basic\",B13=\"Intermediate\"),H36,'Design Input'!D145)","v":0},"Cable length",{"$f":"IF(AND(B48=\"NO\",B51<=0.2),\"YES\",\"NO\")","v":"NO"},"OH & cable length ≤ 0.2km",{"$f":"IF(D51=\"YES\",\"Combined\",\"Separate\")","v":"Separate"},"Default s/s & pole electrodes",{"$f":"IF(F51=\"Separate\",20,\"\")","v":20},"Default pole term earth resistance"]
[null,{"$f":"IF(OR(B48=\"YES\",B13=\"Basic\",B13=\"Advanced - ASC Earthing\"),\"NO\",\"YES\")","v":"NO"},"Mod of pole term details permitted?",{"$f":"IF(B52=\"NO\",\"NO\",IF(ISBLANK('Design Input'!B158),\"NO\",'Design Input'!B158))","v":"NO"},"Modify pole term details",{"$f":"IF(ISBLANK('Design Input'!F163),\"\",'Design Input'!F163)","v":""},"Modified s/s & pole electrodes",{"$f":"IF(ISBLANK('Design Input'!F164),\"\",'Design Input'!F164)","v":20},"Modified pole term earth resistance"]
[null,null,null,null,null,{"$f":"IF(D52=\"YES\",F52,F51)","v":"Separate"},"Value used: s/s & pole electrodes",{"$f":"IF(D52=\"YES\",H52,H51)","v":20},"Value used in calculations"]
["Design Input 15",{"$f":"'Design Input'!B169","v":0},"Units",null,null,{"$f":"IF(B54=\"km2\",B55,IF(B55=\"0 to 749,999\",\"0 to 0.74\",IF(B55=\"750,000 to 3,999,999\",\"0.75 to 3.99\",IF(B55=\"4,000,000 to 12,999,999\",\"4.00 to 12.99\",\"13.00 or more\"))))","v":"13.00 or more"},"Value used in calculations"]
[null,{"$f":"'Design Input'!B170","v":0},"Area"]
["Design Input 16",{"$f":"'Design Input'!B175","v":0},"Network type"]
["Soil Resistivity Assistant",{"$f":"'Design Input'!C184","v":0},"Top resistivity from",{"$f":"AVERAGE(B57:B58)","v":0},"Top average resistivity",{"$f":"IF(D63<D59,\"Lo/Hi\",IF(D63>D59,\"Hi/Lo\",\"Uniform\"))","v":"Uniform"},"Hi/Lo, Lo/Hi or Uniform"]
[null,{"$f":"'Design Input'!D184","v":0},"Top resistivity to",{"$f":"AVERAGE(B59:B60)","v":0},"Middle average resistivity",{"$f":"IF(F57=\"Lo/Hi\",D59/D63,IF(F57=\"Hi/Lo\",D63/D59,1))","v":1},"Raw highest proportion"]
[null,{"$f":"'Design Input'!C185","v":0},"Middle resistivity from",{"$f":"AVERAGE(B61:B62)","v":0},"Bottom average resistivity",{"$f":"IF(F58<=1,1,IF(F58<=2,2,IF(F58<=3,3,IF(F58<=4,4,IF(F58<=5,5,IF(F58<=6,6,IF(F58<=7,7,IF(F58<=8,8,IF(F58<=9,9,10)))))))))","v":1},"Standard highest proportion"]
[null,{"$f":"'Design Input'!D185","v":0},"Middle resistivity from",{"$f":"AVERAGE(B63:B64)","v":0},"Top average depth",{"$f":"IF(F57=\"Lo/Hi\",CONCATENATE(\"1 : \",F59),IF(F57=\"Hi/Lo\",CONCATENATE(F59,\" : 1\"),\"1 : 1\"))","v":"1 : 1"},"Assign standard ratio"]
[null,{"$f":"'Design Input'!C186","v":0},"Bottom resistivity from",{"$f":"AVERAGE(B65:B66)","v":0},"Middle average depth"]
[null,{"$f":"'Design Input'!D186","v":0},"Bottom resistivity to",{"$f":"D60+D61","v":0},"Top & middle combined depth"]
[null,{"$f":"'Design Input'!E184","v":0},"Top depth from",{"$f":"IF(D62=0,0,ROUND(((D60/D62)*D57)+((D61/D62)*D58),0))","v":0},"Top & middle average resistivity"]
[null,{"$f":"'Design Input'!F184","v":0},"Top depth to",{"$f":"IF(D63<=25,25,IF(D63<=50,50,IF(D63<=75,75,IF(D63<=100,100,IF(D63<=150,150,IF(D63<=200,200,IF(D63<=300,300,IF(D63<=400,400,IF(D63<=500,500,IF(D63<=750,750,1000))))))))))","v":25},"Assign standard resistivity"]
[null,{"$f":"'Design Input'!E185","v":0},"Middle depth from",{"$f":"IF(D62<=3,2,IF(D62<=5,4,IF(D62<=7,6,IF(D62<=9,8,10))))","v":2},"Assign standard depth"]
[null,{"$f":"'Design Input'!F185","v":0},"Middle depth to"]
["Design Input 17",{"$f":"'Design Input'!B198","v":300},"Upper soil resistivity"]
["Design Input 18",{"$f":"'Design Input'!B202","v":"1 : 3"},"Upper / lower resistivity ratio",{"$f":"IF(B68=0,\"UNIFORM resistivity soil\",VLOOKUP(B68,'Data-General'!H2:I20,2,FALSE))","v":"LOW above HIGH resistivity soil"},"Soil type"]
[null,{"$f":"IF(B68=0,10,VLOOKUP(B68,'Data-General'!H2:J20,3,FALSE))","v":3},"U-L ratio",{"$f":"IF(B68=0,0,B67*VLOOKUP(B68,'Data-General'!H2:J20,3,FALSE))","v":900},"Lower soil resistivity"]
["Design Input 18A",{"$f":"'Design Input'!B211","v":2},"Soil depth",{"$f":"'Soil Depth Factor'!A27","v":1},"Soil depth factor"]
["Design Input 19A",{"$f":"'Design Input'!B223","v":"NO"},"Dispense with perimeter electrode",{"$f":"IF(AND(G11=\"Required\",B71=\"Yes\"),\"Omitted\",IF(AND(G11=\"Required\",B71=\"No\"),\"Required\",\"Not Applicable\"))","v":"Not Applicable"},"Value: Perimeter electrode"]
["Design Input 19",{"$f":"'Design Input'!B229","v":0},"Electrode tail length",{"$f":"IF(ISERROR('Data-HV Electrode Resistance'!C42),\"\",'Data-HV Electrode Resistance'!C42*(B67/25))","v":120000},"Electrode resistance excl network",{"$f":"D72*D70","v":120000},"Electrode resistance excl network x soil depth factor"]
[null,null,null,{"$f":"IF(ISERROR('Data-Network Contribution'!D31),\"\",'Data-Network Contribution'!D31)","v":0.85000000000000009},"Network contribution",{"$f":"D73*D70","v":0.85000000000000009},"Network contribution x soil depth factor"]
[null,null,null,{"$f":"IF(ISERR(1/((1/D72)+(1/D73))),20,1/((1/D72)+(1/D73)))","v":0.84999397920931408},"Overall earthing resistance",{"$f":"D74*D70","v":0.84999397920931408},"Overall earthing resistance x soil depth factor"]
["Design Input 20",{"$f":"IF(B13=\"Advanced - ASC Earthing\",50,IF(OR(B13=\"Basic\",B13=\"Intermediate\"),'Simple Calcs - Fault Current'!H44,IF(ISERR('Calculations-Fault Current'!B31),\"\",'Calculations-Fault Current'!B31)))","v":10000},"Total fault current"]
[null,{"$f":"IF(B13=\"Advanced - ASC Earthing\",100,IF(F53=\"Combined\",100,'Ground Current Default'!B70))","v":100},"% fault current into ground"]
[null,{"$f":"IF(OR(B13=\"Basic\",B13=\"Advanced - ASC Earthing\"),\"NO\",IF(ISBLANK('Design Input'!B261),\"NO\",'Design Input'!B261))","v":"NO"},"Modify % fault current",{"$f":"'Design Input'!B266","v":100},"Modified % fault current into ground",{"$f":"IF(B77=\"NO\",B76,D77)","v":100},"Value used in calculations"]
[null,{"$f":"IF(ISERR(B75*F77/100),\"\",B75*F77/100)","v":10000},"Fault current into ground"]
["Design Input 21",70,"Conductor XSA",{"$f":"B87/F72","v":7.7916114760853805E-2},"Current in HV electrode"]
[null,{"$f":"IF(ISERR('Calculations-Surface Area'!B22),\"\",'Calculations-Surface Area'!B22)","v":307.72348110429317},"Minimum HV electrode SA"]
[null,{"$f":"'Design Input'!B297","v":0},"Number of 'tail' conductors"]
[null,{"$f":"'Calculations-Surface Area'!B14","v":0},"SA of perimeter electrode"]
[null,{"$f":"'Calculations-Surface Area'!B13","v":0},"SA of earth rods"]
[null,{"$f":"'Calculations-Surface Area'!B15","v":0},"SA of tail"]
[null,{"$f":"'Calculations-Surface Area'!B16","v":0},"Total SA",{"$f":"IF(B85>B80,\"YES\",\"NO\")","v":"NO"},"SA Criteria Met?"]
[null,{"$f":"IF(ISERR(B78*F74),\"\",B78*F74)","v":8499.9397920931406},"Calculated EPR"]
[null,{"$f":"IF(ISERR(B86*1.1),\"\",B86*1.1)","v":9349.9337713024561},"Design EPR"]
["Design Input 22",{"$f":"IF(B13=\"Advanced - ASC Earthing\",10,3)","v":3},"Fault clearance time"]
[null,{"$f":"IF(OR(B13=\"Basic\",B13=\"Advanced - ASC Earthing\"),\"NO\",IF(ISBLANK('Design Input'!B344),\"NO\",'Design Input'!B344))","v":"NO"},"Modify clearance time"]
[null,100,"CB time"]
[null,{"$f":"'Design Input'!E350","v":0},"CT ratio - primary"]
[null,{"$f":"'Design Input'!G350","v":0},"CT ratio - secondary"]
[null,{"$f":"'Design Input'!E351","v":0},"IDMT current setting value"]
[null,{"$f":"'Design Input'!F351","v":0},"IDMT current setting units"]
[null,{"$f":"IF(B94=\"Primary Amps\",B93,IF(B94=\"Secondary Amps\",B93*B91/B92,IF(B94=\"Percent\",B93*B91/100,B93*B91)))","v":0},"IDMT current setting primary equiv"]
[null,{"$f":"'Design Input'!E353","v":0},"Time-current characteristic"]
[null,{"$f":"'Design Input'!E354","v":0},"TM setting"]
[null,{"$f":"IF(ISERROR('Calculations-IDMT Op Time'!C17),\"\",'Calculations-IDMT Op Time'!C17)","v":0},"Protection operating time"]
[null,{"$f":"SUM(B90,B98)/1000","v":0.1},"Total fault clearance time"]
[null,{"$f":"IF(B89=\"NO\",B88,B99)","v":3},"Value used in calculations"]
[null,{"$f":"IF(B13=\"Advanced - ASC Earthing\",10,IF(ISERR(B100+0.4),\"\",B100+0.4))","v":3.4},"Design HV fault clearance time"]
["Design Input 23",{"$f":"VLOOKUP(D102,'Data-Safety Voltages'!B38:D41,3,FALSE)","v":156},"HV Touch voltage limit - soil","Soil or outdoor concrete","Stance grating limit = +10s step voltage limit for soil or wet concrete i.e. someone stepping onto the grating",{"$f":"IF(AND(B116=\"Soil or outdoor concrete\",OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\")),B102,\"\")","v":""},"Value used in calculation - soil"]
[null,{"$f":"VLOOKUP(D103,'Data-Safety Voltages'!B38:D41,3,FALSE)","v":198},"HV Touch voltage limit - indoor concrete","Indoor concrete",null,{"$f":"IF(AND(B116=\"Indoor concrete\",OR(E10=\"B\",E10=\"F\",E10=\"H\")),B103,\"\")","v":""},"Value used in calculation - indoor concrete"]
[null,{"$f":"VLOOKUP(D104,'Data-Safety Voltages'!B38:D41,3,FALSE)","v":897},"HV Touch voltage limit - tarmac","100mm tarmac",null,{"$f":"IF(AND(B116=\"100mm tarmac\",OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\")),B104,\"\")","v":""},"Value used in calculation - tarmac"]
[null,11012,"HV Touch voltage limit - stance grating","Stance grating",null,{"$f":"IF(AND(B116=\"Stance grating\",OR(E10=\"B\",E10=\"F\",E10=\"H\")),B105,\"\")","v":""},"Value used in calculation - stance grating"]
[null,{"$f":"VLOOKUP(D106,'Data-Safety Voltages'!B48:D51,3,FALSE)","v":156},"EHV Touch voltage limit - soil","Soil or outdoor concrete","Stance grating limit = +10s step voltage limit for soil or wet concrete i.e. someone stepping onto the grating",{"$f":"IF(AND(B116=\"Soil or outdoor concrete\",OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\")),B106,\"\")","v":""},"Value used in calculation - soil"]
[null,{"$f":"VLOOKUP(D107,'Data-Safety Voltages'!B48:D51,3,FALSE)","v":198},"EHV Touch voltage limit - indoor concrete","Indoor concrete",null,{"$f":"IF(AND(B116=\"Indoor concrete\",OR(E10=\"B\",E10=\"F\",E10=\"H\")),B107,\"\")","v":""},"Value used in calculation - indoor concrete"]
[null,{"$f":"VLOOKUP(D108,'Data-Safety Voltages'!B48:D51,3,FALSE)","v":897},"EHV Touch voltage limit - tarmac","100mm tarmac",null,{"$f":"IF(AND(B116=\"100mm tarmac\",OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\")),B108,\"\")","v":""},"Value used in calculation - tarmac"]
[null,11012,"EHV Touch voltage limit - stance grating","Stance grating",null,{"$f":"IF(AND(B116=\"Stance grating\",OR(E10=\"B\",E10=\"F\",E10=\"H\")),B109,\"\")","v":""},"Value used in calculation - stance grating"]
[null,{"$f":"'% Touch Voltage'!C30","v":21},"Max touch voltage %EPR "]
[null,{"$f":"IF(ISERR((B110*B87)/100),\"\",(B110*B87)/100)","v":1963.4860919735158},"HV calculated touch voltage",null,null,null,null,{"$f":"IF(ISERR((B110*F140)/100),\"\",(B110*F140)/100)","v":0},"EHV calculated touch voltage"]
[null,{"$f":"IF(B111<=B102,\"YES\",\"NO\")","v":"NO"},"HV VTOUCH ≤ Safety limit for soil",{"$f":"IF(AND(B116=\"Soil or outdoor concrete\",OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\")),B112,\"\")","v":""},"HV value used in calculation - soil",null,null,{"$f":"IF(H111<=B106,\"YES\",\"NO\")","v":"YES"},"EHV VTOUCH ≤ Safety limit for soil",{"$f":"IF(AND(B116=\"Soil or outdoor concrete\",OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\")),H112,\"\")","v":""},"EHV value used in calculation - soil"]
[null,{"$f":"IF(B111<=B104,\"YES\",\"NO\")","v":"NO"},"HV VTOUCH ≤ Safety limit for tarmac",{"$f":"IF(AND(B116=\"100mm tarmac\",OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\")),B113,\"\")","v":""},"HV value used in calculation - tarmac",null,null,{"$f":"IF(H111<=B108,\"YES\",\"NO\")","v":"YES"},"EHV VTOUCH ≤ Safety limit for tarmac",{"$f":"IF(AND(B116=\"100mm tarmac\",OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\")),H113,\"\")","v":""},"EHV value used in calculation - tarmac"]
[null,{"$f":"IF(B111<=B103,\"YES\",\"NO\")","v":"NO"},"HV VTOUCH ≤ Safety limit for indoor concrete",{"$f":"IF(AND(B116=\"Indoor concrete\",OR(E10=\"B\",E10=\"F\",E10=\"H\")),B114,\"\")","v":""},"HV value used in calculation - indoor concrete",{"$f":"IF(OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\"),\"Soil or outdoor concrete\",\"Indoor concrete\")","v":"Indoor concrete"},"Ground surface covering options",{"$f":"IF(H111<=B107,\"YES\",\"NO\")","v":"YES"},"EHV VTOUCH ≤ Safety limit for indoor concrete",{"$f":"IF(AND(B116=\"Indoor concrete\",OR(E10=\"B\",E10=\"F\",E10=\"H\")),H114,\"\")","v":""},"EHV value used in calculation - indoor concrete"]
[null,{"$f":"IF(B111<=B105,\"YES\",\"NO\")","v":"YES"},"HV VTOUCH ≤ Safety limit for stance grating",{"$f":"IF(AND(B116=\"Stance grating\",OR(E10=\"B\",E10=\"F\",E10=\"H\")),B115,\"\")","v":""},"HV value used in calculation - stance grating",{"$f":"IF(OR(E10=\"A\",E10=\"C\",E10=\"E\",E10=\"G\"),\"100mm tarmac\",\"Stance grating\")","v":"Stance grating"},null,{"$f":"IF(H111<=B109,\"YES\",\"NO\")","v":"YES"},"EHV VTOUCH ≤ Safety limit for stance grating",{"$f":"IF(AND(B116=\"Stance grating\",OR(E10=\"B\",E10=\"F\",E10=\"H\")),H115,\"\")","v":""},"EHV value used in calculation - stance grating"]
[null,{"$f":"'Design Input'!B445","v":0},"Ground surface covering"]
["Design Input 24",{"$f":"IF(ISBLANK('Design Input'!B452),\"\",'Design Input'!B452)","v":""},"LV neutral multiply earthed?"]
[null,{"$f":"IF(AND(G10=\"YES\",B117=\"YES\"),\"\",B102)","v":156},"[HV Fault] LV system limit - single earth"]
[null,{"$f":"IF(AND(G10=\"YES\",B117=\"YES\"),\"\",IF(B87<=B118,\"YES\",\"NO\"))","v":"NO"},"[HV Fault] EPR < LV system limit - single earth"]
[null,{"$f":"IF(AND(G10=\"YES\",B117=\"NO\"),\"\",2*B102)","v":312},"[HV Fault] LV system limit - multiple earth"]
[null,{"$f":"IF(AND(G10=\"YES\",B117=\"NO\"),\"\",IF(B87<=B120,\"YES\",\"NO\"))","v":"NO"},"[HV Fault] EPR < LV system limit - multiple earth"]
[null,1150,"[HV Fault] LV Customer's telecom equipment limit"]
[null,{"$f":"IF(B87<=B122,\"YES\",\"NO\")","v":"NO"},"[HV Fault] EPR < LV Customer's telecom equipment limit"]
[null,430,"[HV Fault] ITU limit"]
[null,{"$f":"IF(B87<=B124,\"YES\",\"NO\")","v":"NO"},"[HV Fault] EPR < ITU limit"]
[null,{"$f":"IF(B125=\"NO\",\"HOT\",\"COLD\")","v":"HOT"},"[HV Fault] ITU Classifiaction"]
[null,{"$f":"IF(OR(AND(G10=\"YES\",B117=\"NO\",B119=\"NO\"),AND(G10=\"YES\",B117=\"YES\",B121=\"NO\"),AND(G10=\"NO\",B119=\"NO\"),AND(G10=\"NO\",B121=\"NO\"),B123=\"NO\"),\"HEPR\",\"LEPR\")","v":"HEPR"},"[HV Fault] NGED 3rd party impact classification"]
[null,{"$f":"IF(OR(AND(G10=\"YES\",B117=\"YES\"),ISERROR('Data-Transfer Voltages'!D38)),\"\",'Data-Transfer Voltages'!D38)","v":156},"[EHV Fault] LV system limit - single earth"]
[null,{"$f":"IF(AND(G10=\"YES\",B117=\"YES\"),\"\",IF(F140<=B128,\"YES\",\"NO\"))","v":"YES"},"[EHV Fault] Transfer < LV system limit - single"]
[null,{"$f":"IF(OR(AND(G10=\"YES\",B117=\"NO\"),ISERROR('Data-Transfer Voltages'!D38)),\"\",2*'Data-Transfer Voltages'!D38)","v":312},"[EHV Fault] LV system limit - multiple earth"]
[null,{"$f":"IF(AND(G10=\"YES\",B117=\"NO\"),\"\",IF(F140<=B130,\"YES\",\"NO\"))","v":"YES"},"[EHV Fault] Transfer < LV system limit - multiple"]
[null,{"$f":"IF(F22<=0.2,1700,1150)","v":1150},"[EHV Fault] LV Customer's telecom equipment limit"]
[null,{"$f":"IF(F140<=B132,\"YES\",\"NO\")","v":"YES"},"[EHV Fault] Transfer < LV Customer's telecom equipment limit"]
[null,{"$f":"IF(F22<=0.2,650,430)","v":430},"[EHV Fault] ITU limit"]
[null,{"$f":"IF(F140<=B134,\"YES\",\"NO\")","v":"YES"},"[EHV Fault] Transfer < ITU limit"]
[null,{"$f":"IF(B135=\"NO\",\"HOT\",\"COLD\")","v":"COLD"},"[EHV Fault] ITU Classification"]
[null,{"$f":"IF(OR(AND(G10=\"YES\",B117=\"NO\",B129=\"NO\"),AND(G10=\"YES\",B117=\"YES\",B131=\"NO\"),AND(G10=\"NO\",B129=\"NO\"),AND(G10=\"NO\",B131=\"NO\"),B133=\"NO\"),\"HEPR\",\"LEPR\")","v":"LEPR"},"[EHV Fault] NGED 3rd party impact classification"]
["Design Input 25",{"$f":"'Transfer Potential Default'!C55","v":0},"% transfer voltage"]
[null,{"$f":"F20*(B138/100)","v":0},"Transfer voltage"]
[null,{"$f":"IF(OR(B13=\"Basic\",B13=\"Advanced - ASC Earthing\",B48=\"NO\"),\"NO\",IF(ISBLANK('Design Input'!B373),\"NO\",'Design Input'!B373))","v":"NO"},"Modify transfer voltage",{"$f":"'Design Input'!B378","v":0},"Modified transfer voltage",{"$f":"IF(B140=\"NO\",B139,D140)","v":0},"Design transfer voltage"]
["Design Input 26",{"$f":"IF(OR(ISNA(B127),ISNA(B137)),\"HEPR\",IF(AND(B127=\"LEPR\",B137=\"LEPR\"),\"LEPR\",\"HEPR\"))","v":"HEPR"},"3rd party impact - overall",{"$f":"IF(AND(B125=\"YES\",B135=\"YES\"),\"COLD\",\"HOT\")","v":"HOT"},"ITU Classification - overall"]
[null,{"$f":"IF('Data-HV to LV Separation SNE'!D51=0,0,'Data-HV to LV Separation SNE'!D51)","v":60},"Theoretical separation - general",{"$f":"IF(B142>40,40,B142)","v":40},"Practicable separation - general",{"$f":"D142","v":40},"Value used in calculations - general"]
[null,{"$f":"IF(AND(G10=\"YES\",B117=\"YES\"),\"\",IF(AND('Data-HV to LV Separation SNE'!D51=0,G10=\"YES\"),0,IF(AND('Data-HV to LV Separation SNE'!D51=0,G10=\"NO\"),0,'Data-HV to LV Separation SNE'!D51)))","v":60},"Theoretical separation - SNE LV",{"$f":"IF(B143>40,40,B143)","v":40},"Practicable separation - SNE LV",{"$f":"IF(AND(G10=\"YES\",B117=\"YES\"),\"\",D143)","v":40},"Value used in calculations - SNE LV"]
[null,{"$f":"IF(AND(G10=\"YES\",B117=\"NO\"),\"\",IF(AND('Data-HV to LV Separation CNE'!D51=0,G10=\"YES\"),0,IF(AND('Data-HV to LV Separation CNE'!D51=0,G10=\"NO\"),0,'Data-HV to LV Separation CNE'!D51)))","v":28},"Theoretical separation - CNE LV",{"$f":"IF(B144>40,40,B144)","v":28},"Practicable separation - CNE LV",{"$f":"IF(AND(G10=\"YES\",B117=\"NO\"),\"\",D144)","v":28},"Value used in calculations - CNE LV"]
[null,{"$f":"IF(AND(G10=\"YES\",B141=\"LEPR\"),\"COMBINED HV & LV Earth Electrode\",IF(AND(G10=\"YES\",B141=\"HEPR\"),\"SEPARATE HV & LV Earth Electrodes\",\"\"))","v":"SEPARATE HV & LV Earth Electrodes"},"Combined or separate electrodes",{"$f":"IF(LEFT(B145,8)=\"COMBINED\",\"Inserted\",IF(LEFT(B145,8)=\"SEPARATE\",\"Removed\",\"\"))","v":"Removed"},"HV/LV Earth Link",{"$f":"IF(LEFT(B145,8)=\"SEPARATE\",\"YES\",\"\")","v":"YES"},"Separate electrode?"]
[null,{"$f":"'Design Input'!B554","v":0},"Length of LV electrode",{"$f":"IF(B146=0,\"\",IF(AND(G10=\"YES\",LEFT(B145,8)=\"SEPARATE\"),B146,\"\"))","v":""},"Value used in calculations - length"]
[null,{"$f":"'Data-LV Electrode Resistance'!C40*(B67/25)*D70","v":6.8640000000000008},"LV electrode resistance",{"$f":"IF(B147=0,\"\",IF(AND(G10=\"YES\",LEFT(B145,8)=\"SEPARATE\"),B147,\"\"))","v":6.8640000000000008},"Value used in calculations - resistance"]

{"sheet":"Title Page","index":9,"n_rows":49,"n_cols":5,"rows_kept":49,"cut":false,"hidden":true,"merged":[[23,0,23,1],[46,4,46,5],[11,0,11,7],[13,0,13,7],[15,0,15,7],[21,0,21,1],[48,4,48,5],[25,0,25,1],[25,2,25,6],[28,0,28,1],[30,0,30,1],[32,0,32,1],[34,0,34,1],[37,0,37,1],[39,0,39,1],[48,0,48,3]]}
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["EARTHING DESIGN REPORT"]
[]
["FOR"]
[]
[{"$f":"UPPER('Data Entered'!B10)","v":"0"}]
[]
[]
[]
[]
[]
["Licence Area:",null,{"$f":"'Data Entered'!B6","v":0}]
[]
["Substation:",null,{"$f":"'Data Entered'!B7","v":0}]
[]
["Address:",null,{"$f":"'Data Entered'!B8","v":0}]
[]
[]
["Earthing Design By:",null,{"$f":"'Data Entered'!B2","v":0}]
[]
[{"$f":"IF('Data Entered'!B2=\"ICP\",\"ICP Name:\",\"NGED Managed Unit:\")","v":"NGED Managed Unit:"},null,{"$f":"'Data Entered'!B4","v":0}]
[]
[{"$f":"IF('Data Entered'!B2=\"ICP\",\"ICP Designer:\",\"NGED Designer:\")","v":"NGED Designer:"},null,{"$f":"'Data Entered'!B3","v":0}]
[]
[{"$f":"IF('Data Entered'!B2=\"ICP\",\"ICP Job Reference:\",\"NGED Crown Enquiry:\")","v":"NGED Crown Enquiry:"},null,{"$f":"'Data Entered'!B5","v":0}]
[]
[]
["Date:",null,{"$f":"'Publish Report'!C78","v":"26/03/2020"}]
[]
["Time:",null,{"$f":"'Publish Report'!C79","v":"17:03:58"}]
[]
[]
[]
[]
[]
[]
["Report Compiled Using Earthing Design Tool:",null,null,null,{"$f":"Disclaimer!E47","v":"TP21G_EDT_VERSION 2b"}]
[]
[{"$f":"'Publish Report'!C75","v":"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"},null,null,null,"Page 1 of 10"]

{"sheet":"Report Disclaimer","index":10,"n_rows":50,"n_cols":5,"rows_kept":50,"cut":false,"hidden":true,"merged":[[49,0,49,3],[49,4,49,5],[1,0,1,7],[31,1,34,6],[46,0,46,7],[36,1,39,6],[26,1,29,6],[22,1,24,6],[3,1,6,6],[19,1,20,6],[16,1,17,6],[11,1,14,6],[8,1,9,6]]}
[]
["DISCLAIMER"]
[]
[null,"National Grid Electricity Distribution (NGED) has developed a spreadsheet calculation tool (Excel Workbook) in order to analyse the performance of a proposed earthing system without having to employ specialist consultants or advanced earthing software packages."]
[]
[]
[]
[]
[null,"The spreadsheet calculation tool has been prepared for use on the NGED network only. "]
[]
[]
[null,"The spreadsheet calculation tool uses data derived from CDEGS studies of the proposed substation arrangement. It also uses the formulae and guidelines contained within ENA Engineering Recommendation S34 and ENA Technical Specification 41-24."]
[]
[]
[]
[]
[null,"[CDEGS is \"Current Distribution Electromagnetic Interference Grounding and Soil Structure Analysis\" software from Safe Engineering Services & Technologies Ltd]"]
[]
[]
[null,"This Earthing Design Report is the output from the spreadsheet calculation tool."]
[]
[]
[null,"The information contained within this report is based on data supplied by the End User of the spreadsheet calculation tool. NGED shall not be liable for any incidents or costs incurred due to inaccurate information."]
[]
[]
[]
[null,"It is the responsibility of the End User of the spreadsheet calculation tool to ensure that any installation work is carried out as per the recommendations contained within this Earthing Design Report. NGED shall not be liable for any incidents or costs incurred due to non-conforming installation."]
[]
[]
[]
[]
[null,"The Earthing Design Report, spreadsheet calculation tool, and the associated data and calculations are provided \"as is\" and for use at your own risk. NGED makes no warranties as to performance, fitness for purpose, or any other warranties, whether expressed or implied."]
[]
[]
[]
[]
[null,"Under no circumstances will NGED be liable for direct, indirect, special, incidental, or consequential damages resulting from the use, misuse, or inability to use the Earthing Design Report, spreadsheet calculation tool (Excel Workbook), and the associated data and calculations. "]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["© National Grid Electricity Distribution 2022"]
[]
[]
[{"$f":"'Publish Report'!C75","v":"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"},null,null,null,"Page 2 of 10"]

{"sheet":"Report","index":11,"n_rows":395,"n_cols":8,"rows_kept":395,"cut":false,"hidden":true,"merged":[[385,0,385,5],[381,0,381,6],[383,0,383,5],[320,0,320,6],[367,0,367,6],[379,0,379,7],[348,0,348,6],[336,0,336,5],[337,0,337,5],[338,0,338,5],[339,0,339,5],[340,0,340,5],[341,0,341,5],[352,5,352,6],[353,0,353,5],[354,0,354,5],[355,0,355,5],[350,0,350,5],[346,0,346,7],[325,0,325,5],[326,0,326,5],[327,0,327,5],[328,0,328,5],[332,0,332,7],[384,0,384,5],[271,0,271,1],[271,2,271,3],[271,4,271,5],[253,0,253,2],[198,0,198,3],[198,4,198,5],[277,0,277,1],[277,2,277,4],[277,5,277,6],[274,4,274,5],[268,0,268,1],[268,3,268,4],[269,0,269,1],[269,3,269,4],[287,5,287,6],[273,0,273,1],[273,2,273,3],[273,4,273,5],[249,0,249,7],[251,0,251,6],[220,0,220,3],[221,0,221,3],[222,0,222,3],[70,0,70,3],[70,4,70,6],[84,0,84,4],[84,5,84,6],[90,0,90,4],[68,0,68,3],[68,4,68,6],[69,0,69,3],[174,0,174,4],[78,4,78,6],[71,0,71,3],[132,5,132,6],[152,0,152,4],[153,0,153,4],[157,0,157,4],[158,0,158,4],[162,0,162,4],[163,0,163,4],[151,0,151,4],[156,0,156,4],[71,4,71,6],[72,4,72,6],[77,0,77,4],[83,0,83,4],[394,0,394,3],[394,4,394,5],[210,0,210,4],[211,0,211,4],[214,0,214,4],[215,0,215,4],[201,0,201,4],[202,0,202,4],[203,0,203,4],[204,0,204,4],[205,0,205,4],[207,0,207,4],[206,0,206,4],[201,5,207,5],[267,0,267,1],[286,0,286,1],[286,2,286,4],[286,5,286,6],[284,0,284,1],[270,0,270,1],[270,3,270,4],[248,4,248,5],[214,5,215,5],[214,6,215,6],[5,5,5,6],[7,3,7,4],[7,5,7,6],[8,3,8,4],[9,3,9,4],[69,4,69,6],[283,0,283,1],[283,2,283,4],[283,5,283,6],[280,0,280,1],[280,2,280,4],[280,5,280,6],[281,0,281,1],[281,2,281,4],[281,5,281,6],[282,0,282,1],[282,2,282,4],[282,5,282,6],[82,0,82,4],[82,5,82,6],[80,0,80,4],[80,5,80,6],[79,0,79,4],[78,0,78,3],[20,0,20,4],[20,5,20,6],[28,0,29,4],[28,5,29,6],[28,7,29,7],[0,0,0,7],[9,0,9,2],[8,0,8,2],[18,0,18,4],[18,5,18,6],[3,1,3,6],[12,0,12,3],[12,4,12,6],[13,0,13,4],[13,5,13,6],[16,0,16,3],[16,4,16,6],[4,0,4,4],[4,5,4,6],[14,0,14,4],[14,5,14,6],[11,0,11,4],[11,5,11,6],[5,0,5,4],[22,7,26,7],[54,0,55,6],[61,0,61,4],[61,5,61,6],[60,0,60,4],[62,0,63,3],[31,0,32,4],[31,5,32,6],[59,1,59,6],[40,0,40,3],[41,0,41,3],[39,0,39,5],[42,0,42,3],[51,0,52,2],[51,3,52,5],[48,0,48,3],[48,4,48,5],[49,0,49,7],[31,7,32,7],[34,0,36,1],[34,2,36,6],[60,5,60,6],[83,5,83,6],[101,0,101,4],[101,5,101,6],[102,0,102,4],[102,5,102,6],[103,0,103,4],[103,5,103,6],[108,0,108,4],[113,0,113,4],[90,5,90,6],[98,4,98,5],[91,0,91,4],[91,5,91,6],[118,0,118,3],[253,3,253,6],[179,0,179,4],[228,0,229,0],[228,1,228,5],[231,1,232,5],[231,0,232,0],[124,0,124,4],[125,0,125,4],[127,0,127,4],[126,0,126,4],[175,0,175,4],[175,5,175,6],[167,0,167,4],[168,0,168,4],[139,0,139,4],[132,0,132,4],[234,1,236,5],[234,0,236,0],[135,0,135,4],[136,0,136,4],[137,0,137,4],[138,0,138,4],[223,0,223,3],[220,4,220,6],[221,4,221,6],[222,4,222,6],[223,4,223,6],[118,4,118,6],[201,6,207,6],[214,7,215,7],[210,5,211,5],[210,6,211,6],[210,7,211,7],[201,7,207,7],[248,0,248,3],[276,2,276,4],[276,5,276,6],[275,0,275,1],[275,2,275,3],[275,4,275,5],[256,0,256,5],[257,0,257,5],[259,0,259,5],[263,0,263,7],[265,0,265,6],[267,2,267,5],[272,0,272,1],[272,2,272,3],[272,4,272,5],[274,0,274,1],[274,2,274,3],[276,0,276,1],[373,0,373,5],[374,0,374,5],[375,0,375,5],[345,0,345,3],[345,4,345,5],[369,0,369,4],[369,5,369,6],[370,0,370,2],[370,3,370,6],[371,0,371,5],[372,0,372,5],[356,0,356,5],[357,0,357,5],[359,0,359,5],[360,0,360,5],[364,0,364,7],[366,0,366,6],[351,0,351,5],[352,0,352,4],[334,0,334,6],[317,0,317,7],[319,0,319,6],[324,0,324,2],[324,3,324,6],[322,0,323,2],[322,3,323,6],[311,0,311,4],[311,5,311,6],[312,0,312,2],[312,3,312,6],[313,0,313,4],[313,5,313,6],[288,0,288,1],[288,2,288,4],[288,5,288,6],[278,0,278,1],[278,2,278,4],[278,5,278,6],[279,0,279,1],[279,2,279,4],[279,5,279,6],[287,2,287,4],[287,0,287,1],[284,2,284,4],[284,5,284,6],[285,0,285,1],[285,2,285,4],[285,5,285,6],[302,0,302,5],[306,0,306,7],[309,0,309,6],[289,0,289,1],[289,2,289,4],[289,5,289,6],[290,0,290,1],[290,2,290,4],[290,5,290,6],[297,0,297,3],[297,4,297,5],[308,0,308,6],[300,0,300,6],[298,0,298,7],[8,5,8,6],[9,5,9,6],[258,0,258,5],[180,0,180,4],[180,5,180,6],[144,0,144,4],[144,5,144,6],[148,0,148,3],[148,4,148,5],[254,0,254,5],[255,0,255,5],[98,0,98,3],[89,0,89,4],[89,5,89,6],[77,5,77,6],[72,0,72,3],[79,5,79,6],[81,0,81,4],[81,5,81,6],[62,4,63,6],[22,0,26,4],[22,5,26,6],[19,0,19,4],[19,5,19,6]]}
["KEYNOTE DESIGN INFORMATION"]
[]
[]
["Format",{"$f":"'Data Entered'!B10","v":0}]
["International Telecommunication Union (ITU) Classification",null,null,null,null,{"$f":"PROPER('Data Entered'!D141)","v":"Hot"}]
["NGED Third Party Impact Classification",null,null,null,null,{"$f":"IF('Data Entered'!B141=\"HEPR\",\"High EPR\",\"Low EPR\")","v":"High EPR"}]
[]
[null,null,null,"HV Faults",null,"EHV Faults"]
["EPR",null,null,{"$f":"'Data Entered'!B87","v":9349.9337713024561},null,{"$f":"'Data Entered'!F140","v":0},null,"V"]
["Earth Fault Clearance Time",null,null,{"$f":"'Data Entered'!B101","v":3.4},null,{"$f":"'Data Entered'!F23","v":3.4},null,"s"]
[]
["HV \"Perimeter\" Electrode",null,null,null,null,{"$f":"'Data Entered'!D71","v":"Not Applicable"}]
["Minimum Length of Insulated HV \"Tail\" Electrode",null,null,null,{"$f":"IF('Data Entered'!G12=\"YES\",\"To achieve HV separation distance\",\"\")","v":""},null,null,"m"]
["Minimum Length of Bare HV \"Tail\" Electrode",null,null,null,null,{"$f":"'Data Entered'!B72","v":0},null,"m"]
["Number of Conductors (Min 100mm Apart) in 'Tail' Electrode",null,null,null,null,{"$f":"'Data Entered'!B81","v":0}]
[]
["Operator's Standing Surface",null,null,null,{"$f":"'Data Entered'!B116","v":0}]
[]
["HV & LV Earth Electrodes",null,null,null,null,{"$f":"PROPER(LEFT('Data Entered'!B145,8))","v":"Separate"}]
["HV / LV Link",null,null,null,null,{"$f":"'Data Entered'!D145","v":"Removed"}]
["Length of LV Electrode",null,null,null,null,{"$f":"'Data Entered'!D146","v":""},null,"m"]
[]
["Minimum HV Separation Distance to Railway, Tramway, Metallic Pipeline, Bulk Storage Tanks For Petroleum or Flammable Liquids, Zoo, Stable, Pond/Lake Used For Commercial Fishing, Outdoor Swimming Pool, Outdoor Paddling Pool, Outdoor Shower, Telephone Exchange or Customer TT Electrode",null,null,null,null,{"$f":"'Data Entered'!F142","v":40},null,"m"]
[]
[]
[]
[]
[]
["Minimum HV separation distance to LV system whose neutral is earthed at a single point",null,null,null,null,{"$f":"'Data Entered'!F143","v":40},null,"m"]
[]
[]
["Minimum HV separation distance to LV system whose neutral is earthed at multiple points",null,null,null,null,{"$f":"'Data Entered'!F144","v":28},null,"m"]
[]
[]
["Comments",null,{"$f":"IF(LEFT('Data Entered'!B12,2)=\"NO\",\"\",\"Employ earthing specialist to review or carry out bespoke design where actual separation distance does not exceed minimum permitted by at least 5m.\")","v":"Employ earthing specialist to review or carry out bespoke design where actual separation distance does not exceed minimum permitted by at least 5m."}]
[]
[]
[]
[]
["Target Commissioning Resistance Values"]
["HV Earth Electrode alone #",null,null,null,"≤",{"$f":"'Data Entered'!F72","v":120000},"Ω"]
["LV Earth Electrode alone #",null,null,null,"≤",{"$f":"'Data Entered'!D147","v":6.8640000000000008},"Ω"]
["HV Earth Electrode on completion $",null,null,null,"≤",{"$f":"'Data Entered'!F74","v":0.84999397920931408},"Ω"]
["# prior to connecting HV cables, LV cables, and bonds to customer earthing system"]
["$ after connecting HV cables, LV cables, and bonds to customer earthing system"]
[]
[]
[]
[{"$f":"'Publish Report'!C75","v":"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"},null,null,null,"Page 3 of 10"]
["EARTHING DESIGN REPORT"]
[]
["This report has been prepared using",null,null,{"$f":"CONCATENATE(\"Earthing Design Tool \",'Data-General'!A2)","v":"Earthing Design Tool TP21G_EDT_VERSION 2b"}]
[]
[]
["A summary of the technical information and calculation results is listed below. Further information can be found in the Appendices:"]
[]
[]
["DISTRIBUTION SUBSTATION"]
[]
["Format",{"$f":"'Data Entered'!B10","v":0}]
["Voltage",null,null,null,null,{"$f":"'Data Entered'!B14","v":0},null,"V"]
["Cable Connected To Source",null,null,null,null,{"$f":"'Data Entered'!B48","v":"YES"}]
["Problematic Location",null,null,null,{"$f":"'Data Entered'!B12","v":0}]
[]
[]
[]
["SOIL RESISTIVITY MODEL"]
[]
["Resistivity of Upper Soil Layer",null,null,null,{"$f":"'Data Entered'!B67","v":300},null,null,"Ωm"]
["Thickness of Upper Soil Layer",null,null,null,{"$f":"'Data Entered'!B70","v":2},null,null,"m"]
["Resistivity of Lower Soil Layer",null,null,null,{"$f":"'Data Entered'!D69","v":900},null,null,"Ωm"]
["Assumed Thickness of Lower Soil Layer",null,null,null,"Infinite",null,null,"m"]
["Comments",null,null,null,{"$f":"'Data Entered'!D68","v":"LOW above HIGH resistivity soil"}]
[]
[]
["HV ELECTRODE"]
[]
["\"Perimeter\" Electrode",null,null,null,null,{"$f":"'Data Entered'!D71","v":"Not Applicable"}]
["Minimum Length of Insulated HV \"Tail\" Electrode",null,null,null,{"$f":"IF('Data Entered'!G12=\"YES\",\"To achieve HV separation distance\",\"\")","v":""},null,null,"m"]
["Minimum Length of Bare HV \"Tail\" Electrode",null,null,null,null,{"$f":"'Data Entered'!B72","v":0},null,"m"]
["Number of Conductors (Min 100mm Apart) in 'Tail' Electrode",null,null,null,null,{"$f":"'Data Entered'!B81","v":0}]
["Electrode Cross Sectional Area",null,null,null,null,{"$f":"'Data Entered'!B79","v":70},null,"mm2"]
["Electrode Resistance Excluding Network Contribution",null,null,null,null,{"$f":"'Data Entered'!F72","v":120000},null,"Ω"]
["Network Contribution To Electrode Resistance",null,null,null,null,{"$f":"'Data Entered'!F73","v":0.85000000000000009},null,"Ω"]
["Electrode Resistance Including Network Contribution",null,null,null,null,{"$f":"'Data Entered'!F74","v":0.84999397920931408},null,"Ω"]
[]
[]
["HV EARTH FAULT CURRENT"]
[]
["Total Earth Fault Current",null,null,null,null,{"$f":"'Data Entered'!B75","v":10000},null,"A"]
["Percentage of fault current flowing into the ground",null,null,null,null,{"$f":"'Data Entered'!F77","v":100},null,"%"]
["Ground Return Current",null,null,null,null,{"$f":"'Data Entered'!B78","v":10000},null,"A"]
[]
[]
[]
[]
[]
[]
[{"$f":"'Publish Report'!C75","v":"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"},null,null,null,"Page 4 of 10"]
["HV ELECTRODE SURFACE AREA"]
[]
["Minimum Surface Area Required",null,null,null,null,{"$f":"'Data Entered'!B80","v":307.72348110429317},null,"mm2"]
["Actual Surface Area",null,null,null,null,{"$f":"'Data Entered'!B85","v":0},null,"mm2"]
["Surface Area Requirement Met",null,null,null,null,{"$f":"'Data Entered'!D85","v":"NO"}]
[]
[]
["EARTH POTENTIAL RISE"]
[null,null,null,null,null,"HV Fault","EHV Fault"]
["Earth Potential Rise",null,null,null,null,{"$f":"'Data Entered'!B87","v":9349.9337713024561},{"$f":"'Data Entered'!F140","v":0},"V"]
[]
[]
["FAULT CLEARANCE TIME"]
[null,null,null,null,null,"HV Fault","EHV Fault"]
["Earth Fault Clearance Time",null,null,null,null,{"$f":"'Data Entered'!B101","v":3.4},{"$f":"'Data Entered'!F23","v":3.4},"s"]
[]
[]
["OPERATOR'S STANDING SURFACE"]
[]
["Selected Operator's Standing Surface",null,null,null,{"$f":"'Data Entered'!B116","v":0}]
[]
[]
["SAFETY LIMITS FOR TOUCH VOLTAGE"]
[]
[null,null,null,null,null,"HV Fault","EHV Fault"]
["Safety Limit On Soil Or Outdoor Concrete",null,null,null,null,{"$f":"'Data Entered'!F102","v":""},{"$f":"'Data Entered'!F106","v":""},"V"]
["Safety Limit On 100mm Tarmac",null,null,null,null,{"$f":"'Data Entered'!F104","v":""},{"$f":"'Data Entered'!F108","v":""},"V"]
["Safety Limit On Indoor Concrete",null,null,null,null,{"$f":"'Data Entered'!F103","v":""},{"$f":"'Data Entered'!F107","v":""},"V"]
["Safety Limit On Stance Grating",null,null,null,null,{"$f":"'Data Entered'!F105","v":""},{"$f":"'Data Entered'!F109","v":""},"V"]
[]
[]
["TOUCH VOLTAGES INSIDE & AROUND EXTERIOR OF SUBSTATION "]
[]
["Maximum Touch Voltage For The Substation",null,null,null,null,{"$f":"'Data Entered'!B110","v":21},null,"% of EPR"]
[]
[null,null,null,null,null,"HV Fault","EHV Fault"]
["Calculated Touch Voltage",null,null,null,null,{"$f":"'Data Entered'!B111","v":1963.4860919735158},{"$f":"'Data Entered'!H111","v":0},"V"]
["Touch voltage ≤ safety limit on soil or outdoor concrete",null,null,null,null,{"$f":"'Data Entered'!D112","v":""},{"$f":"'Data Entered'!J112","v":""}]
["Touch voltage ≤ safety limit on 100mm tarmac",null,null,null,null,{"$f":"'Data Entered'!D113","v":""},{"$f":"'Data Entered'!J113","v":""}]
["Touch voltage ≤ safety limit on indoor concrete",null,null,null,null,{"$f":"'Data Entered'!D114","v":""},{"$f":"'Data Entered'!J114","v":""}]
["Touch voltage ≤ safety limit on stance grating",null,null,null,null,{"$f":"'Data Entered'!D115","v":""},{"$f":"'Data Entered'!J115","v":""}]
[]
[]
["LV SYSTEM"]
[]
["LV System Neutral Multiply Earthed",null,null,null,null,{"$f":"'Data Entered'!B117","v":""}]
[]
[]
[]
[{"$f":"'Publish Report'!C75","v":"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"},null,null,null,"Page 5 of 10"]
["IMPACT ON 3rd PARTY PERSONS AND EQUIPMENT "]
[]
["LV Neutral Earthed at Single Point",null,null,null,null,"HV Fault","EHV Fault"]
["Safety Limit For LV Customers",null,null,null,null,{"$f":"'Data Entered'!B118","v":156},{"$f":"IF('Data Entered'!F140=0,\"\",'Data Entered'!B128)","v":""},"V"]
["EPR ≤ Safety Limit For LV Customers",null,null,null,null,{"$f":"'Data Entered'!B119","v":"NO"},{"$f":"IF('Data Entered'!F140=0,\"\",'Data Entered'!B129)","v":""}]
[]
[]
["LV Neutral Earthed at Multiple Points",null,null,null,null,"HV Fault","EHV Fault"]
["Safety Limit For LV Customers",null,null,null,null,{"$f":"'Data Entered'!B120","v":312},{"$f":"IF('Data Entered'!F140=0,\"\",'Data Entered'!B130)","v":""},"V"]
["EPR ≤ Safety Limit For LV Customers",null,null,null,null,{"$f":"'Data Entered'!B121","v":"NO"},{"$f":"IF('Data Entered'!F140=0,\"\",'Data Entered'!B131)","v":""}]
[]
[]
[null,null,null,null,null,"HV Fault","EHV Fault"]
["Limit For LV Customer's Telecommunication Equipment",null,null,null,null,{"$f":"'Data Entered'!B122","v":1150},{"$f":"IF('Data Entered'!F140=0,\"\",'Data Entered'!B132)","v":""},"V"]
["EPR ≤ Limit For LV Customer's Telecommunication Equipment",null,null,null,null,{"$f":"'Data Entered'!B123","v":"NO"},{"$f":"IF('Data Entered'!F140=0,\"\",'Data Entered'!B133)","v":""}]
[]
[]
[null,null,null,null,null,"HV Fault","EHV Fault"]
["International Telecommunication Union (ITU) Limit",null,null,null,null,{"$f":"'Data Entered'!B124","v":430},{"$f":"IF('Data Entered'!F140=0,\"\",'Data Entered'!B134)","v":""},"V"]
["EPR ≤ International Telecommunication Union (ITU) Limit",null,null,null,null,{"$f":"'Data Entered'!B125","v":"NO"},{"$f":"IF('Data Entered'!F140=0,\"\",'Data Entered'!B135)","v":""}]
[]
[]
["3rd PARTY IMPACT CLASSIFICATION"]
[]
[null,null,null,null,null,"HV Fault","EHV Fault"]
["NGED Third Party Impact Classification",null,null,null,null,{"$f":"IF('Data Entered'!B127=\"HEPR\",\"High EPR\",IF('Data Entered'!B127=\"LEPR\",\"Low EPR\",\"\"))","v":"High EPR"},{"$f":"IF(AND('Data Entered'!B48=\"YES\",'Data Entered'!B137=\"HEPR\"),\"High EPR\",IF(AND('Data Entered'!B48=\"YES\",'Data Entered'!B137=\"LEPR\"),\"Low EPR\",\"\"))","v":"Low EPR"}]
["Overall NGED Third Party Impact Classification",null,null,null,null,{"$f":"IF('Data Entered'!B141=\"HEPR\",\"High EPR\",IF('Data Entered'!B141=\"LEPR\",\"Low EPR\",\"\"))","v":"High EPR"}]
[]
[]
[null,null,null,null,null,"HV Fault","EHV Fault"]
["ITU Classification",null,null,null,null,{"$f":"IF('Data Entered'!B126=\"HOT\",\"Hot\",IF('Data Entered'!B126=\"COLD\",\"Cold\",\"\"))","v":"Hot"},{"$f":"IF(AND('Data Entered'!B48=\"YES\",'Data Entered'!B136=\"HOT\"),\"Hot\",IF(AND('Data Entered'!B48=\"YES\",'Data Entered'!B136=\"COLD\"),\"Cold\",\"\"))","v":"Cold"}]
["Overall ITU Classification",null,null,null,null,{"$f":"IF('Data Entered'!D141=\"HOT\",\"Hot\",IF('Data Entered'!D141=\"COLD\",\"Cold\",\"\"))","v":"Hot"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[{"$f":"'Publish Report'!C75","v":"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"},null,null,null,"Page 6 of 10"]
["HV SEPARATION DISTANCE"]
[null,null,null,null,null,"Theoretical","Practicable"]
["Minimum HV Separation Distance To: ",null,null,null,null,{"$f":"'Data Entered'!B142","v":60},{"$f":"'Data Entered'!F142","v":40},"m"]
["   - Railway, Tramway or Metallic Pipeline"]
["   - Bulk Storage Tanks For Petroleum or Flammable Liquids"]
["   - Zoo, Stable, Pond/Lake Used For Commercial Fishing"]
["   - Outdoor Swimming Pool, Paddling Pool or Shower"]
["   - Telephone Exchange"]
["   - Customer TT Electrode"]
[]
[null,null,null,null,null,"Theoretical","Practicable"]
["Minimum HV Separation Distance To:",null,null,null,null,{"$f":"'Data Entered'!B143","v":60},{"$f":"'Data Entered'!F143","v":40},"m"]
["   - LV System Whose Neutral Is Earthed At A Single Point"]
[]
[null,null,null,null,null,"Theoretical","Practicable"]
["Minimum HV Separation Distance To:",null,null,null,null,{"$f":"'Data Entered'!B144","v":28},{"$f":"'Data Entered'!F144","v":28},"m"]
["   - LV System Whose Neutral Is Earthed At Multiple Points"]
[]
[]
["LV ELECTRODE"]
[]
["Separate LV Electrode Required",null,null,null,{"$f":"'Data Entered'!F145","v":"YES"}]
["Minimum Length Of Insulated LV Electrode",null,null,null,{"$f":"IF('Data Entered'!F145=\"YES\",\"To achieve HV separation distance\",\"\")","v":"To achieve HV separation distance"},null,null,"m"]
["Minimum Length Of Bare LV Electrode",null,null,null,{"$f":"IF('Data Entered'!F145=\"YES\",'Data Entered'!D146,\"\")","v":""},null,null,"m"]
["LV Electrode Resistance",null,null,null,{"$f":"IF('Data Entered'!F145=\"YES\",'Data Entered'!D147,\"\")","v":6.8640000000000008},null,null,"Ω"]
[]
[]
["ACTIONS REQUIRED"]
[]
["1.","The distribution substation earthing system shall be constructed"]
[null,"in accordance with the preceding stipulations and ",null,null,null,{"$f":"'Data Entered'!I10","v":"TP21G-0"}]
[]
["2.",{"$f":"IF(AND('Data Entered'!G10=\"NO\",'Data Entered'!B141=\"HEPR\"),\"Advise HV Customer to consider the risks arising from earth potential rise\",\"\")","v":""}]
[]
[]
["3.",{"$f":"IF(AND('Data Entered'!G10=\"NO\",'Data Entered'!D141=\"HOT\"),\"Advise HV Customer to notify telecommunication network provider if they have / are having a telecommunication service installed\",\"\")","v":""}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[{"$f":"'Publish Report'!C75","v":"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"},null,null,null,"Page 7 of 10"]
["APPENDIX A: SOURCE SUBSTATION DATA"]
[]
["Further information relating to the source substation is listed below:"]
[]
["Source Substation Name / Number",null,null,{"$f":"'Data Entered'!D16","v":{"$error":"#N/A"}}]
["Arc Suppression Coil Earthed HV Network",null,null,null,null,null,{"$f":"'Data Entered'!D13","v":"NO"}]
["Earthing System Impedance Of Source Substation",null,null,null,null,null,{"$f":"'Data Entered'!F18","v":0.1},"Ω"]
["EPR Of Source Substation",null,null,null,null,null,{"$f":"'Data Entered'!F20","v":3000},"V"]
["EHV Fault Clearance Time For Source Substation",null,null,null,null,null,{"$f":"'Data Entered'!F22","v":3},"s"]
["EHV Fault Cleared By INST, DT or IDMT Earth Fault Protection",null,null,null,null,null,{"$f":"'Data Entered'!B23","v":0}]
["Telecommunication System Limit For EHV Fault Clearance Time ",null,null,null,null,null,{"$f":"'Data Entered'!B132","v":1150},"V"]
[]
[]
[]
["APPENDIX B: SYSTEM IMPEDANCE DATA"]
[]
["Further information relating to the system impedance information is listed below:"]
[]
["Methodology",null,{"$f":"IF('Data Entered'!B13<>\"Advanced - ASC Earthing\",'Data Entered'!B13,\"\")","v":"Basic"}]
["Z1 Resistance",null,{"$f":"IF('Data Entered'!$B$13=\"Advanced - Fault Level Study\",'Data Entered'!B25,\"\")","v":""},"Z1 Reactance",null,{"$f":"IF('Data Entered'!$B$13=\"Advanced - Fault Level Study\",'Data Entered'!C25,\"\")","v":""},{"$f":"IF('Data Entered'!$B$13=\"Advanced - Fault Level Study\",'Data Entered'!B24,\"\")","v":""}]
["Z2 Resistance",null,{"$f":"IF('Data Entered'!$B$13=\"Advanced - Fault Level Study\",'Data Entered'!B26,\"\")","v":""},"Z2 Reactance",null,{"$f":"IF('Data Entered'!$B$13=\"Advanced - Fault Level Study\",'Data Entered'!C26,\"\")","v":""},{"$f":"IF('Data Entered'!$B$13=\"Advanced - Fault Level Study\",'Data Entered'!B24,\"\")","v":""}]
["Z0 Resistance",null,{"$f":"IF('Data Entered'!$B$13=\"Advanced - Fault Level Study\",'Data Entered'!B27,\"\")","v":""},"Z0 Reactance",null,{"$f":"IF('Data Entered'!$B$13=\"Advanced - Fault Level Study\",'Data Entered'!C27,\"\")","v":""},{"$f":"IF('Data Entered'!$B$13=\"Advanced - Fault Level Study\",'Data Entered'!B24,\"\")","v":""}]
["Neutral Earthing",null,{"$f":"IF('Data Entered'!B28=0,\"\",IF('Data Entered'!$B$13=\"Basic\",'Data Entered'!B28,\"\"))","v":""},null,{"$f":"IF('Data Entered'!C28=0,\"\",IF('Data Entered'!$B$13=\"Basic\",'Data Entered'!C28,\"\"))","v":""},null,"A"]
["NER 1",null,{"$f":"IF('Data Entered'!B29=0,\"\",IF('Data Entered'!$B$13=\"Intermediate\",'Data Entered'!B29,\"\"))","v":""},null,{"$f":"IF('Data Entered'!C29=0,\"\",IF('Data Entered'!$B$13=\"Intermediate\",'Data Entered'!C29,\"\"))","v":""},null,"A"]
["NER 2",null,{"$f":"IF('Data Entered'!B30=0,\"\",IF('Data Entered'!$B$13=\"Intermediate\",'Data Entered'!B30,\"\"))","v":""},null,{"$f":"IF('Data Entered'!C30=0,\"\",IF('Data Entered'!$B$13=\"Intermediate\",'Data Entered'!C30,\"\"))","v":""},null,"A"]
["NER 3",null,{"$f":"IF('Data Entered'!B31=0,\"\",IF('Data Entered'!$B$13=\"Intermediate\",'Data Entered'!B31,\"\"))","v":""},null,{"$f":"IF('Data Entered'!C31=0,\"\",IF('Data Entered'!$B$13=\"Intermediate\",'Data Entered'!C31,\"\"))","v":""},null,"A"]
["NER 4",null,{"$f":"IF('Data Entered'!B32=0,\"\",IF('Data Entered'!$B$13=\"Intermediate\",'Data Entered'!B32,\"\"))","v":""},null,{"$f":"IF('Data Entered'!C32=0,\"\",IF('Data Entered'!$B$13=\"Intermediate\",'Data Entered'!C32,\"\"))","v":""},null,"A"]
["SECTION 1",null,{"$f":"IF('Data Entered'!B33=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B33,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C33=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C33,\"\"))","v":""},null,"km"]
["SECTION 2",null,{"$f":"IF('Data Entered'!B34=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B34,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C34=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C34,\"\"))","v":""},null,"km"]
["SECTION 3",null,{"$f":"IF('Data Entered'!B35=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B35,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C35=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C35,\"\"))","v":""},null,"km"]
["SECTION 4",null,{"$f":"IF('Data Entered'!B36=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B36,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C36=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C36,\"\"))","v":""},null,"km"]
["SECTION 5",null,{"$f":"IF('Data Entered'!B37=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B37,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C37=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C37,\"\"))","v":""},null,"km"]
["SECTION 6",null,{"$f":"IF('Data Entered'!B38=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B38,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C38=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C38,\"\"))","v":""},null,"km"]
["SECTION 7",null,{"$f":"IF('Data Entered'!B39=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B39,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C39=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C39,\"\"))","v":""},null,"km"]
["SECTION 8",null,{"$f":"IF('Data Entered'!B40=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B40,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C40=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C40,\"\"))","v":""},null,"km"]
["SECTION 9",null,{"$f":"IF('Data Entered'!B41=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B41,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C41=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C41,\"\"))","v":""},null,"km"]
["SECTION 10",null,{"$f":"IF('Data Entered'!B42=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B42,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C42=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C42,\"\"))","v":""},null,"km"]
["SECTION 11",null,{"$f":"IF('Data Entered'!B43=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B43,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C43=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C43,\"\"))","v":""},null,"km"]
["SECTION 12",null,{"$f":"IF('Data Entered'!B44=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B44,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C44=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C44,\"\"))","v":""},null,"km"]
["SECTION 13",null,{"$f":"IF('Data Entered'!B45=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B45,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C45=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C45,\"\"))","v":""},null,"km"]
["SECTION 14",null,{"$f":"IF('Data Entered'!B46=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B46,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C46=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C46,\"\"))","v":""},null,"km"]
["SECTION 15",null,{"$f":"IF('Data Entered'!B47=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!B47,\"\"))","v":""},null,null,{"$f":"IF('Data Entered'!C47=0,\"\",IF(OR('Data Entered'!$B$13=\"Basic\",'Data Entered'!$B$13=\"Intermediate\"),'Data Entered'!C47,\"\"))","v":""},null,"km"]
[]
[]
[]
[]
[]
[]
[{"$f":"'Publish Report'!C75","v":"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"},null,null,null,"Page 8 of 10"]
["APPENDIX C: POLE TERMINATION DATA"]
[]
["Further information relating to the HV cable pole termination is listed below:"]
[]
["Earthing System Impedance Of Pole Termination",null,null,null,null,null,{"$f":"IF('Data Entered'!B48=\"NO\",'Data Entered'!H53,\"\")","v":""},"Ω"]
[]
[]
[]
["APPENDIX D: NETWORK CONTRIBUTION DATA"]
[]
["Further information relating to the network contribution to the earth electrode "]
["resistance is listed below:"]
[]
["Built-Up Area Covered By The Local HV & LV Network",null,null,null,null,{"$f":"'Data Entered'!B55","v":0},null,{"$f":"'Data Entered'!B54","v":0}]
["Type Of Local HV & LV Network",null,null,{"$f":"'Data Entered'!B56","v":0}]
["Network Contribution To Electrode Resistance",null,null,null,null,{"$f":"'Data Entered'!D73","v":0.85000000000000009},null,"Ω"]
[]
[]
[]
["APPENDIX E: CURRENT INTO GROUND DATA"]
[]
["Further information relating to the calculation of the percentage of fault current flowing "]
["into the ground is listed below:"]
[]
["Source To Unit Substation Connection",null,null,{"$f":"IF('Data Entered'!F77=100,\"\",'Design Input'!D269)","v":""}]
[]
["Predominant Cable Type",null,null,{"$f":"IF('Data Entered'!F77=100,\"\",'Design Input'!D270)","v":""}]
["Earth Resistance At Start Of Cable",null,null,null,null,null,{"$f":"IF('Data Entered'!F77=100,\"\",'Design Input'!D271)","v":""},"Ω"]
["Earth Resistance At End Of Cable",null,null,null,null,null,{"$f":"IF('Data Entered'!F77=100,\"\",'Design Input'!D272)","v":""},"Ω"]
["Cable Length",null,null,null,null,null,{"$f":"IF('Data Entered'!F77=100,\"\",'Design Input'!D273)","v":""},"km"]
["Calculated % Of Fault Current Flowing Into The Ground",null,null,null,null,null,{"$f":"'Data Entered'!F77","v":100},"%IGR"]
[]
[]
[]
["APPENDIX F: ELECTRODE SURFACE AREA DATA"]
[]
["Further information relating to the calculation of the electrode surface area is listed below:"]
[]
["Minimum HV Electrode Surface Area Requirement",null,null,null,null,null,{"$f":"'Data Entered'!B80","v":307.72348110429317},"mm2"]
["Surface Area Of Perimeter Electrode",null,null,null,null,null,{"$f":"'Data Entered'!B82","v":0},"mm2"]
["Surface Area Of 4 x 1.2m Earth Rods",null,null,null,null,null,{"$f":"'Data Entered'!B83","v":0},"mm2"]
["Surface Area Of Electrode 'Tail'",null,null,null,null,null,{"$f":"'Data Entered'!B84","v":0},"mm2"]
["Total Surface Area",null,null,null,null,null,{"$f":"'Data Entered'!B85","v":0},"mm2"]
["Electrode Surface Area Criteria Met",null,null,null,null,null,{"$f":"'Design Input'!E319","v":"NO"}]
[]
[]
[]
[{"$f":"'Publish Report'!C75","v":"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"},null,null,null,"Page 9 of 10"]
["APPENDIX G: HV FAULT CLEARANCE TIME DATA"]
[]
["Further information relating to the calculation of the fault clearance time is listed below:"]
[]
["CB Operating Time",null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!B89=\"YES\"),AND('Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B89=\"YES\")),'Data Entered'!B90,\"\")","v":""},"ms"]
["IDMT CT Ratio",null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!B89=\"YES\"),AND('Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B89=\"YES\")),CONCATENATE('Data Entered'!B91,\"/\",'Data Entered'!B92),\"\")","v":""}]
["IDMT EF Current Setting",null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!B89=\"YES\"),AND('Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B89=\"YES\")),CONCATENATE('Data Entered'!B93,\" \",'Data Entered'!B94),\"\")","v":""}]
["IDMT EF Current Setting (Primary Current Equivalent)",null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!B89=\"YES\"),AND('Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B89=\"YES\")),'Data Entered'!B95,\"\")","v":""},"A"]
["IDMT EF Time-Current Characteristic",null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!B89=\"YES\"),AND('Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B89=\"YES\")),'Data Entered'!B96,\"\")","v":""}]
["IDMT EF Time Multiplier Setting",null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!B89=\"YES\"),AND('Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B89=\"YES\")),'Data Entered'!B97,\"\")","v":""}]
["IDMT EF Protection Operating Time",null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!B89=\"YES\"),AND('Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B89=\"YES\")),'Data Entered'!B98,\"\")","v":""},"ms"]
["Calculated Total Fault Clearance Time",null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!B89=\"YES\"),AND('Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B89=\"YES\")),'Data Entered'!B99,\"\")","v":""},"s"]
[]
["Design Margin",null,null,null,null,null,{"$f":"IF(OR(AND('Data Entered'!B13=\"Intermediate\",'Data Entered'!B89=\"YES\"),AND('Data Entered'!B13=\"Advanced - Fault Level Study\",'Data Entered'!B89=\"YES\")),400,\"\")","v":""},"ms"]
["Design Fault Clearance Time",null,null,null,null,null,{"$f":"'Data Entered'!B101","v":3.4},"s"]
[]
[]
[]
["APPENDIX H: TRANSFER VOLTAGE FROM SOURCE DATA"]
[]
["Further information relating to the calculation of the transfer voltage from the source "]
["substation to the distribution substation is listed below:"]
[]
["Source To Unit Substation Connection",null,null,null,null,{"$f":"IF('Data Entered'!B48=\"YES\",'Data Entered'!B49,\"\")","v":"All Cable"}]
["Predominant Cable Type",null,null,{"$f":"IF('Data Entered'!B48=\"YES\",'Data Entered'!B50,\"\")","v":0}]
["Earth Resistance At Start Of Cable",null,null,null,null,null,{"$f":"IF('Data Entered'!B48=\"YES\",'Data Entered'!F18,\"\")","v":0.1},"Ω"]
["Earth Resistance At End Of Cable",null,null,null,null,null,{"$f":"IF('Data Entered'!B48=\"YES\",'Data Entered'!F74,\"\")","v":0.84999397920931408},"Ω"]
["Cable Length",null,null,null,null,null,{"$f":"IF('Data Entered'!B48=\"YES\",'Data Entered'!B51,\"\")","v":0},"km"]
["Source Substation EPR",null,null,null,null,null,{"$f":"IF('Data Entered'!B48=\"YES\",'Data Entered'!F20,\"\")","v":3000},"V"]
["Calculated Transfer Voltage From Source Substation",null,null,null,null,null,{"$f":"IF('Data Entered'!B48=\"YES\",'Data Entered'!F140,\"\")","v":0},"V"]
[]
[]
[]
["APPENDIX I: EHV FAULT CLEARANCE TIME"]
[]
["Further information relating to the EHV earth fault clearance time is listed below:"]
[]
["EHV Fault Clearance Time For Source Substation",null,null,null,null,null,{"$f":"'Data Entered'!F22","v":3},"s"]
["Design Margin",null,null,null,null,null,{"$f":"'Data Entered'!D23","v":0.4},"s"]
["Design Fault Clearance Time",null,null,null,null,null,{"$f":"'Data Entered'!F23","v":3.4},"s"]
[]
[]
[]
[]
[]
[]
[]
[]
[{"$f":"'Publish Report'!C75","v":"ER_WPD_EM_1234567_26-03-2020 17-03-58hrs"},null,null,null,"Page 10 of 10"]

{"sheet":"Source-Num","index":12,"n_rows":1990,"n_cols":9,"rows_kept":1990,"cut":false,"hidden":true,"merged":[]}
[null,1,2,3,4,5,6,7,8]
["AREA","SUBSTATION_NUMBER","SUBSTATION_NAME","ZE","Assumed ZE","UE","Assumed UE","t","Assumed t"]
["South West",104098,"Norrington 132/33kV S Stn",0.2,"Y",1400,"Y",3,"Y"]
["South West",106009,"Iron Acton 275/132kV S Stn",0.2,"Y",1486,"",1,"Y"]
["South West",106010,"Melksham 400/275/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
["South West",110375,"Woodland Way 33/11kV S Stn",8.7999999999999995E-2,null,151,"",3,"Y"]
["South West",110641,"Bedminster 33/11kV S Stn",0.12,null,348,"",3,"Y"]
["South West",110644,"Eastville 33/11kV S Stn",0.10199999999999999,null,500,"Y",3,"Y"]
["South West",110772,"Lockleaze 33/11kV S Stn",5.7000000000000002E-2,null,21,"",3,"Y"]
["South West",110803,"Cairns Road 33/11kV S Stn",0.09,null,207,"",3,"Y"]
["South West",110804,"St Pauls BSP 132/11kV S Stn",0.06,null,43,"",3,"Y"]
["South West",111158,"Clifton 33/11kV S Stn",0.12,null,251,"",3,"Y"]
["South West",111481,"Keynsham East 33/11kV S Stn",0.108,null,130,"",3,"Y"]
["South West",111800,"Mangotsfield 33/11kV S Stn",9.2999999999999999E-2,null,23,"",3,"Y"]
["South West",111935,"Almondsbury 33/11kV S Stn",0.121,null,143,"",3,"Y"]
["South West",112130,"Winterbourne 33/11kV S Stn",0.30099999999999999,null,474,"",3,"Y"]
["South West",112272,"Whitchurch 33/11kV S Stn",4.2000000000000003E-2,null,13,"",3,"Y"]
["South West",112389,"Stoke Bishop 33/11kV S Stn",0.12,null,500,"Y",3,"Y"]
["South West",113180,"Keynsham West 33/11kV S Stn",0.108,null,170,"",3,"Y"]
["South West",113193,"Bishopsworth 33/11kV S Stn",0.12,null,198,"",3,"Y"]
["South West",113277,"Avonmouth Docks 33/6.6kV S Stn",0.08,null,119,"",3,"Y"]
["South West",113339,"Kingsweston 33/11kV S Stn",0.11,null,206,"",3,"Y"]
["South West",113367,"Avonmouth BSP 132/33kV S Stn",1.4999999999999999E-2,null,92,"",3,"Y"]
["South West",113368,"Avonmouth 33/11kV S Stn",7.0000000000000007E-2,null,109,"",3,"Y"]
["South West",113369,"Filton Dc 33/11kV S Stn",0.13,null,201,"",3,"Y"]
["South West",113370,"Lockleaze 132/33/11kV S Stn",5.7000000000000002E-2,null,184,"",3,"Y"]
["South West",113371,"Bower Ashton 33/11kV S Stn",0.12,null,186,"",3,"Y"]
["South West",113372,"Feeder Road 33kV S Stn",0.05,null,79,"",3,"Y"]
["South West",113373,"Feeder Road A 33/11kV S Stn",0.05,null,140,"",3,"Y"]
["South West",113374,"Feeder Road B 33/11kV S Stn",0.05,null,140,"",3,"Y"]
["South West",113429,"British Gas Hallen 33/11kV S Stn",7.0999999999999994E-2,null,110,"",3,"Y"]
["South West",113449,"Feeder Road 132/33kV S Stn",0.05,null,251,"",3,"Y"]
["South West",113450,"St Pauls 132/11kV S Stn",0.06,null,314,"",1,"Y"]
["South West",113572,"Bradley Stoke 132/33kV S Stn",0.21,null,1024,"",3,"Y"]
["South West",113720,"Hewlett Packard 33/11kV S Stn",6.3E-2,null,28,"",3,"Y"]
["South West",113760,"Bradley Stoke 33/11kV S Stn",0.21,null,500,"Y",3,"Y"]
["South West",113884,"Abbeywood 33/11kV S Stn",0.77900000000000003,null,265,"",3,"Y"]
["South West",113983,"Cribbs Causeway 33/11kV S Stn",7.6999999999999999E-2,null,32,"",3,"Y"]
["South West",114023,"Seabank 400/132kV S Stn",8.5999999999999993E-2,null,1274,"",1,"Y"]
["South West",114059,"Rolls Royce Filton 132kV S Stn",0.13300000000000001,null,291,"",1,"Y"]
["South West",114258,"Astrazeneca 33/11kV S Stn",0.47,null,348,"",3,"Y"]
["South West",114259,"Seabank 132/33kV S Stn",8.5999999999999993E-2,null,695,"",3,"Y"]
["South West",114260,"Broadweir 33/11kV S Stn",0.06,null,13.5,"",3,"Y"]
["South West",114389,"Cotham 33/11kV S Stn",0.16500000000000001,null,81,"",3,"Y"]
["South West",114391,"Emersons Green 33/11kV S Stn",0.33,null,144,"",3,"Y"]
["South West",114393,"Staplehill 33kV S Stn",0.43,null,132,"",3,"Y"]
["South West",114434,"Western Approach 33/11kV S Stn",0.1,null,200,"",3,"Y"]
["South West",114632,"Hewlett Packard 33kV S Stn",6.3E-2,null,500,"Y",3,"Y"]
["South West",114652,"Avonmouth Biogas 33kV S Stn",0.183,null,500,"Y",3,"Y"]
["South West",114741,"Patchway 33/11kV S Stn",0.62,null,500,"Y",3,"Y"]
["South West",114756,"Severnside Energy Recovery Centre 132kV S Stn",0.125,null,1400,"Y",1,"Y"]
["South West",118093,"Avonmouth Wind Farm 33kV S Stn",8.5000000000000006E-2,null,500,"Y",3,"Y"]
["South West",118115,"Northwood Solar Park 33kV S Stn",0.14000000000000001,null,500,"Y",3,"Y"]
["South West",118117,"Marksbury Solar Park 33kV S Stn",9.6000000000000002E-2,null,500,"Y",3,"Y"]
["South West",118154,"Chelwood Solar Park 33kV S Stn",0.125,null,500,"Y",3,"Y"]
["South West",118157,"Oakham Farm Solar Park 33kV S Stn",0.14399999999999999,null,500,"Y",3,"Y"]
["South West",118166,"Lawrence Weston Solar Park 33kV S Stn",0.186,null,278.8,"",3,"Y"]
["South West",118179,"Lockleaze Battery Storage 33kV S Stn",0.69,null,500,"Y",3,"Y"]
["South West",118180,"Old Green Generation Station 132kV S Stn",0.114,null,1400,"Y",1,"Y"]
["South West",118183,"Rockingham 33kV S Stn",0.23,null,500,"Y",3,"Y"]
["South West",118184,"Viridor Waste To Energy 33kV S Stn",9.2999999999999999E-2,null,500,"Y",3,"Y"]
["South West",160050,"Oldfield Park33/ 6.6kV S Stn",0.26100000000000001,null,86,"",3,"Y"]
["South West",160060,"Park Street 33/6.6kV S Stn",3.1E-2,null,21,"",3,"Y"]
["South West",160355,"Entry Hill 33/6.6kV S Stn",6.5000000000000002E-2,null,88,"",3,"Y"]
["South West",160389,"Batheaston 33/6.6kV S Stn",4.3999999999999997E-2,null,59,"",3,"Y"]
["South West",160390,"Twerton 33/6.6kV S Stn",0.08,null,119,"",3,"Y"]
["South West",160415,"Chewton Mendip 33/11kV S Stn",2,null,2670,"",3,"Y"]
["South West",160423,"Midsomer Norton 33/11kV S Stn",0.05,null,82,"",3,"Y"]
["South West",160739,"Whatley Quarry 33/11kV S Stn",0.91700000000000004,null,569,"",3,"Y"]
["South West",160811,"Dinder 33/11kV S Stn",4.2699999999999996,null,4582,"",3,"Y"]
["South West",160824,"Wells 33/11kV S Stn",0.14799999999999999,null,129,"",3,"Y"]
["South West",161315,"Paulton 33/11kV S Stn",0.19700000000000001,null,127,"",3,"Y"]
["South West",161532,"High Littleton 33/11kV S Stn",0.24,null,401,"",3,"Y"]
["South West",161641,"Shepton Mallet 33/11kV S Stn",0.192,null,251,"",3,"Y"]
["South West",161701,"Newbury 33/11kV S Stn",0.97099999999999997,null,1035,"",3,"Y"]
["South West",161823,"Evercreech 33/11kV S Stn",0.129,null,103,"",3,"Y"]
["South West",162344,"Foxhills 33/11kV S Stn",0.16200000000000001,null,226,"",3,"Y"]
["South West",162406,"Peasedown 33/11kV S Stn",0.10199999999999999,null,113,"",3,"Y"]
["South West",162633,"Radstock 132/33kV S Stn",0.25700000000000001,null,247,"",3,"Y"]
["South West",162888,"Shooters Bottom W/F 33kV S Stn",1.2,null,1464,"",3,"Y"]
["South West",164016,"Combe Park 33/6.6kV S Stn",7.5999999999999998E-2,null,96,"",3,"Y"]
["South West",164087,"Bath Dolemeads 132/33/6.6kV S Stn",7.1999999999999995E-2,null,68,"",3,"Y"]
["South West",164170,"Dorchester Street 33/6.6kV S Stn",7.1999999999999995E-2,null,105,"",3,"Y"]
["South West",164210,"University Of Bath 33/11kV S Stn",0.11700000000000001,null,500,"Y",3,"Y"]
["South West",168000,"Whitchurch Farm Solar Park 33kV S Stn",0.20300000000000001,null,500,"Y",3,"Y"]
["South West",168001,"Shooters Bottom Solar Park 33kV S Stn",0.90400000000000003,null,500,"Y",3,"Y"]
["South West",168104,"New Row Farm Solar Park 33kV S Stn",0.66600000000000004,null,500,"Y",3,"Y"]
["South West",168105,"Pitts Farm Solar Park 33kV S Stn",0.65600000000000003,null,500,"Y",3,"Y"]
["South West",168106,"Dinder Farm Solar Park 33kV S Stn",0.65600000000000003,null,500,"Y",3,"Y"]
["South West",168138,"Pylle Solar Park 33kV S Stn",0.17699999999999999,null,500,"Y",3,"Y"]
["South West",180003,"Gas Lane 33/11kV S Stn",3.7999999999999999E-2,null,36,"",3,"Y"]
["South West",180006,"Congresbury 33/11kV S Stn",0.153,null,325,"",3,"Y"]
["South West",180017,"Axbridge 33/11kV S Stn",0.19,null,281,"",3,"Y"]
["South West",180092,"Weston Locking Road 33/11kV S Stn",6.2E-2,null,128,"",3,"Y"]
["South West",180173,"Blagdon 33/11kV S Stn",0.11799999999999999,null,160,"",3,"Y"]
["South West",180198,"Clevedon 33/11kV S Stn",0.26200000000000001,null,275,"",3,"Y"]
["South West",180471,"Bournville 33/11kV S Stn",7.9000000000000001E-2,null,141,"",3,"Y"]
["South West",180820,"Weston-In-Gordano 33/11kV S Stn",0.17199999999999999,null,351,"",3,"Y"]
["South West",180952,"Winscombe 33/11kV S Stn",0.21199999999999999,null,428,"",3,"Y"]
["South West",181000,"Nailsea 33/11kV S Stn",0.23499999999999999,null,404,"",3,"Y"]
["South West",181216,"Lypstone Farm 33/11kV S Stn",6.2E-2,null,143,"",3,"Y"]
["South West",181230,"Chew Stoke 33/11kV S Stn",0.40200000000000002,null,339,"",3,"Y"]
["South West",181345,"Cheddar 33/11kV S Stn",8.2000000000000003E-2,null,128,"",3,"Y"]
["South West",181346,"Compton Martin 33/11kV S Stn",0.46899999999999997,null,935,"",3,"Y"]
["South West",181360,"Weston Central 33/11kV S Stn",0.30299999999999999,null,135,"",3,"Y"]
["South West",181414,"Easton-In-Gordano 33/11kV S Stn",0.189,null,417,"",3,"Y"]
["South West",181425,"East Brent 33/11kV S Stn",0.158,null,144,"",3,"Y"]
["South West",181817,"Wedmore 33/11kV S Stn",0.123,null,217,"",3,"Y"]
["South West",182000,"Frys Hill Radio 33kV/LV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",182150,"Royal Portbury Dock 33/11kV S Stn",5.0999999999999997E-2,null,20,"",3,"Y"]
["South West",182332,"Brent Knoll 33kV S Stn",0.191,null,154,"",3,"Y"]
["South West",182372,"Weston 132/33kV S Stn",6.2E-2,null,174,"",3,"Y"]
["South West",182373,"Churchill 132/33kV S Stn",0.18,null,271,"",3,"Y"]
["South West",182570,"Churchill Gate 33/11kV S Stn",0.55000000000000004,null,853,"",3,"Y"]
["South West",182736,"Bristol International Airport 33/11kV S Stn",0.28299999999999997,null,406,"",3,"Y"]
["South West",182768,"Stancombe Quarry 33kV S Stn",1.0840000000000001,null,1444,"",3,"Y"]
["South West",182800,"Portishead 132/33kV S Stn",5.8999999999999997E-2,null,118,"",3,"Y"]
["South West",182982,"West Wick 33/11kV S Stn",0.158,null,316,"",3,"Y"]
["South West",182983,"Portishead Ashlands 33/11kV S Stn",5.8999999999999997E-2,null,423,"",3,"Y"]
["South West",188112,"Carditch Drove Solar Park 33kV S Stn",0.1,null,500,"Y",3,"Y"]
["South West",188122,"Iwood Lane Solar Park 33kV S Stn",8.5000000000000006E-2,null,500,"Y",3,"Y"]
["South West",188123,"Ashlawn Farm Solar Park 33kV S Stn",8.5000000000000006E-2,null,500,"Y",3,"Y"]
["South West",188124,"Hawkers Farm Solar Park 33kV S Stn",0.109,null,500,"Y",3,"Y"]
["South West",188139,"Rookery Farm Solar Park 33kV S Stn",0.254,null,500,"Y",3,"Y"]
["South West",188140,"Towerhead Farm Solar Park 33kV S Stn",0.1,null,500,"Y",3,"Y"]
["South West",188150,"Wick Farm Solar Park 33kV S Stn",7.0000000000000007E-2,null,500,"Y",3,"Y"]
["South West",188168,"Wick Farm West Solar Park 33kV S Stn",0.11,null,500,"Y",3,"Y"]
["South West",200433,"Winterbourne Abbas 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",200435,"Yeovil 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",206001,"Alverdiscott 400/132kV S Stn",0.2,"Y",2028,"",1,"Y"]
["South West",206006,"Axminster GSP 400/132kV S Stn",0.2,"Y",2096,"",1,"Y"]
["South West",206007,"Taunton Main 400/132kV S Stn",0.2,"Y",3500,"",1,"Y"]
["South West",206008,"Bridgwater GSP 275/132kV S Stn",5.6000000000000001E-2,null,820,"",1,"Y"]
["South West",210010,"Taunton Local 33/11kV S Stn",4.7E-2,null,24,"",3,"Y"]
["South West",210020,"Trull 33/11kV S Stn",0.06,null,46,"",3,"Y"]
["South West",210030,"Creech St Michael 33/11kV S Stn",0.30399999999999999,null,333,"",3,"Y"]
["South West",210040,"Priorswood 33/11kV S Stn",7.4999999999999997E-2,null,112,"",3,"Y"]
["South West",210050,"Lydeard St Lawrence 33/11kV S Stn",0.86799999999999999,null,1075,"",3,"Y"]
["South West",210060,"Bridgwater Local 33/11kV S Stn",9.0999999999999998E-2,null,358,"",3,"Y"]
["South West",210070,"Wiveliscombe 33/11kV S Stn",2.06,null,2616,"",3,"Y"]
["South West",210080,"Somerton 33/11kV S Stn",0.06,null,69,"",3,"Y"]
["South West",210090,"North Street Langport 33/11kV S Stn",0.1,null,169,"",3,"Y"]
["South West",210100,"Millfield 33/11kV S Stn",0.189,null,275,"",3,"Y"]
["South West",210110,"Edgarley 33/11kV S Stn",0.14799999999999999,null,194,"",3,"Y"]
["South West",210120,"Colley Lane 33/11kV S Stn",8.2000000000000003E-2,null,295,"",3,"Y"]
["South West",210130,"Nether Stowey 33/11kV S Stn",0.443,null,269,"",3,"Y"]
["South West",210140,"Exebridge 33/11kV S Stn",1.25,null,689,"",3,"Y"]
["South West",210150,"Watchfield 33/11kV S Stn",0.09,null,263,"",3,"Y"]
["South West",210160,"Bath Road 33/11kV S Stn",0.06,null,90,"",3,"Y"]
["South West",210180,"Periton 33/11kV S Stn",0.255,null,172,"",3,"Y"]
["South West",210190,"Alcombe 33/11kV S Stn",0.107,null,103,"",3,"Y"]
["South West",210200,"Wellington 33/11kV S Stn",0.44,null,903,"",3,"Y"]
["South West",210210,"Bowhays Cross 132/33kV S Stn",0.192,null,396,"",3,"Y"]
["South West",210210,"Bowhays Cross 33/11kV S Stn",0.192,null,396,"",3,"Y"]
["South West",210260,"Bradon Fm Generator 33kV S Stn",7.6999999999999999E-2,null,54,"",3,"Y"]
["South West",210270,"Huntworth Generator 33kV S Stn",0.219,null,494.9,"",3,"Y"]
["South West",210380,"Wellington Town 33/11kV S Stn",0.28799999999999998,null,166,"",3,"Y"]
["South West",210390,"Culmhead 33/11kV S Stn",0.79300000000000004,null,948,"",3,"Y"]
["South West",210444,"Bridgwater Grid 132/33kV S Stn",6.0999999999999999E-2,null,431,"",3,"Y"]
["South West",210448,"Street 132/33kV S Stn",0.28000000000000003,null,580,"",3,"Y"]
["South West",210450,"Curry Mallet 33/11kV S Stn",0.78800000000000003,null,871,"",3,"Y"]
["South West",210460,"Shapwick 33/11kV S Stn",0.61399999999999999,null,1166,"",3,"Y"]
["South West",210470,"Burnham 33/11kV S Stn",4.2999999999999997E-2,null,54,"",3,"Y"]
["South West",210490,"Luckwell Bridge 33/11kV S Stn",4.79,null,2476,"",3,"Y"]
["South West",210500,"Staplegrove 33/11kV S Stn",0.14799999999999999,null,183,"",3,"Y"]
["South West",210540,"Quartley 33kV S Stn",3.95,null,2386,"",3,"Y"]
["South West",210560,"Holford 33/11kV S Stn",1.7,null,430,"",3,"Y"]
["South West",210600,"Blackditch 33kV S Stn",0.123,null,369,"",3,"Y"]
["South West",210612,"Taunton Main 132/33kV S Stn",0.08,null,3500,"",3,"Y"]
["South West",210670,"Wansbrough Paper Mill 33kV S Stn",7.8E-2,null,105,"",3,"Y"]
["South West",210999,"R.O.F. Power House 33kV S Stn",6.2E-2,null,93,"",3,"Y"]
["South West",218000,"New Rendy Farm Solar Farm 33kV S Stn",0.11600000000000001,null,500,"Y",3,"Y"]
["South West",218002,"Park Wall Solar Park 33kV S Stn",9.4E-2,null,500,"Y",3,"Y"]
["South West",218004,"Grange Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",218005,"Woolavington Solar Park 33kV S Stn",4.2999999999999997E-2,null,500,"Y",3,"Y"]
["South West",218009,"Culmhead Solar Park 33kV S Stn",0.13700000000000001,null,500,"Y",3,"Y"]
["South West",218016,"Watchfield Lawn Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",218017,"Redlands Farm Solar Park 33kV S Stn",0.13,null,500,"Y",3,"Y"]
["South West",218018,"Tengore Lane Solar Park 33kV S Stn",0.1,null,500,"Y",3,"Y"]
["South West",218019,"Somerton Door Solar Park 33kV S Stn",7.8E-2,null,500,"Y",3,"Y"]
["South West",218020,"Tricky Warren Solar Park 33kV S Stn",0.25,null,500,"Y",3,"Y"]
["South West",218021,"Higher Bye Farm Solar Park 33kV S Stn",6.5000000000000002E-2,null,500,"Y",3,"Y"]
["South West",218025,"Puriton Landfill Solar Park 33kV S Stn",0.115,null,500,"Y",3,"Y"]
["South West",218032,"Tonedale Farm Solar Park 33kV S Stn",0.23100000000000001,null,500,"Y",3,"Y"]
["South West",218039,"Tricky Warren 33kV S Stn",0.25,null,500,"Y",3,"Y"]
["South West",218040,"Withy Drove Solar Park 33kV S Stn",6.3E-2,null,500,"Y",3,"Y"]
["South West",218041,"Montys Farm Solar Park 33kV S Stn",0.19700000000000001,null,500,"Y",3,"Y"]
["South West",218043,"Halse Solar Farm 33kV S Stn",0.09,null,112,null,3,"Y"]
["South West",218044,"Glebe Farm 2 Solar Farm 33kV S Stn",0.69,null,578,null,3,"Y"]
["South West",218045,"Hele Manor STOR 33kV S Stn",0.26500000000000001,null,133,"",3,"Y"]
["South West",218061,"Cobbs Cross Solar Farm 33kV S Stn",0.157,null,500,"Y",3,"Y"]
["South West",218071,"Aller Court Solar Farm 33kV S Stn",0.17,null,500,"Y",3,"Y"]
["South West",218075,"Whitley Farm Solar Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",250280,"Axminster 33/11kV S Stn",0.11600000000000001,null,196,"",3,"Y"]
["South West",250290,"East Chinnock 33/11kV S Stn",0.29599999999999999,null,413,"",3,"Y"]
["South West",250300,"Martock 33/11kV S Stn",0.33600000000000002,null,265,"",3,"Y"]
["South West",250310,"Colyford 33/11kV S Stn",0.60899999999999999,null,605,"",3,"Y"]
["South West",250320,"Penn Cross 33/11kV S Stn",0.29199999999999998,null,455,"",3,"Y"]
["South West",250330,"Waterlake 33/11kV S Stn",0.15,null,220,"",3,"Y"]
["South West",250340,"Bridport 33/11kV S Stn",5.8000000000000003E-2,null,56,"",3,"Y"]
["South West",250350,"Dowlish Ford 33/11kV S Stn",0.16,null,202,"",3,"Y"]
["South West",250360,"Chard 33/11kV S Stn",2.9000000000000001E-2,null,39,"",3,"Y"]
["South West",250370,"Crewkerne 33/11kV S Stn",8.8999999999999996E-2,null,307,"",3,"Y"]
["South West",250400,"Montacute 33/11kV S Stn",0.42799999999999999,null,537,"",3,"Y"]
["South West",250437,"Woodcote 132/33kV S Stn",0.17699999999999999,null,283,"",3,"Y"]
["South West",250530,"Coker 33/11kV S Stn",1.1120000000000001,null,1672,"",3,"Y"]
["South West",250620,"Beaminster 33/11kV S Stn",0.439,null,358,"",3,"Y"]
["South West",258019,"Beechgrove Farm Solar Park 33kV S Stn",0.16700000000000001,null,274,"",3,"Y"]
["South West",258023,"Wyld Meadow Solar Park 33kV S Stn",0.15,null,500,"Y",3,"Y"]
["South West",258062,"Newlands Farm Solar Park 33kV S Stn",0.23,null,500,"Y",3,"Y"]
["South West",258063,"Cricket St Thomas Solar Park 33kV S Stn",0.13600000000000001,null,500,"Y",3,"Y"]
["South West",258065,"Parsonage Barn Solar Park 33kV S Stn",0.16,null,500,"Y",3,"Y"]
["South West",258073,"Stonebarrow Farm Solar Farm 33kV S Stn",0.151,null,500,"Y",3,"Y"]
["South West",258083,"Higher Berechapel Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",258127,"Hurcott Solar Park 33kV S Stn",8.4000000000000005E-2,null,500,"Y",3,"Y"]
["South West",258130,"Hurcott 33kV S Stn",0.55000000000000004,null,500,"Y",3,"Y"]
["South West",258153,"Crewkerne Solar Park 33kV S Stn",0.13800000000000001,null,500,"Y",3,"Y"]
["South West",258174,"Axe View Solar Farm 33kV S Stn",3.1E-2,null,500,"Y",3,"Y"]
["South West",260006,"Fullabrook Windfarm 132kV S Stn",0.4,null,580,"",1,"Y"]
["South West",260180,"Darracott Moor Windfarm 33kV S Stn",0.82,null,792,"",3,"Y"]
["South West",260220,"Braunton 33/11kV S Stn",0.372,null,463,"",3,"Y"]
["South West",260230,"Ilfracombe 33/11kV S Stn",0.36899999999999999,null,349,"",3,"Y"]
["South West",260240,"Roundswell 33/11kV S Stn",0.14000000000000001,null,133,"",3,"Y"]
["South West",260250,"Barnstaple Quay 33/11kV S Stn",0.1,null,115,"",3,"Y"]
["South West",260260,"South Molton 33/11kV S Stn",1.1100000000000001,null,1095,"",3,"Y"]
["South West",260270,"Great Torrington 33/11kV S Stn",0.28999999999999998,null,234,"",3,"Y"]
["South West",260410,"Lynton 33/11kV S Stn",4.5,null,2133,"",3,"Y"]
["South West",260420,"Middle Barlington 33/11kV S Stn",2.4500000000000002,null,1581,"",3,"Y"]
["South West",260430,"Heddon Cross 33/11kV S Stn",1.68,null,1054,"",3,"Y"]
["South West",260440,"Tinkers Cross 33/11kV S Stn",1.593,null,1284,"",3,"Y"]
["South West",260465,"East Yelland 132/33kV S Stn",0.22,null,263,"",3,"Y"]
["South West",260467,"Barnstaple 132/33/11kV S Stn",6.2E-2,null,93,"",3,"Y"]
["South West",260480,"Fremington 33/11kV S Stn",1.7090000000000001,null,2616,"",3,"Y"]
["South West",260550,"Bratton Fleming 33/11kV S Stn",3.82,null,2475,"",3,"Y"]
["South West",260570,"Georgeham 33/11kV S Stn",3.23,null,2061,"",3,"Y"]
["South West",260580,"Aaronsons 33kV S Stn",0.32,null,322,"",3,"Y"]
["South West",260590,"Rock Park 132/33/11kV S Stn",6.2E-2,null,116,"",3,"Y"]
["South West",268000,"Bratton Fleming Solar Park 33kV S Stn",0.81,null,500,"Y",3,"Y"]
["South West",268001,"Knockworthy Farm Solar Park 33kV S Stn",0.57999999999999996,null,500,"Y",3,"Y"]
["South West",268002,"West Hill Solar Farm 33kV S Stn",0.66,null,500,"Y",3,"Y"]
["South West",268004,"Horsacott Solar Farm 33kV S Stn",0.17,null,500,"Y",3,"Y"]
["South West",268005,"Beaford Solar Farm 33kV S Stn",0.375,null,500,"Y",3,"Y"]
["South West",268007,"Kingsland Barton Solar Park 33kV S Stn",0.29199999999999998,null,500,"Y",3,"Y"]
["South West",268008,"Week Farm Solar Park 33kV S Stn",0.43,null,500,"Y",3,"Y"]
["South West",268078,"Luscott Barton Solar Farm 33kV S Stn",0.46899999999999997,null,500,"Y",3,"Y"]
["South West",268081,"Bommerton Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",268091,"Cleave Farm Solar Park 33kV S Stn",0.29199999999999998,null,500,"Y",3,"Y"]
["South West",268113,"Capelands Farm Solar Park 33kV S Stn",0.86,null,500,"Y",3,"Y"]
["South West",268136,"Bommertown Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",306004,"Abham 400/132kV S Stn",0.2,"Y",6635,"",1,"Y"]
["South West",306005,"Exeter Main 400/132kV S Stn",0.115,null,1648,"",1,"Y"]
["South West",310001,"Exeter City 132/33kV S Stn",0.1,null,467,"",3,"Y"]
["South West",310002,"Tiverton 132/33/11kV S Stn",0.187,null,257,"",3,"Y"]
["South West",310003,"Exeter Main 33kV S Stn",0.15,null,1648,"",3,"Y"]
["South West",310004,"Exmouth 132/33kV S Stn",7.5999999999999998E-2,null,323,"",3,"Y"]
["South West",310005,"Sowton 132/33/11kV S Stn",0.1,null,643,"",3,"Y"]
["South West",310006,"Marsh Barton Power Station 132kV S Stn",0.10170999999999999,null,612.70000000000005,"",1,"Y"]
["South West",310007,"North Tawton 132/33kV S Stn",0.20399999999999999,null,255,"",3,"Y"]
["South West",310011,"Witheridge 33/11kV S Stn",3.806,null,3342,"",3,"Y"]
["South West",310012,"Newton St Cyres 33/11kV S Stn",0.72699999999999998,null,1246,"",3,"Y"]
["South West",310013,"Lapford 33/11kV S Stn",0.73099999999999998,null,681,"",3,"Y"]
["South West",310014,"Cowley Road 33/11kV S Stn",6.4000000000000001E-2,null,77,"",3,"Y"]
["South West",310015,"Crediton 33/11kV S Stn",0.11700000000000001,null,120,"",3,"Y"]
["South West",310016,"Folly Bridge 33/11kV S Stn",0.621,null,631,"",3,"Y"]
["South West",310017,"St Thomas 33/11kV S Stn",3.4000000000000002E-2,null,11,"",3,"Y"]
["South West",310018,"Bridge Mills 33/11kV S Stn",0.21,null,201,"",3,"Y"]
["South West",310020,"Athelstan Road 33/11kV S Stn",0.2,null,261,"",3,"Y"]
["South West",310022,"Marsh Barton 33/11kV S Stn",0.7,"Y",87,"",3,"Y"]
["South West",310023,"Tiverton Moorhayes 33/11kV S Stn",0.19900000000000001,null,220,"",3,"Y"]
["South West",310024,"Cullompton 33/11kV S Stn",0.27100000000000002,null,298,"",3,"Y"]
["South West",310025,"Tiverton South 33/11kV S Stn",7.9000000000000001E-2,null,87,"",3,"Y"]
["South West",310026,"Pinhoe 33/11kV S Stn",5.0999999999999997E-2,null,31,"",3,"Y"]
["South West",310028,"Sowton 33/11kV S Stn",0.1,null,20,"",3,"Y"]
["South West",310029,"Heavitree 33/11kV S Stn",0.26,null,323,"",3,"Y"]
["South West",310030,"Exminster 33/11kV S Stn",0.16400000000000001,null,187,"",3,"Y"]
["South West",310031,"Topsham 33/11kV S Stn",0.32400000000000001,null,302,"",3,"Y"]
["South West",310032,"Tiverton Junction 132/33/11kV S Stn",0.187,null,257,"",3,"Y"]
["South West",310033,"Burlescombe 33/11kV S Stn",0.52300000000000002,null,1029,"",3,"Y"]
["South West",310034,"Clyst Honiton 33/11kV S Stn",0.5,null,565,"",3,"Y"]
["South West",310035,"Woodbury 33/11kV S Stn",0.74,null,842,"",3,"Y"]
["South West",310036,"Marsh Green 33/11kV S Stn",0.82799999999999996,null,800,"",3,"Y"]
["South West",310037,"Withycombe Raleigh 33/11kV S Stn",4.4999999999999998E-2,null,14,"",3,"Y"]
["South West",310038,"Exmouth Works 33/11kV S Stn",0.11,null,151,"",3,"Y"]
["South West",310039,"Budleigh Salterton 33/11kV S Stn",9.9000000000000005E-2,null,118,"",3,"Y"]
["South West",310040,"East Budleigh 33/11kV S Stn",2.5,null,2390,"",3,"Y"]
["South West",310041,"Offwell 33/11kV S Stn",1.2410000000000001,null,1452,"",3,"Y"]
["South West",310042,"Honiton Heathfield 33/11kV S Stn",0.21099999999999999,null,180,"",3,"Y"]
["South West",310043,"Ottery St Mary 33/11kV S Stn",0.442,null,487,"",3,"Y"]
["South West",310044,"Core Hill 33/11kV S Stn",0.17799999999999999,null,160,"",3,"Y"]
["South West",310045,"Newton Poppleford 33/11kV S Stn",0.34,null,284,"",3,"Y"]
["South West",310046,"Sidmouth Town 33/11kV S Stn",0.124,null,110,"",3,"Y"]
["South West",310047,"Winslakefoot 33kV S Stn",0.55000000000000004,null,553,"",3,"Y"]
["South West",310048,"Countess Wear 33/11kV S Stn",0.124,null,35,"",3,"Y"]
["South West",310049,"Haven Road 33/11kV S Stn",0.19,null,253,"",3,"Y"]
["South West",310056,"Hemyock 33/11kV S Stn",0.60699999999999998,null,715,"",3,"Y"]
["South West",310057,"Dunkeswell 33/11kV S Stn",0.29099999999999998,null,203,"",3,"Y"]
["South West",310058,"North Tawton 33/11kV S Stn",0.20399999999999999,null,105,"",3,"Y"]
["South West",310059,"Sowton B 33/11kV S Stn",0.1,null,500,"Y",3,"Y"]
["South West",310060,"Exeter Science Park 33/11kV S Stn",0.32,null,500,"Y",3,"Y"]
["South West",310061,"Hill Barton Primary 33/11kV S Stn",0.16900000000000001,null,500,"Y",3,"Y"]
["South West",318026,"Burrowton Farm Solar Park 33kV S Stn",0.16,null,500,"Y",3,"Y"]
["South West",318031,"Fulford Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",318032,"Nether Mill Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",318035,"Ayshford Court Farm Solar Park 33kV S Stn",0.17499999999999999,null,500,"Y",3,"Y"]
["South West",318090,"Till House Solar Park 33kV S Stn",0.17699999999999999,null,500,"Y",3,"Y"]
["South West",318098,"Cullompton Solar Park 33kV S Stn",0.2,null,500,"Y",3,"Y"]
["South West",318110,"Liverton Farm Solar Park 33kV S Stn",0.245,null,500,"Y",3,"Y"]
["South West",318118,"Francis Court Farm Solar Park 33kV S Stn",0.41499999999999998,null,500,"Y",3,"Y"]
["South West",318137,"Bystock Farm Solar Park 33kV S Stn",0.185,null,500,"Y",3,"Y"]
["South West",318146,"Coombe Farm Solar Park 33kV S Stn",0.25,null,500,"Y",3,"Y"]
["South West",318152,"Batsworthy Cross Wind Farm 33kV S Stn",0.49,null,500,"Y",3,"Y"]
["South West",318155,"Red Hill Solar Park 33kV S Stn",0.27100000000000002,null,500,"Y",3,"Y"]
["South West",318161,"Makro Exeter STOR Generator 33kV S Stn",0.34499999999999997,null,500,"Y",3,"Y"]
["South West",318164,"Great Houndbeare Farm Solar Park 33kV S Stn",0.22900000000000001,null,500,"Y",3,"Y"]
["South West",318165,"Water Lane STOR Generator 33kV S Stn",0.49,null,500,"Y",3,"Y"]
["South West",318172,"Sharland Farm Solar Park 33kV S Stn",0.219,null,500,"Y",3,"Y"]
["South West",318173,"Stoneshill Solar Park 33kV S Stn",0.19600000000000001,null,500,"Y",3,"Y"]
["South West",330001,"Ernesettle 132/33kV S Stn",0.153,null,1232,"",3,"Y"]
["South West",330002,"Milehouse 132/33kV S Stn",0.11700000000000001,null,303,"",3,"Y"]
["South West",330003,"Plymouth 132/33kV S Stn",8.5999999999999993E-2,null,43,"",3,"Y"]
["South West",330006,"Plympton 132/33kV S Stn",0.67900000000000005,null,764,"",3,"Y"]
["South West",330011,"Tavistock 33/11kV S Stn",0.53400000000000003,null,737,"",3,"Y"]
["South West",330012,"Weston Mill 33/11kV S Stn",0.14799999999999999,null,205,"",3,"Y"]
["South West",330013,"St Levan Road 33/11kV S Stn",8.7999999999999995E-2,null,130,"",3,"Y"]
["South West",330014,"Adelaide Road 33/11kV S Stn",0.47,null,85,"",3,"Y"]
["South West",330015,"Newport Street 33/11kV S Stn",0.55300000000000005,null,147,"",3,"Y"]
["South West",330016,"Yelverton 33/11kV S Stn",0.42699999999999999,null,445,"",3,"Y"]
["South West",330017,"Merrivale 33/11kV S Stn",0.153,null,214,"",3,"Y"]
["South West",330018,"Alexandra Road 33/11kV S Stn",0.36,null,113,"",3,"Y"]
["South West",330019,"Elim Terrace 33/11kV S Stn",0.16,null,281,"",3,"Y"]
["South West",330020,"Alma Road 33/11kV S Stn",0.16500000000000001,null,244,"",3,"Y"]
["South West",330021,"Armada Street 33/11kV S Stn",0.27,null,113,"",3,"Y"]
["South West",330022,"Buckwell Street 33/11kV S Stn",0.57999999999999996,null,229,"",3,"Y"]
["South West",330023,"Southway 33/11kV S Stn",0.245,null,70,"",3,"Y"]
["South West",330024,"Longbridge 33/11kV S Stn",0.20899999999999999,null,341,"",3,"Y"]
["South West",330025,"Eggbuckland 33/11kV S Stn",7.1999999999999995E-2,null,24,"",3,"Y"]
["South West",330026,"Old Laira Road 33/11kV S Stn",0.65200000000000002,null,266,"",3,"Y"]
["South West",330027,"Prince Rock 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",330028,"Torycombe 33/11kV S Stn",0.32200000000000001,null,284,"",3,"Y"]
["South West",330029,"Linketty Lane 33/11kV S Stn",0.161,null,162,"",3,"Y"]
["South West",330030,"Ivybridge 33/11kV S Stn",0.20200000000000001,null,245,"",3,"Y"]
["South West",330031,"Stentaway 33/11kV S Stn",8.6999999999999994E-2,null,73,"",3,"Y"]
["South West",330032,"Newton Ferrers 33/11kV S Stn",0.46,null,457,"",3,"Y"]
["South West",330037,"Plymstock South 33/11kV S Stn",0.157,null,229,"",3,"Y"]
["South West",330038,"Ernesettle B & S 33/11kV S Stn",0.153,null,216,"",3,"Y"]
["South West",330039,"North Intake 33kV S Stn",0.22,null,297,"",3,"Y"]
["South West",330040,"Lifton 33/11kV S Stn",0.09,null,58,"",3,"Y"]
["South West",330041,"Central Intake 33kV S Stn",0.3,null,421,"",3,"Y"]
["South West",330042,"Langage 33/11kV S Stn",0.121,null,157,"",3,"Y"]
["South West",330044,"Tamar Pumping Station 33kV S Stn",1.46,null,1508,"",3,"Y"]
["South West",330045,"Plymouth BSP 33kV S Stn",8.5999999999999993E-2,null,43,"",3,"Y"]
["South West",330046,"Chelson Generator 33kV S Stn",0.24,null,326,"",3,"Y"]
["South West",330047,"Langage Energy Centre 33kV S Stn",0.61699999999999999,null,5577,null,3,"Y"]
["South West",333718,"Faraday Road STOR Generator 33kV S Stn",0.124,null,500,"Y",3,"Y"]
["South West",333743,"Ernesettle Lane STOR Generator 33kV S Stn",0.156,null,1171,"",3,"Y"]
["South West",333760,"Hemerdon Mine 33/11kV S Stn",0.53,null,500,"Y",3,"Y"]
["South West",338028,"Warleigh Barton Solar Park 33kV S Stn",0.63400000000000001,null,500,"Y",3,"Y"]
["South West",338120,"Balls Wood Solar Park 33kV S Stn",0.28899999999999998,null,500,"Y",3,"Y"]
["South West",338133,"Newnham Farm Solar Park 33kV S Stn",0.56000000000000005,null,500,"Y",3,"Y"]
["South West",338151,"Portworthy Dams Solar Park 33kV S Stn",0.31,null,500,"Y",3,"Y"]
["South West",338169,"Tamerton Bridge STOR Generator 33kV S Stn",1.2949999999999999,null,500,"Y",3,"Y"]
["South West",338177,"Cattledown STOR Generator 33kV S Stn",0.124,null,500,"Y",3,"Y"]
["South West",338181,"Sherford IDNO Connection 33kV S Stn",0.51800000000000002,null,500,"Y",3,"Y"]
["South West",338185,"Marlands Fields Creacombe Solar Park 33kV S Stn",0.48399999999999999,null,483,"",3,"Y"]
["South West",338190,"Newton Downs Solar Park 33kV S Stn",0.46,null,457,"",3,"Y"]
["South West",340001,"Newton Abbot 132/33/11kV S Stn",0.11,null,405,"",3,"Y"]
["South West",340002,"Paignton 132/33kV S Stn",0.42799999999999999,null,823,"",3,"Y"]
["South West",340003,"Torquay 132/33kV S Stn",0.11799999999999999,null,38,"",3,"Y"]
["South West",340004,"Totnes BSP 132/33kV S Stn",0.59599999999999997,null,3699,"",3,"Y"]
["South West",340011,"Chudleigh Knighton 33/11kV S Stn",0.24199999999999999,null,222,"",3,"Y"]
["South West",340012,"Mortonhampstead 33/11kV S Stn",0.20899999999999999,null,116,"",3,"Y"]
["South West",340013,"Ashburton 33/11kV S Stn",0.34,null,481,"",3,"Y"]
["South West",340014,"Buckfastleigh 33/11kV S Stn",0.55700000000000005,null,495,"",3,"Y"]
["South West",340015,"South Brent 33/11kV S Stn",0.5,null,671,"",3,"Y"]
["South West",340016,"Kingsbridge 33/11kV S Stn",0.18,null,118,"",3,"Y"]
["South West",340017,"Teignmouth Gas Works 33/11kV S Stn",6.7000000000000004E-2,null,36,"",3,"Y"]
["South West",340018,"Higher Woodway 33/11kV S Stn",0.16800000000000001,null,198,"",3,"Y"]
["South West",340019,"Newton Abbot Main 33/11kV S Stn",8.5000000000000006E-2,null,23,"",3,"Y"]
["South West",340020,"Bradley Lane 33/11kV S Stn",8.3000000000000004E-2,null,78,"",3,"Y"]
["South West",340021,"Totnes 33/11kV S Stn",0.04,null,46,"",3,"Y"]
["South West",340022,"Blackawton 33/11kV S Stn",1.3859999999999999,null,1249,"",3,"Y"]
["South West",340023,"Dawlish 33/11kV S Stn",0.14299999999999999,null,125,"",3,"Y"]
["South West",340024,"Barton 33/11kV S Stn",0.58099999999999996,null,109,"",3,"Y"]
["South West",340025,"Lawes Bridge 33/11kV S Stn",0.26,null,384,"",3,"Y"]
["South West",340026,"Upton Valley 33/11kV S Stn",6.9000000000000006E-2,null,20,"",3,"Y"]
["South West",340027,"Marldon 33/11kV S Stn",0.14899999999999999,null,119,"",3,"Y"]
["South West",340029,"Churston 33/11kV S Stn",0.621,null,384,"",3,"Y"]
["South West",340030,"Dartmouth 33/11kV S Stn",0.39300000000000002,null,381,"",3,"Y"]
["South West",340032,"Torwood 33/11kV S Stn",8.3000000000000004E-2,null,37,"",3,"Y"]
["South West",340033,"Hollicombe 33/11kV S Stn",0.08,null,23,"",3,"Y"]
["South West",340034,"Colley End 33/11kV S Stn",0.18,null,214,"",3,"Y"]
["South West",340035,"Laywell Brixham 33/11kV S Stn",0.39500000000000002,null,499,"",3,"Y"]
["South West",340038,"Salcombe 33/11kV S Stn",0.20100000000000001,null,270,"",3,"Y"]
["South West",340039,"Bovey Tracey 33/11kV S Stn",0.19700000000000001,null,215,"",3,"Y"]
["South West",340040,"Modbury 33/11kV S Stn",0.21299999999999999,null,218,"",3,"Y"]
["South West",340041,"Stokenham 33/11kV S Stn",0.45500000000000002,null,348,"",3,"Y"]
["South West",340042,"Paignton 33/11kV S Stn",0.42799999999999999,null,823,"",3,"Y"]
["South West",340043,"Heathfield Landfill 33kV S Stn",0.28999999999999998,null,341,"",3,"Y"]
["South West",341542,"Laywell 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",348027,"Marley Thatch Farm Solar Park 33kV S Stn",0.76200000000000001,null,500,"Y",3,"Y"]
["South West",348033,"Slade Farm Solar Park 33kV S Stn",0.498,null,500,"Y",3,"Y"]
["South West",348045,"Hatchlands Farm Solar Park 33kV S Stn",0.4,null,500,"Y",3,"Y"]
["South West",348077,"Hazard Farm Solar Park 33kV S Stn",0.496,null,500,"Y",3,"Y"]
["South West",348103,"Bidwell Solar Park 33kV S Stn",0.29799999999999999,null,500,"Y",3,"Y"]
["South West",348111,"Yonder Parks Solar Park 33kV S Stn",0.86,null,500,"Y",3,"Y"]
["South West",348121,"Rydon Farm Solar Park 33kV S Stn",8.5999999999999993E-2,null,500,"Y",3,"Y"]
["South West",348131,"Coombeshead Farm Solar Park 33kV S Stn",0.56000000000000005,null,500,"Y",3,"Y"]
["South West",348132,"Ashcombe Solar Park 33kV S Stn",6.6000000000000003E-2,null,500,"Y",3,"Y"]
["South West",348134,"Parkview Solar Park 33kV S Stn",0.63,null,500,"Y",3,"Y"]
["South West",348175,"Old Stone Farm Solar Park 33kV S Stn",1.3019229999999999,null,500,"Y",3,"Y"]
["South West",348176,"Place Barton Farm Solar Park 33kV S Stn",0.89551000000000003,null,500,"Y",3,"Y"]
["South West",348178,"Barton Hill STOR Generator 33kV S Stn",0.41,null,500,"Y",3,"Y"]
["South West",348182,"Alders Way STOR 33kV S Stn",0.42799999999999999,null,500,"Y",3,"Y"]
["South West",350001,"Pyworthy 132/33kV S Stn",0.57199999999999995,null,904,"",3,"Y"]
["South West",350011,"Clovelly 33/11kV S Stn",2.1,null,1338,"",3,"Y"]
["South West",350012,"Stratton 33/11kV S Stn",0.36699999999999999,null,595,"",3,"Y"]
["South West",350013,"Shebbear 33/11kV S Stn",2.5,null,1853,"",3,"Y"]
["South West",350014,"Holsworthy 33/11kV S Stn",0.251,null,402,"",3,"Y"]
["South West",350015,"East Curry 33/11kV S Stn",0.93100000000000005,null,865,"",3,"Y"]
["South West",350016,"Northam 33/11kV S Stn",0.11600000000000001,null,126,"",3,"Y"]
["South West",350017,"Park Lane 33/11kV S Stn",7.3999999999999996E-2,null,83,"",3,"Y"]
["South West",350018,"Bideford Main 33/11kV S Stn",0.104,null,115,"",3,"Y"]
["South West",350019,"Hatherleigh 33/11kV S Stn",0.155,null,177,"",3,"Y"]
["South West",350021,"Whiddon Down 33/11kV S Stn",2.2200000000000002,null,1725,"",3,"Y"]
["South West",350022,"Ashwater 33/11kV S Stn",2.8330000000000002,null,3043,"",3,"Y"]
["South West",350023,"Roadford 33kV S Stn",0.41,null,406,"",3,"Y"]
["South West",350024,"Morwenstow 33/11kV S Stn",2.09,null,2036,"",3,"Y"]
["South West",350025,"Forestmoor 33/11kV S Stn",0.72,null,715,"",3,"Y"]
["South West",350050,"Okehampton 33/11kV S Stn",0.23,null,216,"",3,"Y"]
["South West",357295,"Galsworthy Wind Farm 132kV S Stn",0.54,null,1400,"Y",1,"Y"]
["South West",357304,"Carnworthy Solar Park 132kV S Stn",1.254,null,1400,"Y",1,"Y"]
["South West",358017,"East Langford Solar Park 33kV S Stn",0.28999999999999998,null,402,"",3,"Y"]
["South West",358022,"Eastacombe Solar Farm 33kV S Stn",0.33500000000000002,null,500,"Y",3,"Y"]
["South West",358050,"Lower Tinacre Solar Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",358056,"Higher North Beer Farm Solar Park 33kV S Stn",0.20699999999999999,null,500,"Y",3,"Y"]
["South West",358057,"Bradford Manor Solar Farm 33kV S Stn",0.34,null,500,"Y",3,"Y"]
["South West",358064,"Rexon Cross Farm Solar Park 33kV S Stn",0.45800000000000002,null,500,"Y",3,"Y"]
["South West",358067,"Willsland Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",358068,"Crinacott Farm Solar Park 33kV S Stn",0.14000000000000001,null,500,"Y",3,"Y"]
["South West",358074,"Pitworthy Solar Park 33kV S Stn",0.33700000000000002,null,500,"Y",3,"Y"]
["South West",358076,"Foxcombe Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",358079,"Alverdiscott Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",358080,"Derriton Fields Solar Park 33kV S Stn",0.28499999999999998,null,500,"Y",3,"Y"]
["South West",358085,"Chalhanger Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",358114,"East Youlstone Windfarm 33kV S Stn",0.7,null,500,"Y",3,"Y"]
["South West",358116,"Northmoor Solar Park 132kV S Stn",0.92,null,1400,"Y",1,"Y"]
["South West",358129,"Walland Farm Solar Park 33kV S Stn",0.3,null,500,"Y",3,"Y"]
["South West",358159,"Denbrook Wind Farm 33kV S Stn",0.16600000000000001,null,500,"Y",3,"Y"]
["South West",358160,"Ashwater Solar Park 33kV S Stn",0.5,null,500,"Y",3,"Y"]
["South West",358167,"Dunsland Cross Wind Farm 33kV S Stn",0.29799999999999999,null,500,"Y",3,"Y"]
["South West",406002,"Indian Queens 400/132kV S Stn",0.2,"Y",3070,"",1,"Y"]
["South West",406003,"Landulph GSP 400/132kV S Stn",0.43,null,3182,"",1,"Y"]
["South West",407020,"Camborne 132/33kV S Stn",0.23200000000000001,null,512,"",3,"Y"]
["South West",407150,"Hayle 132/33kV S Stn",9.5000000000000001E-2,null,112,"",3,"Y"]
["South West",407380,"Fraddon 132/33kV S Stn",0.27400000000000002,null,2392,"",3,"Y"]
["South West",407450,"St Tudy 132/33kV S Stn",1.069,null,1110,"",3,"Y"]
["South West",415927,"Goonhilly Wind Farm 33kV S Stn",0.52,null,388,"",3,"Y"]
["South West",417010,"Camborne Treswithian 33/11kV S Stn",2.2789999999999999,null,3519,"",3,"Y"]
["South West",417020,"Camborne Carn Brea 33/11kV S Stn",0.216,null,177,"",3,"Y"]
["South West",417030,"Lanner 33/11kV S Stn",8.4740000000000002,null,4813,"",3,"Y"]
["South West",417040,"Geevor 33/11kV S Stn",3.4,null,2309,"",3,"Y"]
["South West",417050,"Helston 33/11kV S Stn",0.25900000000000001,null,336,"",3,"Y"]
["South West",417060,"Wheal Reeth 33/11kV S Stn",4.51,null,2500,"",3,"Y"]
["South West",417070,"Marazion 33/11kV S Stn",1.347,null,1611,"",3,"Y"]
["South West",417080,"Penzance Heamoor 33/11kV S Stn",0.32300000000000001,null,627,"",3,"Y"]
["South West",417090,"St Buryan 33/11kV S Stn",6.9039999999999999,null,4163,"",3,"Y"]
["South West",417100,"Perranporth 33/11kV S Stn",4.29,null,3693,"",3,"Y"]
["South West",417110,"Redruth 33/11kV S Stn",0.42599999999999999,null,849,"",3,"Y"]
["South West",417120,"Roseland 33/11kV S Stn",3.1789999999999998,null,2241,"",3,"Y"]
["South West",417130,"St Ives 33/11kV S Stn",3.37,null,5220,"",3,"Y"]
["South West",417140,"Truro Shortlanesend 33/11kV S Stn",3.4020000000000001,null,3742,"",3,"Y"]
["South West",417150,"Hayle 33/11kV S Stn",9.5000000000000001E-2,null,131,"",3,"Y"]
["South West",417160,"Falmouth Bickland Hill 33/11kV S Stn",0.186,null,275,"",3,"Y"]
["South West",417170,"Penryn 33/11kV S Stn",0.99399999999999999,null,1552,"",3,"Y"]
["South West",417180,"Falmouth Docks 33/11kV S Stn",0.13400000000000001,null,182,"",3,"Y"]
["South West",417310,"Devoran 33/11kV S Stn",2.1150000000000002,null,2563,"",3,"Y"]
["South West",417320,"Constantine 33/11kV S Stn",3.8519999999999999,null,4898,"",3,"Y"]
["South West",417330,"St Keverne 33/11kV S Stn",4.3120000000000003,null,4271,"",3,"Y"]
["South West",417340,"Mousehole 33/11kV S Stn",3.3639999999999999,null,2301,"",3,"Y"]
["South West",417500,"Rame132/33kV S Stn",1.7230000000000001,null,2340,"",3,"Y"]
["South West",417540,"Camborne Holmans 33/11kV S Stn",0.23699999999999999,null,390,"",3,"Y"]
["South West",417560,"Probus 33/11kV S Stn",2.69,null,1783,"",3,"Y"]
["South West",417580,"Penzance Causewayhead 33/11kV S Stn",0.112,null,149,"",3,"Y"]
["South West",417590,"St Agnes 33/11kV S Stn",4.59,null,2528,"",3,"Y"]
["South West",417600,"Truro Treyew Road 33/11kV S Stn",0.224,null,343,"",3,"Y"]
["South West",417670,"St Day Landfill 33kV S Stn",0.63,null,419,"",3,"Y"]
["South West",417680,"Twelveheads 33/11kV S Stn",7.48,null,5739,"",3,"Y"]
["South West",417690,"Newlyn 33/11kV S Stn",0.55100000000000005,null,1160,"",3,"Y"]
["South West",417740,"Truro 132/33kV S Stn",0.99,null,946,"",3,"Y"]
["South West",417760,"Isles Of Scilly 33/11kV S Stn",0.52400000000000002,null,214,"",3,"Y"]
["South West",417780,"Mullion 33/11kV S Stn",0.443,null,338,"",3,"Y"]
["South West",417800,"Carland Cross Wind Farm 33kV S Stn",0.52,null,1435,"",3,"Y"]
["South West",417820,"Four Burrows Windfarm 33kV S Stn",0.38200000000000001,null,845,"",3,"Y"]
["South West",418008,"Churchtown Farm Solar Park 33kV S Stn",0.37,null,262,"",3,"Y"]
["South West",418009,"Chynoweth Solar Park 33kV S Stn",0.38,null,821,null,3,"Y"]
["South West",418029,"Hope Solar Park 33kV S Stn",0.432,null,500,"Y",3,"Y"]
["South West",418034,"Higher Trenhayle Farm Solar Park 33kV S Stn",0.93300000000000005,null,500,"Y",3,"Y"]
["South West",418041,"Fourburrows Pendown 33kV S Stn",0.48,null,500,"Y",3,"Y"]
["South West",418046,"Causilgey Solar Farm 33kV S Stn",1.1100000000000001,null,500,"Y",3,"Y"]
["South West",418049,"Higher Tregarne Solar Farm 33kV S Stn",1.04,null,500,"Y",3,"Y"]
["South West",418060,"Little Trevease Farm Solar Farm 33kV S Stn",1.79,null,500,"Y",3,"Y"]
["South West",418069,"Penare Farm Solar Farm 33kV S Stn",0.41,null,500,"Y",3,"Y"]
["South West",418070,"Tregassow Solar Farm 33kV S Stn",0.71,null,500,"Y",3,"Y"]
["South West",418096,"Gover Park Solar Park 33kV S Stn",0.54900000000000004,null,500,"Y",3,"Y"]
["South West",418101,"Nanteague Solar Park 33kV S Stn",0.75,null,500,"Y",3,"Y"]
["South West",418102,"Goonhilly Solar Park 33kV S Stn",0.36,null,500,"Y",3,"Y"]
["South West",418108,"Four Burrows Blackdown Solar Park 33kV S Stn",0.878,null,500,"Y",3,"Y"]
["South West",418125,"Pencoose Solar Park 33kV S Stn",1.26,null,500,"Y",3,"Y"]
["South West",418126,"Garvinack Farm Solar Park 33kV S Stn",0.7,null,500,"Y",3,"Y"]
["South West",418135,"Roskrow Barton Solar Park 33kV S Stn",0.7,null,500,"Y",3,"Y"]
["South West",418141,"Burthy Solar Park 33kV S Stn",0.46,null,500,"Y",3,"Y"]
["South West",418158,"Carnemough Farm Solar Park 33kV S Stn",0.56100000000000005,null,500,"Y",3,"Y"]
["South West",418163,"Nancrossa Solar Park 33kV S Stn",1.9279999999999999,null,500,"Y",3,"Y"]
["South West",437150,"Bears Down Wind Farm 33kV S Stn",0.55000000000000004,null,282,"",3,"Y"]
["South West",437190,"St Austell  33/11kV S Stn",0.77,null,1482,"",3,"Y"]
["South West",437200,"St Blazey 33kV S Stn",0.443,null,678,"",3,"Y"]
["South West",437210,"Wadebridge 33/11kV S Stn",3.92,null,3775,"",3,"Y"]
["South West",437220,"Newquay Trevemper 33/11kV S Stn",0.66600000000000004,null,1010,"",3,"Y"]
["South West",437230,"Bodmin 33/11kV S Stn",0.189,null,242,"",3,"Y"]
["South West",437340,"Connon Bridge Landfill 33kV S Stn",1.7,null,1513,"",3,"Y"]
["South West",437350,"Blackpool 33/11kV S Stn",0.53300000000000003,null,534,"",3,"Y"]
["South West",437360,"Bugle 33/11kV S Stn",0.43,null,476,"",3,"Y"]
["South West",437370,"Drinnick 33/11kV S Stn",0.96699999999999997,null,1462,"",3,"Y"]
["South West",437380,"Fraddon 33/11kV S Stn",0.27400000000000002,null,2121,"",3,"Y"]
["South West",437390,"Lostwithiel 33/11kV S Stn",1.377,null,1526,"",3,"Y"]
["South West",437400,"Mevagissey 33/11kV S Stn",0.9,null,1128,"",3,"Y"]
["South West",437410,"Davidstow 33/11kV S Stn",4.3,null,3677,"",3,"Y"]
["South West",437420,"Delabole 33/11kV S Stn",1.278,null,1388,"",3,"Y"]
["South West",437430,"Padstow 33/11kV S Stn",1.21,null,975,"",3,"Y"]
["South West",437440,"St Mawgan 33/11kV S Stn",0.76800000000000002,null,658,"",3,"Y"]
["South West",437450,"St Tudy 33/11kV S Stn",1.069,null,2071,"",3,"Y"]
["South West",437460,"Lanreath 33/11kV S Stn",1.4710000000000001,null,1352,"",3,"Y"]
["South West",437470,"Dairy Crest Davidstow 33/11kV S Stn",1.1499999999999999,null,771,"",3,"Y"]
["South West",437490,"St Columb Major 33/11kV S Stn",1.591,null,1632,"",3,"Y"]
["South West",437550,"Polzeath 33/11kV S Stn",2.573,null,2560,"",3,"Y"]
["South West",437570,"Fowey 33/11kV S Stn",1.448,null,1725,"",3,"Y"]
["South West",437610,"Newquay Trencreek Ln 33/11kV S Stn",0.46899999999999997,null,463,"",3,"Y"]
["South West",437640,"Sawles Road 33/11kV S Stn",0.28899999999999998,null,252,"",3,"Y"]
["South West",437670,"Par Harbour 33/11kV S Stn",0.22800000000000001,null,350,"",3,"Y"]
["South West",437720,"Trebal 33/11kV S Stn",1.7050000000000001,null,1755,"",3,"Y"]
["South West",437730,"St Austell BSP 132/33kV S Stn",0.629,null,775,"",3,"Y"]
["South West",437750,"Treningle 33kV S Stn",2.0699999999999998,null,1888,"",3,"Y"]
["South West",437790,"St Breock 33kV S Stn",0.83,null,425,"",3,"Y"]
["South West",437830,"Callywith 33/11kV S Stn",0.46800000000000003,null,394,"",3,"Y"]
["South West",438010,"Trenouth Farm Solar Park 33kV S Stn",0.8,null,735,"",3,"Y"]
["South West",438011,"Manor Farm Solar Park 33kV S Stn",0.214,null,350,"",3,"Y"]
["South West",438018,"Rockhead Wind Farm 33kV S Stn",1.133,null,1176,"",3,"Y"]
["South West",438020,"Bodiniel Solar Park 33kV S Stn",0.9,null,500,"Y",3,"Y"]
["South West",438024,"Woodland Barton Solar Park 33kV S Stn",0.71,null,500,"Y",3,"Y"]
["South West",438025,"Luxulyan Solar Park 33kV S Stn",1.89,null,500,"Y",3,"Y"]
["South West",438036,"Middle Treworder Farm Solar Park 33kV S Stn",0.68100000000000005,null,500,"Y",3,"Y"]
["South West",438037,"Rew Farm Solar Park 33kV S Stn",0.57999999999999996,null,500,"Y",3,"Y"]
["South West",438038,"Winnards Perch Solar Farm 33kV S Stn",0.38,null,500,"Y",3,"Y"]
["South West",438039,"Penhale Solar Farm 33kV S Stn",0.8,null,500,"Y",3,"Y"]
["South West",438040,"Trekenning Farm Solar Park 33kV S Stn",0.39,null,500,"Y",3,"Y"]
["South West",438051,"Ninnis Solar Farm 33kV S Stn",0.26500000000000001,null,459,null,3,"Y"]
["South West",438059,"Langunnett Farm Solar Farm 33kV S Stn",0.38,null,500,"Y",3,"Y"]
["South West",438066,"Hewas Solar Farm 33kV S Stn",0.32,null,500,"Y",3,"Y"]
["South West",438084,"Garlenick Wind Farm 33kV S Stn",1.306,null,500,"Y",3,"Y"]
["South West",438087,"Carloggas Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",438088,"Tregarrick Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",438092,"Outlands Wood Solar Park 33kV S Stn",0.434,null,500,"Y",3,"Y"]
["South West",438094,"St Stephen Solar Park 33kV S Stn",0.36199999999999999,null,500,"Y",3,"Y"]
["South West",438099,"Kerriers Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",438107,"Victoria Wind Farm 33kV S Stn",1.121,null,500,"Y",3,"Y"]
["South West",438148,"Denzell Downs Wind Farm 33kV S Stn",0.15640000000000001,null,500,"Y",3,"Y"]
["South West",438149,"Cornwall Energy Recovery Centre 132kV S Stn",0.78,null,1400,"Y",1,"Y"]
["South West",438156,"West Carclaze Solar Park 33kV S Stn",0.78,null,500,"Y",3,"Y"]
["South West",438171,"Bodwen Solar Farm 33kV S Stn",1.46,null,500,"Y",3,"Y"]
["South West",457240,"Torpoint Antony 33/11kV S Stn",1.39,null,1936,"",3,"Y"]
["South West",457250,"Launceston 33/11kV S Stn",0.13,null,296,"",3,"Y"]
["South West",457260,"Callington 33/11kV S Stn",0.13800000000000001,null,180,"",3,"Y"]
["South West",457270,"Gunnislake 33/11kV S Stn",8.6,null,4954,"",3,"Y"]
["South West",457280,"Saltash Whity Cross 33/11kV S Stn",3.0339999999999998,null,3501,"",3,"Y"]
["South West",457290,"Liskeard 33/11kV S Stn",0.432,null,638,"",3,"Y"]
["South West",457300,"Looe 33/11kV S Stn",0.94099999999999995,null,1622,"",3,"Y"]
["South West",457470,"Pensilva 33/11kV S Stn",5.0110000000000001,null,3403,"",3,"Y"]
["South West",457480,"St Neot 33/11kV S Stn",3.91,null,2491,"",3,"Y"]
["South West",457510,"St Germans 132/33kV S Stn",0.95299999999999996,null,3810,"",3,"Y"]
["South West",457520,"Saltash Dunheved Rd 33/11kV S Stn",0.27500000000000002,null,271,"",3,"Y"]
["South West",457530,"Torpoint Town 33/11kV S Stn",0.245,null,290,"",3,"Y"]
["South West",457620,"Laneast 33/11kV S Stn",5.55,null,2270,"",3,"Y"]
["South West",457710,"Landulph 132/33kV S Stn",0.32,null,3050,"",3,"Y"]
["South West",457810,"Cold Northcott Wind Farm 33kV S Stn",0.12,null,69,"",3,"Y"]
["South West",458013,"Howton Farm Solar Park 33kV S Stn",0.57999999999999996,null,1148,"",3,"Y"]
["South West",458030,"Haye Lane Solar Park 33kV S Stn",0.112,null,500,"Y",3,"Y"]
["South West",458047,"Ford Farm Solar Farm 33kV S Stn",1.1499999999999999,null,500,"Y",3,"Y"]
["South West",458048,"Higher Trevartha Solar Farm 33kV S Stn",1.46,null,500,"Y",3,"Y"]
["South West",458052,"Trequite Solar Farm 33kV S Stn",0.57899999999999996,null,500,"Y",3,"Y"]
["South West",458053,"Yonder Netherton 33kV Solar Farm 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",458058,"Trefinnick Farm Solar Farm 33kV S Stn",0.39,null,500,"Y",3,"Y"]
["South West",458082,"Trehawke Farm Solar Park 33kV S Stn",0.308,null,500,"Y",3,"Y"]
["South West",458086,"Hexworthy Barton Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",458089,"Freathy Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South West",458095,"Trewidland Farm Solar Park 33kV S Stn",0.34799999999999998,null,500,"Y",3,"Y"]
["South West",458097,"North Wayton Solar Park 33kV S Stn",0.28399999999999997,null,500,"Y",3,"Y"]
["South West",458109,"Otterham Wind Farm 132kV S Stn",0.2,null,1400,"Y",1,"Y"]
["South West",458128,"Newton Barton Solar Park 33kV S Stn",0.32,null,500,"Y",3,"Y"]
["South West",458142,"Wilton Farm Solar Park 33kV S Stn",1.0369999999999999,null,500,"Y",3,"Y"]
["South West",458145,"Wilton 33kV S Stn",0.95299999999999996,null,500,"Y",3,"Y"]
["South West",458147,"Wilton Farm Wind Farm 33kV S Stn",1.01,null,500,"Y",3,"Y"]
["South West",458162,"Trerule Solar Park 33kV S Stn",0.29699999999999999,null,500,"",3,"Y"]
["South Wales",510006,"Cardiff Central Grid 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
["South Wales",510007,"Cardiff East Grid 275/132/33/11kV S Stn",0.2,"Y",1480,"",3,"Y"]
["South Wales",510008,"Cardiff North Grid 132/33kV S Stn",8.1000000000000003E-2,null,1000,"Y",3,"Y"]
["South Wales",510009,"Cardiff West Grid 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
["South Wales",510049,"Aberthaw Power Station 275/132kV S Stn",0.2,"Y",2152,"",1,"Y"]
["South Wales",510059,"East Aberthaw 132/33kV S Stn",0.16,null,1000,"Y",3,"Y"]
["South Wales",510064,"Ashgrove 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510069,"Birchgrove 33/11kV S Stn",6.7000000000000004E-2,null,500,"Y",3,"Y"]
["South Wales",510086,"Broad St. Barry 33/11kV S Stn",0.26300000000000001,null,500,"Y",3,"Y"]
["South Wales",510088,"Brynhill Barry Grid 132/33/11kV S Stn",0.08,null,1000,"Y",3,"Y"]
["South Wales",510096,"Canton 33/11kV S Stn",0.19700000000000001,null,500,"Y",3,"Y"]
["South Wales",510104,"Court Rd. Barry 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510108,"Crwys Rd. 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510115,"Cyncoed 33/11kV S Stn",0.23,null,500,"Y",3,"Y"]
["South Wales",510119,"Ely 33/11kV S Stn",7.3999999999999996E-2,null,500,"Y",3,"Y"]
["South Wales",510121,"Fairwater 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510141,"Heath 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510144,"Highmead 33/11kV S Stn",4.5999999999999999E-2,null,96,"",3,"Y"]
["South Wales",510148,"Ironbridge 33/11kV S Stn",7.3999999999999996E-2,null,163,"",3,"Y"]
["South Wales",510152,"Llandough 33/11kV S Stn",7.0000000000000007E-2,null,500,"Y",3,"Y"]
["South Wales",510160,"Llanishen 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510178,"Morlanga Farm 33/11kV S Stn",1.214,null,500,"Y",3,"Y"]
["South Wales",510190,"Northcote St. 33/11kV S Stn",6.8000000000000005E-2,null,500,"Y",3,"Y"]
["South Wales",510198,"Park Lane 33/11kV S Stn",8.2000000000000003E-2,null,500,"Y",3,"Y"]
["South Wales",510199,"Penarth 33/11kV S Stn",0.14199999999999999,null,500,"Y",3,"Y"]
["South Wales",510218,"Sanatorium 33/11kV S Stn",5.5E-2,null,500,"Y",3,"Y"]
["South Wales",510219,"Sandon St. 33/11kV S Stn",0.14000000000000001,null,500,"Y",3,"Y"]
["South Wales",510223,"Ship Hill Barry 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510230,"St Mellons 33/11kV S Stn",0.13600000000000001,null,500,"Y",3,"Y"]
["South Wales",510238,"Taff Bank 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510310,"Wood Street 33/11kV S Stn",0.61,null,500,"Y",3,"Y"]
["South Wales",510327,"Heath Hospital Primary 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510356,"Trident Park Generation 33kV S Stn",0.09,null,500,"Y",3,"Y"]
["South Wales",510362,"Sutton Farm Solar Park 33kV S Stn",0.109,null,500,"Y",3,"Y"]
["South Wales",510366,"Peakgen Barry STOR 33kV S Stn",0.23,null,500,"Y",3,"Y"]
["South Wales",510398,"Jesus College P V Generation 33kV S Stn",0.16200000000000001,null,500,"Y",3,"Y"]
["South Wales",510399,"Sully Moors Power Station 33kV S Stn",0.15,null,500,"Y",3,"Y"]
["South Wales",510401,"Llancadle Solar Farm 33kV S Stn",0.16,null,500,"Y",3,"Y"]
["South Wales",510407,"Derwyn Solar Farm 33kV S Stn",0.14000000000000001,null,500,"Y",3,"Y"]
["South Wales",510428,false,0.20599999999999999,null,405,"",3,"Y"]
["South Wales",510429,"Barry Dock Biomass 33kV S Stn",0.10299999999999999,null,500,"Y",3,"Y"]
["South Wales",510439,"Broad Street Swg Site 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510447,"Trident Park 33kv Waste Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",510902,"Trowbridge 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["South Wales",510905,"Cardiff South Grid 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["South Wales",510908,"Grangetown Grid Primary 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["South Wales",510909,"Sully Grid Primary 132/11kV S Stn",0.13400000000000001,null,1000,"Y",1,"Y"]
["South Wales",510911,"Rover Way 132/11kV S Stn",8.6999999999999994E-2,null,1000,"Y",1,"Y"]
["South Wales",510928,"GKN Rod Mill 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",520002,"Ammanford Grid 132/33kV S Stn",0.41699999999999998,null,1000,"Y",3,"Y"]
["South Wales",520022,"Llanelli Grid 132/11kV S Stn",8.5000000000000006E-2,null,1000,"Y",1,"Y"]
["South Wales",520035,"Swansea North Grid 132/33kV S Stn",0.17,null,4216,"",3,"Y"]
["South Wales",520036,"Swansea West Grid 132/33kV S Stn",0.17599999999999999,null,1000,"Y",3,"Y"]
["South Wales",520037,"Tir John Primary 132/33/6.6kV S Stn",8.4000000000000005E-2,null,1000,"Y",3,"Y"]
["South Wales",520038,"Trostre Grid 132/33kV S Stn",0.14000000000000001,null,1000,"Y",3,"Y"]
["South Wales",520041,"Travellers Rest 33/11kV S Stn",0.32800000000000001,null,500,"Y",3,"Y"]
["South Wales",520045,"Gowerton East Grid 132/33kV S Stn",0.156,null,1000,"Y",3,"Y"]
["South Wales",520070,"Bishopston 33/11kV S Stn",0.434,null,500,"Y",3,"Y"]
["South Wales",520100,"Clase 33/11kV S Stn",0.20399999999999999,null,500,"Y",3,"Y"]
["South Wales",520118,"Westfa 33/11kV S Stn",2.04,null,500,"Y",3,"Y"]
["South Wales",520127,"Garngoch 33/11kV S Stn",0.29199999999999998,null,743,"",3,"Y"]
["South Wales",520129,"Gethin Street Swansea 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",520137,"Gwaun Cae Gurwen 33/11kV S Stn",1.82,null,500,"Y",3,"Y"]
["South Wales",520142,"Hendy 33/11kV S Stn",0.29299999999999998,null,500,"Y",3,"Y"]
["South Wales",520145,"Waunarlwyd 33kV S Stn",0.39300000000000002,null,500,"Y",3,"Y"]
["South Wales",520147,"Inco Europe South 33kV S Stn",0.21,null,500,"Y",3,"Y"]
["South Wales",520162,"Llanrhidian 33/11kV S Stn",1.4319999999999999,null,500,"Y",3,"Y"]
["South Wales",520172,"Meinciau 33/11kV S Stn",3.44,null,500,"Y",3,"Y"]
["South Wales",520187,"New Lodge 33/11kV S Stn",0.18,null,500,"Y",3,"Y"]
["South Wales",520197,"Pantyffynon 33/11kV S Stn",0.20699999999999999,null,500,"Y",3,"Y"]
["South Wales",520207,"Pontardawe 33/11kV S Stn",0.3,null,500,"Y",3,"Y"]
["South Wales",520209,"Pontyates 33/11kV S Stn",0.93600000000000005,null,500,"Y",3,"Y"]
["South Wales",520211,"Ravenhill 33/11kV S Stn",5.6259999999999998E-2,null,161,"",3,"Y"]
["South Wales",520217,"Lime Street Gorseinon 33/11kV S Stn",0.28000000000000003,null,500,"Y",3,"Y"]
["South Wales",520225,"Sketty Park 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",520233,"Strand Swansea 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",520248,"Tumble 33/11kV S Stn",0.154,null,500,"Y",3,"Y"]
["South Wales",520250,"Uplands Swansea 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",520251,"Upper Bank 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",520258,"West Cross 33/11kV S Stn",0.184,null,500,"Y",3,"Y"]
["South Wales",520259,"Westfa 33/11kV S Stn",0.10100000000000001,null,500,"Y",3,"Y"]
["South Wales",520274,"Swansea Trading Estate 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",520284,"Jersey Marine 33/11kV S Stn",9.2999999999999999E-2,null,500,"Y",3,"Y"]
["South Wales",520286,"Kidwelly 33/11kV S Stn",0.748,null,500,"Y",3,"Y"]
["South Wales",520291,"Morriston 132/11kV S Stn",0.127,null,1000,"Y",1,"Y"]
["South Wales",520299,"Maes Ar Dafen 33/11kV S Stn",0.16400000000000001,null,500,"Y",3,"Y"]
["South Wales",520307,"Cross Hands 33/11kV S Stn",0.248,null,500,"Y",3,"Y"]
["South Wales",520312,"Crymlyn Burrows 33kV S Stn",0.3,null,500,"Y",3,"Y"]
["South Wales",520316,"Swansea University 33/11kV S Stn",1.9504999999999999,null,500,"Y",3,"Y"]
["South Wales",520317,"Swansea Waterfront 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",520318,"Pwllfa Gwatkin 33kV S Stn",1.6819999999999999,null,500,"Y",3,"Y"]
["South Wales",520326,"Felindre Pumping Station 33kV S Stn",0.26900000000000002,null,500,"Y",3,"Y"]
["South Wales",520334,"Western Coal 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",520339,"Cefn Betingau Solar PV 33kV S Stn",0.34100000000000003,null,500,"Y",3,"Y"]
["South Wales",520340,"Clawdd Ddu Solar Farm 33kV S Stn",0.34,null,500,"Y",3,"Y"]
["South Wales",520341,"Betws Wind Farm Grid 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["South Wales",520344,"Waunarlwydd STOR Generation 33kV S Stn",0.39300000000000002,null,500,"Y",3,"Y"]
["South Wales",520345,"Ffos Las PV Generation 33kV S Stn",0.32400000000000001,null,500,"Y",3,"Y"]
["South Wales",520346,"Pont Andrew PV Generation 33kV S Stn",0.68100000000000005,null,500,"Y",3,"Y"]
["South Wales",520348,"Tir John STOR Generation 33kV S Stn",8.4000000000000005E-2,null,500,"Y",3,"Y"]
["South Wales",520360,"Swansea North Local 33/11kV S Stn",0.3,null,500,"Y",3,"Y"]
["South Wales",520365,"Pentre Solar Farm Generation 33kV S Stn",0.8,null,500,"Y",3,"Y"]
["South Wales",520371,"Pen Y Cae Solar 33kV S Stn",0.2,null,500,"Y",3,"Y"]
["South Wales",520373,"Saron Solar Farm 33kV S Stn",0.18,null,500,"Y",3,"Y"]
["South Wales",520374,"Brynteg Solar Farm 33kV S Stn",0.34,null,500,"Y",3,"Y"]
["South Wales",520381,"Abergelli PV Generation Site 33kV S Stn",0.36,null,500,"Y",3,"Y"]
["South Wales",520386,"Rhyd Y Pandy Solar Park 33kV S Stn",0.25,null,500,"Y",3,"Y"]
["South Wales",520388,"Blaenlleidi Wind Farm 33kV S Stn",2.2000000000000002,null,500,"Y",3,"Y"]
["South Wales",520392,"Gelliwern Isaf Pv Gen 33kV S Stn",0.42,null,500,"Y",3,"Y"]
["South Wales",520396,"Brynwhilach Solar Park 33kV S Stn",0.13200000000000001,null,500,"Y",3,"Y"]
["South Wales",520410,"Mynydd Y Gwrhyd Wind Generation 33kV S Stn",0.92,null,500,"Y",3,"Y"]
["South Wales",520423,"Cockett Valley Solar Park 33kV S Stn",0.41199999999999998,null,500,"Y",3,"Y"]
["South Wales",520427,"Gowerton STOR 33kV S Stn",0.27300000000000002,null,479,"",3,"Y"]
["South Wales",520435,"Brechfa Forest West Wind Farm 132kV S Stn",1.45,null,1000,"Y",1,"Y"]
["South Wales",520438,"Mynydd Y Gwair Wind Farm 132kV S Stn",0.61599999999999999,null,3000,"",1,"Y"]
["South Wales",520445,"Mynydd Uchaf Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",520446,"Brynhenllys Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",530001,"Abergavenny 132/66kV S Stn",7.8E-2,null,271,null,1,"Y"]
["South Wales",530023,"Llantarnam 132/66kV S Stn",0.10299999999999999,null,460,null,1,"Y"]
["South Wales",530027,"Newport East 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["South Wales",530028,"Newport South 132/33kV S Stn",1.7999999999999999E-2,null,148,null,1,"Y"]
["South Wales",530034,"Sudbrook 132/33kV S Stn",0.11,null,440,null,1,"Y"]
["South Wales",530046,"Uskmouth 275/132kV S Stn",0.2,"Y",901,"",1,"Y"]
["South Wales",530056,"Abersychan 66/11kV S Stn",0.20599999999999999,null,244,null,3,"Y"]
["South Wales",530071,"Blaenavon 66/11kV S Stn",0.11,null,146,"",3,"Y"]
["South Wales",530095,"Caldicot 33/11kV S Stn",0.11600000000000001,null,102,null,3,"Y"]
["South Wales",530099,"Chepstow 33/11kV S Stn",0.36499999999999999,null,341,null,3,"Y"]
["South Wales",530110,"Cwmbran Primary 132/11kV S Stn",6.3E-2,null,287,null,1,"Y"]
["South Wales",530177,"Monmouth 66/11kV S Stn",7.3999999999999996E-2,null,85,null,3,"Y"]
["South Wales",530195,"Orb Works 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",530196,"Panteg 132/11kV S Stn",5.7000000000000002E-2,null,260,null,1,"Y"]
["South Wales",530214,"Ringland Newport 33/11kV S Stn",6.8000000000000005E-2,null,98,null,3,"Y"]
["South Wales",530226,"St Arvans 33/11kV S Stn",1.1020000000000001,null,905,null,3,"Y"]
["South Wales",530252,"Usk 66/11kV S Stn",0.248,null,294,null,3,"Y"]
["South Wales",530294,"Newhouse 33/11kV S Stn",0.32,null,341,null,3,"Y"]
["South Wales",530316,"British Energy Newport South 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",530333,"Rogerstone 66/11kV S Stn",0.20399999999999999,null,157,null,3,"Y"]
["South Wales",530404,"Oak Grove Farm Solar Generation 33kV S Stn",0.43,null,309,"",3,"Y"]
["South Wales",530406,"Lower House P V Generation 66kV S Stn",0.23,null,500,"Y",3,"Y"]
["South Wales",530413,"Traston Road Stor Generation 33kV S Stn",0.17,null,500,"Y",3,"Y"]
["South Wales",530414,"Rhewl Farm Solar Park 33kV S Stn",0.29599999999999999,null,500,"Y",3,"Y"]
["South Wales",530415,"Manor Farm Solar Park 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",530900,"Newport West 132/11kV S Stn",9.1999999999999998E-2,null,672,null,1,"Y"]
["South Wales",530907,"Pontypool North 132/11kV S Stn",7.0999999999999994E-2,null,307,null,1,"Y"]
["South Wales",530914,"Simms Metals 132kV S Stn",0.17299999999999999,null,1000,"Y",1,"Y"]
["South Wales",530941,"Magor BSP 132/11kV S Stn",0.105,null,484,null,1,"Y"]
["South Wales",540039,"Upper Boat 132/11kV S Stn",0.2,"Y",2629,"",1,"Y"]
["South Wales",540094,"Caerphilly Primary 33/11kV S Stn",0.13300000000000001,null,500,"Y",3,"Y"]
["South Wales",540106,"Creigiau 33/11kV S Stn",0.78400000000000003,null,500,"Y",3,"Y"]
["South Wales",540120,"Energlyn Primary 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",540128,"Gas Yard 33/11kV S Stn",0.24199999999999999,null,500,"Y",3,"Y"]
["South Wales",540174,"Middle Fan 33/11kV S Stn",0.247,null,500,"Y",3,"Y"]
["South Wales",540234,"Trethomas 33/11kV S Stn",0.32200000000000001,null,500,"Y",3,"Y"]
["South Wales",540240,"Tonypandy 33/11kV S Stn",0.22,null,500,"Y",3,"Y"]
["South Wales",540241,"Mill St. Tonyrefail 33/11kV S Stn",0.7,"Y",384,"",3,"Y"]
["South Wales",540255,"Wattstown 33/11kV S Stn",0.35199999999999998,null,700,"",3,"Y"]
["South Wales",540263,"Ynysfeio 33/11kV S Stn",0.20399999999999999,null,500,"Y",3,"Y"]
["South Wales",540270,"Talbot Green 132/11kV S Stn",0.29399999999999998,null,1000,"Y",1,"Y"]
["South Wales",540295,"Taff Ely Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",540306,"Maerdy 33/11kV S Stn",0.378,null,500,"Y",3,"Y"]
["South Wales",540332,"Ferndale Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",540335,"Mynydd Portref Wind Farm 33kV S Stn",1.48,null,500,"Y",3,"Y"]
["South Wales",540338,"Maerdy Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",540412,"Tonypandy Stor 33kv Generation 33kV S Stn",3.87,null,500,"Y",3,"Y"]
["South Wales",540425,"St Peters Church Wind Farm 33kV S Stn",0.92300000000000004,null,500,"Y",3,"Y"]
["South Wales",540426,"Berthllwyd Solar Park Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",540903,"Nantgarw BSP 132/11kV S Stn",0.29299999999999998,null,1000,"Y",1,"Y"]
["South Wales",540910,"Energlyn BSP 132/11kV S Stn",0.13800000000000001,null,1000,"Y",1,"Y"]
["South Wales",540913,"Pontyclun 132/11kV S Stn",0.16200000000000001,null,1000,"Y",1,"Y"]
["South Wales",550011,"Crumlin 132/11kV S Stn",0.219,null,1000,"Y",1,"Y"]
["South Wales",550012,"Dowlais Grid 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
["South Wales",550013,"Ebbw Vale 132/11kV S Stn",0.159,null,1000,"Y",1,"Y"]
["South Wales",550018,"Hirwaun 132/33kV S Stn",0.21299999999999999,null,1000,"Y",3,"Y"]
["South Wales",550026,"Mountain Ash Grid 132/33kV S Stn",1.03,null,1000,"Y",3,"Y"]
["South Wales",550060,"Abertillery 33/11kV S Stn",0.16400000000000001,null,500,"Y",3,"Y"]
["South Wales",550061,"Abertysswg 33/11kV S Stn",0.1111,null,500,"Y",3,"Y"]
["South Wales",550090,"Brynmawr 33/11kV S Stn",0.10100000000000001,null,500,"Y",3,"Y"]
["South Wales",550111,"Cwmfelinfach 33/11kV S Stn",0.34399999999999997,null,500,"Y",3,"Y"]
["South Wales",550149,"Lady Windsor 33/11kV S Stn",0.53700000000000003,null,500,"Y",3,"Y"]
["South Wales",550179,"Mountain Ash 33/11kV S Stn",0.14099999999999999,null,500,"Y",3,"Y"]
["South Wales",550182,"Nantwen 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",550183,"Nelson 33/11kV S Stn",0.5,null,500,"Y",3,"Y"]
["South Wales",550202,"Pengam Grid 132/11kV S Stn",0.13100000000000001,null,1000,"Y",1,"Y"]
["South Wales",550203,"Pentrebach 33/11kV S Stn",0.15,null,500,"Y",3,"Y"]
["South Wales",550208,"Pontllanffraith 33/11kV S Stn",0.126,null,500,"Y",3,"Y"]
["South Wales",550244,"Tredegar 33/11kV S Stn",6.6000000000000003E-2,null,500,"Y",3,"Y"]
["South Wales",550267,"Aberdare 33/11kV S Stn",0.13,null,500,"Y",3,"Y"]
["South Wales",550287,"Swansea Road Merthyr 33/11kV S Stn",0.10299999999999999,null,500,"Y",3,"Y"]
["South Wales",550288,"Rassau West 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["South Wales",550313,"Aberaman Park 33kV S Stn",0.63700000000000001,null,500,"Y",3,"Y"]
["South Wales",550321,"Trecatti Generation 33kV S Stn",0.34,null,500,"Y",3,"Y"]
["South Wales",550343,"Hirwaun STOR Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",550354,"Dowlais STOR Generation West 33kV S Stn",0.52,null,500,"Y",3,"Y"]
["South Wales",550375,"Hendre Fawr Solar Farm 33/11kV S Stn",0.16,null,500,"Y",3,"Y"]
["South Wales",550376,"Mynydd Y Bwllfa Wind Farm 132kV S Stn",1.05,null,1000,"Y",1,"Y"]
["South Wales",550377,"Cwm Cae Singrug Solar Park 33kV S Stn",0.5,null,500,"Y",3,"Y"]
["South Wales",550378,"Hendai Solar Farm 33kV S Stn",0.39,null,500,"Y",3,"Y"]
["South Wales",550384,"Aberaman Industrial No.1 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",550389,"Cwmbargoed Coal Washery (Load) 33kV S Stn",0.30199999999999999,null,500,"Y",3,"Y"]
["South Wales",550390,"Hill Solar Farm 33kV S Stn",0.95,null,500,"Y",3,"Y"]
["South Wales",550400,"Pen Y Cymoedd Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",550402,"Hafod Y Dafal Solar Park 33kV S Stn",0.59799999999999998,null,500,"Y",3,"Y"]
["South Wales",550403,"Dowlais Stor Generation East 33kV S Stn",0.3347,null,500,"Y",3,"Y"]
["South Wales",550409,"Pen Rhiw Caradog Pv Generation 33kV S Stn",0.751,null,500,"Y",3,"Y"]
["South Wales",550416,"Bargoed Solar Park 33kV S Stn",0.44,null,500,"Y",3,"Y"]
["South Wales",550418,"Rassau Industrial Estate Stor Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",550422,"Waun Y Pound Gas Stor 33kV S Stn",1.31,null,500,"Y",3,"Y"]
["South Wales",550433,"Rhigos Road Gas Generation 33kV S Stn",1.573,null,500,"Y",3,"Y"]
["South Wales",550434,"Manmoel Solar Park 33kV S Stn",0.84,null,832,"",3,"Y"]
["South Wales",550436,"Crumlin STOR 33kV S Stn",0.84399999999999997,null,710,"",3,"Y"]
["South Wales",550437,"Pen Bryn Oer Windfarm 33kV S Stn",0.55400000000000005,null,680,"",3,"Y"]
["South Wales",550441,"Beaufort Power Stor 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",550442,"Brecon Power Stor 33kV S Stn",0.434,null,240,"",3,"Y"]
["South Wales",550901,"Merthyr East Primary 132/11kV S Stn",0.23599999999999999,null,1000,"Y",1,"Y"]
["South Wales",550906,"Rassau Supergrid 400/132kV S Stn",7.9000000000000001E-2,null,4870,"",1,"Y"]
["South Wales",560004,"Bridgend Grid 132/33kV S Stn",0.127,null,1000,"Y",3,"Y"]
["South Wales",560005,"Briton Ferry 132/33kV S Stn",5.8999999999999997E-2,null,1000,"Y",3,"Y"]
["South Wales",560015,"Grange 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",560024,"Llynfi 66/11kV S Stn",0.26500000000000001,null,500,"Y",3,"Y"]
["South Wales",560025,"Cefn Gwrgan 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",560030,"Pyle Grid 132/33/11kV S Stn",0.14299999999999999,null,2159,"",3,"Y"]
["South Wales",560047,"Margam Grid 132/66kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
["South Wales",560050,"Fords Bridgend 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["South Wales",560053,"Abercrave 33/11kV S Stn",0.92,null,500,"Y",3,"Y"]
["South Wales",560055,"Aberpergwm 33/11kV S Stn",0.30199999999999999,null,500,"Y",3,"Y"]
["South Wales",560075,"Boverton 33/11kV S Stn",0.32200000000000001,null,500,"Y",3,"Y"]
["South Wales",560079,"Bridgend Trading Estate 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",560093,"Caerau Road 66/11kV S Stn",0.34,null,500,"Y",3,"Y"]
["South Wales",560103,"Commercial St. Neath 33/11kV S Stn",0.22500000000000001,null,500,"Y",3,"Y"]
["South Wales",560105,"Cowbridge 33/11kV S Stn",0.21,null,500,"Y",3,"Y"]
["South Wales",560150,"Litchard 33/11kV S Stn",0.151,null,500,"Y",3,"Y"]
["South Wales",560158,"Llangewydd 33/11kV S Stn",0.22600000000000001,null,500,"Y",3,"Y"]
["South Wales",560191,"Nottage 33/11kV S Stn",0.23599999999999999,null,500,"Y",3,"Y"]
["South Wales",560193,"Ogmore Vale 66/11kV S Stn",0.30099999999999999,null,500,"Y",3,"Y"]
["South Wales",560220,"Schwyll 33/11kV S Stn",0.61599999999999999,null,500,"Y",3,"Y"]
["South Wales",560253,"Victoria Road 33/11kV S Stn",0.12,null,500,"Y",3,"Y"]
["South Wales",560256,"Wern 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",560265,"Ynys Street 33/11kV S Stn",0.106,null,500,"Y",3,"Y"]
["South Wales",560290,"Boc Margam Grid 132kV S Stn",0.115,null,1000,"Y",1,"Y"]
["South Wales",560292,"Waterton Industrial Primary 132/11kV S Stn",0.16,null,1000,"Y",1,"Y"]
["South Wales",560311,"South Cornelly 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",560320,"Ffynnon Oer Wind Farm 66kV S Stn",2.2170000000000001,null,500,"Y",3,"Y"]
["South Wales",560322,"Llandarcy 33/11kV S Stn",0.28100000000000003,null,500,"Y",3,"Y"]
["South Wales",560324,"Margam BOC Biomass 33kV S Stn",0.27,null,500,"Y",3,"Y"]
["South Wales",560331,"Maesgwyne Wind Farm 132kV S Stn",0.14299999999999999,null,1000,"Y",1,"Y"]
["South Wales",560336,"Baglan Bay PV Generation 33kV S Stn",0.44,null,500,"Y",3,"Y"]
["South Wales",560342,"Pant Y Wal Wind Farm 66kV S Stn",0.86199999999999999,null,500,"Y",3,"Y"]
["South Wales",560347,"Briton Ferry STOR Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",560358,"Llandarcy STOR Generation 33kV S Stn",0.63,null,500,"Y",3,"Y"]
["South Wales",560359,"Garn Farm Solar Park 33kV S Stn",0.34,null,500,"Y",3,"Y"]
["South Wales",560361,"Treguff Farm PV Generation 33kV S Stn",0.35899999999999999,null,500,"Y",3,"Y"]
["South Wales",560363,"Loughor Solar Park 33kV S Stn",0.14499999999999999,null,500,"Y",3,"Y"]
["South Wales",560372,"Margam Biomass Generation 132kV S Stn",0.11700000000000001,null,822,"",1,"Y"]
["South Wales",560379,"Court Coleman PV Generation 33/11kV S Stn",0.28000000000000003,null,500,"Y",3,"Y"]
["South Wales",560382,"Cenin Energy Park 33kV S Stn",1.5740000000000001,null,500,"Y",3,"Y"]
["South Wales",560397,"Pant Y Moch Solar Farm 33kV S Stn",0.81,null,500,"Y",3,"Y"]
["South Wales",560405,"Stormy Down Pv Generation 33kV S Stn",1,null,1331,"",3,"Y"]
["South Wales",560408,"Rosedew Solar  Farm 33kV S Stn",0.34899999999999998,null,500,"Y",3,"Y"]
["South Wales",560411,"Maesgwyn Wind Farm 33kV S Stn",0.47,null,500,"Y",3,"Y"]
["South Wales",560417,"Mynydd Brombil Windfarm 33kV S Stn",1.5309999999999999,null,500,"Y",3,"Y"]
["South Wales",560419,"Newton Down Wind Farm 33kV S Stn",1.6759999999999999,null,1240,"",3,"Y"]
["South Wales",560420,"Llynfi Afan Wind Farm 66kV S Stn",0.78,null,325,"",3,"Y"]
["South Wales",560421,"Mynydd Yr Aber Wind Farm 66kV S Stn",0.86199999999999999,null,500,"Y",3,"Y"]
["South Wales",560440,"Afan Way Stor Generation 33kV S Stn",0.11700000000000001,null,500,"Y",3,"Y"]
["South Wales",560912,"Pencoed BSP 132/11kV S Stn",0.189,null,1000,"Y",1,"Y"]
["South Wales",580010,"Carmarthen 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
["South Wales",580031,"Rhos 132/33/11kV S Stn",1.21,null,1000,"Y",3,"Y"]
["South Wales",580072,"Blaenporth 33/11kV S Stn",1.18,null,500,"Y",3,"Y"]
["South Wales",580078,"Bridell 33/11kV S Stn",0.24299999999999999,null,500,"Y",3,"Y"]
["South Wales",580201,"Pendine 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",580228,"St Clears 33/11kV S Stn",1.1970000000000001,null,1161,"",3,"Y"]
["South Wales",580247,"Trevaughan 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",580262,"Whitland 33/11kV S Stn",0.75,null,500,"Y",3,"Y"]
["South Wales",580272,"Cardigan 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",580276,"Newcastle Emlyn South 33/11kV S Stn",0.66900000000000004,null,500,"Y",3,"Y"]
["South Wales",580296,"Cwmffrwd 33/11kV S Stn",0.65,null,500,"Y",3,"Y"]
["South Wales",580308,"Llanfyrnach 33/11kV S Stn",3.843,null,500,"Y",3,"Y"]
["South Wales",580314,"Parc Cynog Wind Farm 33kV S Stn",0.37,null,500,"Y",3,"Y"]
["South Wales",580315,"Blaen Bowi Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",580328,"Blaengwen Wind Farm 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["South Wales",580337,"Whitland Solar Park 33kV S Stn",0.152,null,500,"Y",3,"Y"]
["South Wales",580380,"Llwyndu Solar Farm 33kV S Stn",0.54,null,500,"Y",3,"Y"]
["South Wales",580383,"Crugmore Solar Park 33kV S Stn",0.23,null,500,"Y",3,"Y"]
["South Wales",580394,"Red Court Solar Farm 33kV S Stn",0.16900000000000001,null,500,"Y",3,"Y"]
["South Wales",580432,"Bryncyrnau Isaf Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",590020,"Lampeter Primary 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
["South Wales",590021,"Llanarth Primary 132/33kV S Stn",1.1419999999999999,null,1000,"Y",3,"Y"]
["South Wales",590052,"Aberaeron 33/11kV S Stn",0.59,null,500,"Y",3,"Y"]
["South Wales",590151,"Llandeilo 33/11kV S Stn",0.85799999999999998,null,500,"Y",3,"Y"]
["South Wales",590153,"Llandovery 33/11kV S Stn",0.32300000000000001,null,500,"Y",3,"Y"]
["South Wales",590156,"Llanfihangel Ystrad 33/11kV S Stn",1.0109999999999999,null,500,"Y",3,"Y"]
["South Wales",590157,"Llangadog 33/11kV S Stn",0.74,null,500,"Y",3,"Y"]
["South Wales",590161,"Llanllwni 33/11kV S Stn",3.76,null,500,"Y",3,"Y"]
["South Wales",590170,"Manoravon Pumping Station 33kV S Stn",0.72799999999999998,null,1421,"",3,"Y"]
["South Wales",590180,"Nantgaredig 33/11kV S Stn",4.0490000000000004,null,500,"Y",3,"Y"]
["South Wales",590206,"Pont Ar Annell 33/11kV S Stn",1.28,null,500,"Y",3,"Y"]
["South Wales",590246,"Argoed Tregaron 33/11kV S Stn",3.3,null,500,"Y",3,"Y"]
["South Wales",590282,"W G W B Towy Intake 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",590298,"Duffryn Brodyn 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",590304,"Llyn Brianne 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",590424,"Nathenfoel Solar Park 33kV S Stn",0.39500000000000002,null,500,"Y",3,"Y"]
["South Wales",600003,"Texaco Grid 132/11kV S Stn",0.27100000000000002,null,1000,"Y",1,"Y"]
["South Wales",600014,"Golden Hill 132/33kV S Stn",0.24299999999999999,null,1000,"Y",3,"Y"]
["South Wales",600016,"Haverfordwest Grid 132/33kV S Stn",0.45900000000000002,null,1000,"Y",3,"Y"]
["South Wales",600017,"Haverfordwest 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",600029,"Pembroke Power Station 400/132kV S Stn",0.2,"Y",2300,"",1,"Y"]
["South Wales",600040,"Waterston 132/11kV S Stn",0.42,null,1000,"Y",1,"Y"]
["South Wales",600042,"Milford Haven Grid 132/33kV S Stn",1.07,null,1000,"Y",3,"Y"]
["South Wales",600043,"Robeston 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["South Wales",600076,"Brawdy 33/11kV S Stn",2.0630000000000002,null,500,"Y",3,"Y"]
["South Wales",600085,"Broadfield 33/11kV S Stn",0.23799999999999999,null,500,"Y",3,"Y"]
["South Wales",600124,"Fishguard 33/11kV S Stn",1.895,null,500,"Y",3,"Y"]
["South Wales",600173,"Merlins Bridge 33/11kV S Stn",0.2,null,500,"Y",3,"Y"]
["South Wales",600184,"Nevern 33/11kV S Stn",2.6,null,500,"Y",3,"Y"]
["South Wales",600188,"Neyland 33/11kV S Stn",0.66100000000000003,null,500,"Y",3,"Y"]
["South Wales",600200,"Penblewin 33/11kV S Stn",0.80200000000000005,null,500,"Y",3,"Y"]
["South Wales",600229,"St Florence 33/11kV S Stn",2.0499999999999998,null,500,"Y",3,"Y"]
["South Wales",600231,"St Twynnells 33/11kV S Stn",1.4179999999999999,null,500,"Y",3,"Y"]
["South Wales",600232,"Steynton 33/11kV S Stn",0.19,null,500,"Y",3,"Y"]
["South Wales",600271,"St Davids 33/11kV S Stn",2.3860000000000001,null,500,"Y",3,"Y"]
["South Wales",600273,"Tenby 33/11kV S Stn",0.248,null,500,"Y",3,"Y"]
["South Wales",600279,"Milford Haven 33/11kV S Stn",0.22,null,500,"Y",3,"Y"]
["South Wales",600319,"South Hook 132/33kV S Stn",0.15,null,1000,"Y",3,"Y"]
["South Wales",600323,"Withyhedges 33kV S Stn",0.27,null,500,"Y",3,"Y"]
["South Wales",600349,"Wear Point Wind Farm 33kV S Stn",0.8,null,500,"Y",3,"Y"]
["South Wales",600350,"Jordanston Farm PV Generation 33kV S Stn",0.5,null,500,"Y",3,"Y"]
["South Wales",600351,"West Farm PV Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",600352,"Rudbaxton PV Farm 33kV S Stn",0.20200000000000001,null,500,"Y",3,"Y"]
["South Wales",600353,"Little Neath Solar Farm 33kV S Stn",0.59,null,500,"Y",3,"Y"]
["South Wales",600355,"Hoplass Solar Farm PV Generation 33kV S Stn",0.32,null,500,"Y",3,"Y"]
["South Wales",600357,"Liddlestone Ridge PV Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",600364,"Tiers Cross Solar Park 132kV S Stn",0.26,null,1000,"Y",1,"Y"]
["South Wales",600367,"Fenton Farm PV Generation 33kV S Stn",0.16,null,500,"Y",3,"Y"]
["South Wales",600370,"Yerbeston Solar Farm 33kV S Stn",0.252,null,500,"Y",3,"Y"]
["South Wales",600385,"Yerbeston Chapel Hill Solar Farm 33kV S Stn",0.39,null,500,"Y",3,"Y"]
["South Wales",600387,"Haverfordwest Solar Park 33kV S Stn",0.28000000000000003,null,83,"",3,"Y"]
["South Wales",600391,"Little Neath Solar Farm 33kV S Stn",0.44,null,500,"Y",3,"Y"]
["South Wales",600393,"Oak Cottage Solar Farm 33kV S Stn",0.27,null,500,"Y",3,"Y"]
["South Wales",600431,"North Tenement Solar Park 33kV S Stn",0.28399999999999997,null,616,"",3,"Y"]
["South Wales",600448,"Rhoscrowther 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["South Wales",610077,"Brecon 66/11kV S Stn",0.13700000000000001,null,210,null,3,"Y"]
["South Wales",610092,"Builth Wells 66/11kV S Stn",1.39,null,1215,null,3,"Y"]
["South Wales",610107,"Crickhowell 66/11kV S Stn",0.497,null,561,null,3,"Y"]
["South Wales",610133,"Glasbury 66/11kV S Stn",1.099,null,1044,null,3,"Y"]
["South Wales",610154,"Llandrindod Wells 66/11kV S Stn",0.191,null,144,null,3,"Y"]
["South Wales",610277,"Rhayader 66/11kV S Stn",0.439,null,285,null,3,"Y"]
["South Wales",610297,"Bryn Titli Wind Farm 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["South Wales",610443,"Bryn Blaen Wind Farm 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",670001,"Iron Acton 275/132kV S Stn",0.09,null,1503,"",1,"Y"]
["West Midlands",670002,"Bishops Wood 275/132kV S Stn",0.17,null,3145,"",1,"Y"]
["West Midlands",670003,"Feckenham 275/66/11kV S Stn",7.2999999999999995E-2,null,1030,"",3,"Y"]
["West Midlands",670004,"Bustleholm 275/132/11kV S Stn",0.1,null,990,"",1,"Y"]
["West Midlands",670005,"Oldbury 132/11kV S Stn",7.5999999999999998E-2,null,965,"",1,"Y"]
["West Midlands",670006,"Willenhall 275/132/33/25/11kV S Stn",7.0000000000000007E-2,null,211,"",3,"Y"]
["West Midlands",670007,"Nechells East 275/132kV S Stn",7.0000000000000007E-2,null,1540,"",1,"Y"]
["West Midlands",670008,"Port Ham 400/132kV S Stn",0.63,null,561,"",1,"Y"]
["West Midlands",670009,"Penn 400/275/132kV S Stn",9.7000000000000003E-2,null,1242,"",1,"Y"]
["West Midlands",670010,"Ocker Hill C 275/132kV S Stn",7.0000000000000007E-2,null,1266,"",1,"Y"]
["West Midlands",670011,"Kitwell 275/132kV S Stn",0.126,null,2528,"",1,"Y"]
["West Midlands",670012,"Castle Meads 132/33kV S Stn",7.3999999999999996E-2,null,1037,"",3,"Y"]
["West Midlands",670013,"Hereford 132/66kV S Stn",0.129,null,647,"",3,"Y"]
["West Midlands",670014,"Worcester 132/11kV S Stn",9.5000000000000001E-2,null,486,"",1,"Y"]
["West Midlands",670015,"Ryeford 132/33/11kV S Stn",5.6000000000000001E-2,null,209,"",3,"Y"]
["West Midlands",670016,"Walsall 132/33kV S Stn",0.13600000000000001,null,352,"",3,"Y"]
["West Midlands",670017,"Bushbury A 132kV S Stn",8.8999999999999996E-2,null,1664,"",1,"Y"]
["West Midlands",670019,"Timberdine 132/11kV S Stn",0.08,null,515,"",1,"Y"]
["West Midlands",670020,"Tividale 132/11kV S Stn",0.11799999999999999,null,900,"",1,"Y"]
["West Midlands",670021,"Upton Warren 132/66/11kV S Stn",0.104,null,374,"",3,"Y"]
["West Midlands",670022,"Warndon 132/11kV S Stn",4.3999999999999997E-2,null,290,"",1,"Y"]
["West Midlands",670023,"Wednesfield 132/11kV S Stn",0.14699999999999999,null,1102,"",1,"Y"]
["West Midlands",670024,"Wolverhampton 132/33/11kV S Stn",0.114,null,376,"",3,"Y"]
["West Midlands",670025,"Wolverhampton West 132/33/11kV S Stn",0.13300000000000001,null,1157,"",3,"Y"]
["West Midlands",670026,"Woodside 132/11kV S Stn",7.0999999999999994E-2,null,333,"",1,"Y"]
["West Midlands",670027,"Summer Lane 132/11kV S Stn",0.08,null,240,"",1,"Y"]
["West Midlands",670028,"Hall Green 132/11kV S Stn",7.5999999999999998E-2,null,516,"",1,"Y"]
["West Midlands",670029,"Dunlop 132kV S Stn",0.23799999999999999,null,2222,"",1,"Y"]
["West Midlands",670030,"Kitts Green 132/11kV S Stn",0.125,null,635,"",1,"Y"]
["West Midlands",670031,"Lydney Local 132kV S Stn",0.21,null,712,"",1,"Y"]
["West Midlands",670032,"Castle Bromwich 132/11kV S Stn",8.6999999999999994E-2,null,383,"",1,"Y"]
["West Midlands",670033,"Hams Hall 132/33kV S Stn",0.105,null,1775,"",3,"Y"]
["West Midlands",670034,"Erdington 132kV S Stn",0.121,null,581,"",1,"Y"]
["West Midlands",670035,"University Of Birmingham 132/11kV S Stn",2.9000000000000001E-2,null,275,"",1,"Y"]
["West Midlands",670037,"Bushbury B-C 132/33/11kV S Stn",0.12,null,2077,"",3,"Y"]
["West Midlands",670038,"Winson Green 132/11kV S Stn",0.05,null,279,"",1,"Y"]
["West Midlands",670039,"Selly Oak 132kV S Stn",8.5999999999999993E-2,null,791,"",1,"Y"]
["West Midlands",670040,"Ladywood 132/11kV S Stn",0.17299999999999999,null,1358,"",1,"Y"]
["West Midlands",670041,"Bordesley 132/11kV S Stn",9.7000000000000003E-2,null,286,"",1,"Y"]
["West Midlands",670042,"Chipping Sodbury 132/33/11kV S Stn",0.28000000000000003,null,974,"",3,"Y"]
["West Midlands",670043,"Hams Hall South 132/11kV S Stn",0.08,null,1115,"",1,"Y"]
["West Midlands",670045,"Banbury 132/11kV S Stn",6.6000000000000003E-2,null,211,"",1,"Y"]
["West Midlands",670046,"Bentley 132/11kV S Stn",8.8999999999999996E-2,null,694,"",1,"Y"]
["West Midlands",670047,"Birchfield Lane 132/11kV S Stn",5.0999999999999997E-2,null,418,"",1,"Y"]
["West Midlands",670048,"Black Lake 132/11kV S Stn",7.1999999999999995E-2,null,532,"",1,"Y"]
["West Midlands",670049,"Longbridge 132/11kV S Stn",0.04,null,449,"",1,"Y"]
["West Midlands",670050,"Bournville 132/11kV S Stn",6.8000000000000005E-2,null,474,"",1,"Y"]
["West Midlands",670051,"Chad Valley 132/11kV S Stn",0.08,null,336,"",1,"Y"]
["West Midlands",670052,"Cheapside 132/11kV S Stn",7.3999999999999996E-2,null,610,"",1,"Y"]
["West Midlands",670053,"Cheltenham 132/66/11kV S Stn",5.1999999999999998E-2,null,201,"",3,"Y"]
["West Midlands",670054,"Chester Street 132/11kV S Stn",0.38400000000000001,null,614,"",1,"Y"]
["West Midlands",670055,"Copt Heath 132/11kV S Stn",0.115,null,566,"",1,"Y"]
["West Midlands",670056,"Coseley 132/11kV S Stn",0.10100000000000001,null,760,"",1,"Y"]
["West Midlands",670057,"Dudley 132/11kV S Stn",5.3999999999999999E-2,null,437,"",1,"Y"]
["West Midlands",670058,"Eastern Avenue 132/11kV S Stn",3.9E-2,null,416,"",1,"Y"]
["West Midlands",670059,"Elmdon 132/11kV S Stn",0.06,null,424,"",1,"Y"]
["West Midlands",670060,"Halesowen 132/11kV S Stn",8.5000000000000006E-2,null,909,"",1,"Y"]
["West Midlands",670061,"Highters Heath 132/11kV S Stn",6.5000000000000002E-2,null,469,"",1,"Y"]
["West Midlands",670062,"Hinksford 132/33/11kV S Stn",0.12,null,1079,"",3,"Y"]
["West Midlands",670063,"Kidderminster 132/33/11kV S Stn",0.24,null,1546,"",3,"Y"]
["West Midlands",670064,"Ludlow 132/66/33/11kV S Stn",0.15,null,599,"",3,"Y"]
["West Midlands",670065,"Lye 132/11kV S Stn",4.2999999999999997E-2,null,430,"",1,"Y"]
["West Midlands",670066,"Marle Hill 132/66/11kV S Stn",3.5000000000000003E-2,null,160,"",3,"Y"]
["West Midlands",670067,"Malvern 132/11kV S Stn",4.8000000000000001E-2,null,319,"",1,"Y"]
["West Midlands",670068,"Montpellier 132/11kV S Stn",4.3999999999999997E-2,null,216,"",1,"Y"]
["West Midlands",670069,"Nechells West 132/25/11kV S Stn",0.11,null,583,"",1,"Y"]
["West Midlands",670070,"Ocker Hill B 132/33/11kV S Stn",5.1999999999999998E-2,null,854,"",3,"Y"]
["West Midlands",670071,"Perry Barr 132/11kV S Stn",0.112,null,445,"",1,"Y"]
["West Midlands",670072,"Rednal 132/11kV S Stn",6.4000000000000001E-2,null,620,"",1,"Y"]
["West Midlands",670073,"Rushall 132/11kV S Stn",0.16,null,498,"",1,"Y"]
["West Midlands",670074,"Selly Oak 132/11kV S Stn",8.5999999999999993E-2,null,791,"",1,"Y"]
["West Midlands",670075,"Shirley 132/11kV S Stn",6.5000000000000002E-2,null,449,"",1,"Y"]
["West Midlands",670076,"Smethwick 132/11kV S Stn",0.153,null,1121,"",1,"Y"]
["West Midlands",670077,"Solihull 132/11kV S Stn",0.09,null,252,"",1,"Y"]
["West Midlands",670078,"Sparkbrook 132/11kV S Stn",0.04,null,274,"",1,"Y"]
["West Midlands",670079,"Stourport 132/66/33/11kV S Stn",0.112,null,618,"",3,"Y"]
["West Midlands",670080,"Sutton Coldfield 132/11kV S Stn",9.6000000000000002E-2,null,703,"",1,"Y"]
["West Midlands",670081,"Tewkesbury 132/11kV S Stn",5.7000000000000002E-2,null,337,"",1,"Y"]
["West Midlands",670083,"Tewkesbury 66/11kV S Stn",6.4000000000000001E-2,null,532,"",3,"Y"]
["West Midlands",670084,"Abson 33kV S Stn",0.25900000000000001,null,328,"",3,"Y"]
["West Midlands",670085,"Moreton 66/11kV S Stn",0.114,null,191,"",3,"Y"]
["West Midlands",670086,"Bishops Cleeve 66/11kV S Stn",0.115,null,163,"",3,"Y"]
["West Midlands",670087,"Bloxham 66/11kV S Stn",0.31,null,504,"",3,"Y"]
["West Midlands",670088,"Alderton 66/11kV S Stn",0.13,null,179,"",3,"Y"]
["West Midlands",670089,"Broadway 66/11kV S Stn",0.37,null,701,"",3,"Y"]
["West Midlands",670090,"Epwell 66/11kV S Stn",0.34,null,308,"",3,"Y"]
["West Midlands",670091,"Stow 66/11kV S Stn",1.66,null,2296,"",3,"Y"]
["West Midlands",670092,"Wormington 66/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",670093,"Shipston 66/11kV S Stn",0.14799999999999999,null,202,"",3,"Y"]
["West Midlands",670094,"Long Marston 66/11kV S Stn",0.10100000000000001,null,128,"",3,"Y"]
["West Midlands",670095,"Pershore 66/11kV S Stn",0.17100000000000001,null,324,"",3,"Y"]
["West Midlands",670096,"Hereford North 66/11kV S Stn",9.6000000000000002E-2,null,141,"",3,"Y"]
["West Midlands",670097,"Evesham 66/11kV S Stn",0.14499999999999999,null,399,"",3,"Y"]
["West Midlands",670098,"Bevington 66/11kV S Stn",0.154,null,248,"",3,"Y"]
["West Midlands",670099,"Peterchurch 66/11kV S Stn",0.22,null,303,"",3,"Y"]
["West Midlands",670100,"Leominster 66/11kV S Stn",0.253,null,441,"",3,"Y"]
["West Midlands",670101,"Stratford 66/11kV S Stn",0.12,null,304,"",3,"Y"]
["West Midlands",670102,"Brotheridge Green 66/11kV S Stn",0.41,null,614,"",3,"Y"]
["West Midlands",670103,"Hereford South 66/11kV S Stn",0.16600000000000001,null,266,"",3,"Y"]
["West Midlands",670104,"Strensham 66/11kV S Stn",0.20200000000000001,null,352,"",3,"Y"]
["West Midlands",670105,"Great Alne 66/11kV S Stn",0.159,null,348,"",3,"Y"]
["West Midlands",670106,"Pontrilas 66/11kV S Stn",0.2,null,380,"",3,"Y"]
["West Midlands",670107,"Arley 33kV S Stn",1.79,null,1545,"",3,"Y"]
["West Midlands",670108,"Bromyard 66/11kV S Stn",0.223,null,386,"",3,"Y"]
["West Midlands",670109,"Madley 66/11kV S Stn",0.28999999999999998,null,592,"",3,"Y"]
["West Midlands",670110,"Woofferton 66/11kV S Stn",0.14000000000000001,null,211,"",3,"Y"]
["West Midlands",670111,"Presteigne 66/11kV S Stn",0.44,null,722,"",3,"Y"]
["West Midlands",670112,"Bodenham 66/11kV S Stn",0.46,null,1334,"",3,"Y"]
["West Midlands",670113,"St Weonards 66/11kV S Stn",0.38400000000000001,null,472,"",3,"Y"]
["West Midlands",670114,"Kington 66/11kV S Stn",0.38500000000000001,null,454,"",3,"Y"]
["West Midlands",670115,"Droitwich 66/11kV S Stn",9.8000000000000004E-2,null,141,"",3,"Y"]
["West Midlands",670116,"Kenswick 66/11kV S Stn",0.48699999999999999,null,360,"",3,"Y"]
["West Midlands",670117,"Lower Chadnor 66/11kV S Stn",0.35499999999999998,null,383,"",3,"Y"]
["West Midlands",670118,"Redditch South 66/11kV S Stn",7.3999999999999996E-2,null,221,"",3,"Y"]
["West Midlands",670119,"Redditch North 66/11kV S Stn",0.122,null,232,"",3,"Y"]
["West Midlands",670120,"Ipsley 66/11kV S Stn",6.8000000000000005E-2,null,146,"",3,"Y"]
["West Midlands",670121,"Knighton 66/11kV S Stn",0.97299999999999998,null,973,"",3,"Y"]
["West Midlands",670122,"Albrighton 33/11kV S Stn",0.16,null,200,"",3,"Y"]
["West Midlands",670124,"Four Ashes 33/11kV S Stn",0.189,null,230,"",3,"Y"]
["West Midlands",670125,"Aldridge 33/6.6kV S Stn",6.2E-2,null,133,"",3,"Y"]
["West Midlands",670126,"Ross 66/11kV S Stn",0.1,null,139,"",3,"Y"]
["West Midlands",670128,"Kingstanding 132/11kV S Stn",0.23,null,265,"",1,"Y"]
["West Midlands",670129,"Ledbury 66/11kV S Stn",9.6000000000000002E-2,null,294,"",3,"Y"]
["West Midlands",670131,"Chelmsley Wood 33/11kV S Stn",3.6999999999999998E-2,null,37,"",3,"Y"]
["West Midlands",670133,"Newent 66/11kV S Stn",0.3,null,851,"",3,"Y"]
["West Midlands",670136,"Erdington 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["West Midlands",670137,"Boughton Rd 132/11kV S Stn",4.3999999999999997E-2,null,498,"",1,"Y"]
["West Midlands",670138,"Bartley Green 132/11kV S Stn",9.2999999999999999E-2,null,1038,"",1,"Y"]
["West Midlands",670139,"Bustleholm 132/11kV S Stn",0.1,null,990,"",1,"Y"]
["West Midlands",670140,"Chelmsley Wood 132/11kV S Stn",2.9000000000000001E-2,null,609,"",1,"Y"]
["West Midlands",670141,"Four Ashes E F W 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",670142,"Pattingham 33/11kV S Stn",0.12,null,205,"",3,"Y"]
["West Midlands",670143,"Dymock 66/11kV S Stn",0.314,null,891,"",3,"Y"]
["West Midlands",670148,"Barton Abrasives 33/11kV S Stn",0.151,null,831,"",3,"Y"]
["West Midlands",670150,"Wolverhampton Waste Services 33kv S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",670151,"Hereford Central 66/11kv S Stn",0.156,null,279,"",3,"Y"]
["West Midlands",670152,"Wickhamford 66kv S Stn",0.124,null,214,"",3,"Y"]
["West Midlands",670153,"Garreg Lwyd Wind Farm 66kV S Stn",2.2200000000000002,null,2743,"",3,"Y"]
["West Midlands",670154,"Oldbury B 132/33/11kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
["West Midlands",670161,"Air Liquide 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["West Midlands",670170,"Troughton Farm 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["West Midlands",670200,"Hockley 132/11kv S Stn",0.08,null,240,"",1,"Y"]
["West Midlands",675348,"Cambridge Arms 132kV S Stn",7.1999999999999995E-2,null,614,"",1,"Y"]
["West Midlands",680000,"Ironbridge 400/132kV S Stn",0.06,null,1245,"",1,"Y"]
["East Midlands",680001,"Staythorpe C 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
["East Midlands",680002,"Ratcliffe 400/132kV S Stn",6.4399999999999999E-2,null,1269,"",1,"Y"]
["West Midlands",680004,"Shrewsbury 400/132/33kV S Stn",0.11700000000000001,null,1951,"",3,"Y"]
["East Midlands",680005,"Drakelow 275/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
["East Midlands",680006,"Willington 400/275/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
["East Midlands",680007,"Chesterfield 275/132/33kV S Stn",5.6000000000000001E-2,null,1070,"",3,"Y"]
["West Midlands",680008,"Rugeley 400/132kV S Stn",7.4999999999999997E-2,null,983,"",1,"Y"]
["East Midlands",680009,"Burton South 132/33kV S Stn",0.1,null,2006,"",3,"Y"]
["East Midlands",680010,"Pinxton 132kV S Stn",0.13400000000000001,null,601,"",1,"Y"]
["East Midlands",680011,"Annesley 132/33kV S Stn",8.2000000000000003E-2,null,370,"",3,"Y"]
["East Midlands",680012,"Clipstone 132/33kV S Stn",0.18,null,477,"",3,"Y"]
["East Midlands",680013,"Checkerhouse 132/33kV S Stn",0.21,null,685,"",3,"Y"]
["East Midlands",680014,"Willoughby 132/33kV S Stn",7.9000000000000001E-2,null,329,"",3,"Y"]
["East Midlands",680015,"Nottingham East 132/33kV S Stn",3.2000000000000001E-2,null,275,"",3,"Y"]
["East Midlands",680016,"Whitwell 132/33kV S Stn",0.42699999999999999,null,1320,"",3,"Y"]
["East Midlands",680017,"Worksop 132/33kV S Stn",0.14399999999999999,null,586,"",3,"Y"]
["East Midlands",680018,"Mansfield 132/33kV S Stn",0.1,null,383,"",3,"Y"]
["East Midlands",680019,"Toton 132/33kV S Stn",9.6000000000000002E-2,null,567,"",3,"Y"]
["East Midlands",680020,"Staythorpe B 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["East Midlands",680021,"Retford 132/25kV S Stn",0.253,null,1204,"",1,"Y"]
["East Midlands",680022,"Nottingham North 132/33/11kV S Stn",1.7999999999999999E-2,null,160,"",3,"Y"]
["East Midlands",680023,"Nottingham 132/33kV S Stn",7.6999999999999999E-2,null,601,"",3,"Y"]
["West Midlands",680024,"Ketley 132/33/11kV S Stn",0.09,null,720,"",3,"Y"]
["West Midlands",680025,"Ironbridge 132/33kV S Stn",0.04,null,91,"",3,"Y"]
["West Midlands",680026,"Meaford C 132/33/11kV S Stn",0.11,null,1013,"",3,"Y"]
["West Midlands",680027,"Barlaston 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["East Midlands",680028,"Buxton 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",680029,"Derby South 132/33kV S Stn",0.05,null,481,"",3,"Y"]
["East Midlands",680030,"Spondon A 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["East Midlands",680031,"Spondon 'B' 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
["East Midlands",680032,"Chesterfield 33kV S Stn",5.6000000000000001E-2,null,1070,"",3,"Y"]
["East Midlands",680033,"Burton 132/33/11kV S Stn",1.9E-2,null,141,"",3,"Y"]
["East Midlands",680034,"Burnaston 132/11kV S Stn",9.0999999999999998E-2,null,1237,"",1,"Y"]
["East Midlands",680035,"Gresley 132/33kV S Stn",0.11700000000000001,null,671,"",3,"Y"]
["East Midlands",680036,"Heanor 132/33kV S Stn",9.5000000000000001E-2,null,522,"",3,"Y"]
["East Midlands",680037,"Alfreton 132/33kV S Stn",0.193,null,752,"",3,"Y"]
["East Midlands",680038,"Goitside 132/33kV S Stn",9.1999999999999998E-2,null,88,"",3,"Y"]
["East Midlands",680039,"Staveley 132/33kV S Stn",4.8599999999999997E-2,null,372,"",3,"Y"]
["East Midlands",680040,"Winster 132/33kV S Stn",0.2,"Y",565,"",3,"Y"]
["East Midlands",680041,"Derby 132/33/11kV S Stn",8.4000000000000005E-2,null,375,"",3,"Y"]
["East Midlands",680042,"Stanton 132/33kV S Stn",7.3200000000000001E-2,null,457,"",3,"Y"]
["West Midlands",680043,"Uttoxeter 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
["East Midlands",680043,"Uttoxeter 132/33kV S Stn",0.156,null,569,"",3,"Y"]
["West Midlands",680044,"Kidsgrove 132/25kV S Stn",9.5000000000000001E-2,null,826,"",1,"Y"]
["West Midlands",680045,"Newcastle 33/11kV S Stn",5.8000000000000003E-2,null,681,"",3,"Y"]
["West Midlands",680046,"Whitfield 132kV S Stn",0.14499999999999999,null,1767,"",1,"Y"]
["West Midlands",680048,"Forsbrook 132/33kV S Stn",0.82,null,6239,"",3,"Y"]
["West Midlands",680049,"Stafford South 132/11kV S Stn",4.1000000000000002E-2,null,178,"",1,"Y"]
["West Midlands",680050,"Whitfield 132/33/11kV S Stn",0.14000000000000001,null,1249,"",3,"Y"]
["West Midlands",680051,"Rugeley 132kV S Stn",7.4999999999999997E-2,null,983,"",1,"Y"]
["West Midlands",680052,"Boothen 132/33/11kV S Stn",7.3999999999999996E-2,null,681,"",3,"Y"]
["West Midlands",680053,"Burntwood 132/11kV S Stn",0.115,null,602,"",1,"Y"]
["West Midlands",680054,"Burslem 132/33/11kV S Stn",8.5000000000000006E-2,null,280,"",3,"Y"]
["West Midlands",680055,"Cannock 132/11kV S Stn",4.2000000000000003E-2,null,240,"",1,"Y"]
["West Midlands",680056,"Lichfield 132/11kV S Stn",9.8000000000000004E-2,null,470,"",1,"Y"]
["West Midlands",680057,"Newcastle 132/11kV S Stn",0.11,null,722,"",1,"Y"]
["West Midlands",680058,"Stafford 132/25/11kV S Stn",5.7000000000000002E-2,null,304,"",1,"Y"]
["West Midlands",680059,"Stagefields 132/33/11kV S Stn",6.3E-2,null,632,"",3,"Y"]
["West Midlands",680060,"Hortonwood 132/11kV S Stn",0.111,null,876,"",1,"Y"]
["West Midlands",680061,"Rugeley Town 132/11kV S Stn",0.21,null,507,"",1,"Y"]
["West Midlands",680062,"Stafford South 132/11kV S Stn",0.04,null,70,"",1,"Y"]
["West Midlands",680065,"Burslem 33/11/6.6kV S Stn",8.5000000000000006E-2,null,280,"",3,"Y"]
["West Midlands",680066,"Bushbury D 132kV S Stn",8.8999999999999996E-2,null,1664,"",1,"Y"]
["West Midlands",680067,"Cellarhead 400/132kV S Stn",0.105,null,2405,"",1,"Y"]
["East Midlands",680068,"Stoke Bardolph 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
["East Midlands",680069,"Loscoe 132kV S Stn",0.11,null,576,"",1,"Y"]
["East Midlands",690001,"Berkswell 275/132kV S Stn",0.2,"Y",350,"",1,"Y"]
["East Midlands",690002,"Coventry 275/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
["East Midlands",690003,"Bicker Fen 400/132kV S Stn",0.04,null,710,"",1,"Y"]
["East Midlands",690004,"Enderby 400/132kV S Stn",6.5000000000000002E-2,null,849,"",1,"Y"]
["East Midlands",690005,"Walpole 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
["East Midlands",690006,"Bradwell Abbey 132/33kV S Stn",9.4E-2,null,486,"",3,"Y"]
["East Midlands",690007,"Grendon 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
["East Midlands",690008,"Corby 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
["West Midlands",690009,"Tamworth Br 132/25kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["East Midlands",690010,"Harbury 132/33kV S Stn",0.06,null,281,"",3,"Y"]
["East Midlands",690011,"Tamworth Town 132/33/11kV S Stn",3.4000000000000002E-2,null,217,"",3,"Y"]
["East Midlands",690012,"Coventry North 132/33kV S Stn",7.2999999999999995E-2,null,752,"",3,"Y"]
["East Midlands",690013,"Coventry Central 132/33kV S Stn",9.2999999999999999E-2,null,331,"",3,"Y"]
["East Midlands",690014,"Coventry South 132/33kV S Stn",5.7000000000000002E-2,null,553,"",3,"Y"]
["East Midlands",690015,"Coventry West 132/33kV S Stn",0.12,null,1161,"",3,"Y"]
["East Midlands",690016,"Tamworth 132/33kV S Stn",4.7E-2,null,301,"",3,"Y"]
["East Midlands",690017,"Rugby 132/33/25/11kV S Stn",4.2000000000000003E-2,null,361,"",3,"Y"]
["East Midlands",690018,"Nuneaton 132/33kV S Stn",8.5000000000000006E-2,null,632,"",3,"Y"]
["East Midlands",690020,"Warwick 132/33/11kV S Stn",4.1000000000000002E-2,null,274,"",3,"Y"]
["East Midlands",690021,"Middlemarsh 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["East Midlands",690022,"Loughborough 132/33/11kV S Stn",9.1999999999999998E-2,null,436,"",3,"Y"]
["East Midlands",690023,"Leicester North 132/33kV S Stn",0.1,null,113,"",3,"Y"]
["East Midlands",690024,"Coalville 132/33kV S Stn",0.109,null,382,"",3,"Y"]
["East Midlands",690025,"Leicester East 132/33kV S Stn",3.6999999999999998E-2,null,68,"",3,"Y"]
["East Midlands",690026,"Leicester 132/33kV S Stn",4.2999999999999997E-2,null,524,"",1,"Y"]
["East Midlands",690027,"Wigston 132/33/11kV S Stn",0.2,"Y",393,"",3,"Y"]
["East Midlands",690028,"Kibworth 132/33kV S Stn",9.5000000000000001E-2,null,319,"",3,"Y"]
["East Midlands",690029,"Hinckley 132/33/11kV S Stn",0.159,null,872,"",3,"Y"]
["East Midlands",690030,"Skegness 132/33kV S Stn",5.0999999999999997E-2,null,192,"",3,"Y"]
["East Midlands",690031,"Grantham North 132/25/11kV S Stn",0.104,null,376,"",1,"Y"]
["East Midlands",690032,"Grantham South 132kV S Stn",0.2,null,700,"",1,"Y"]
["East Midlands",690033,"Melton Mowbray 132/33kV S Stn",4.2999999999999997E-2,null,242,"",3,"Y"]
["East Midlands",690034,"Asfordby 132kV S Stn",9.5000000000000001E-2,null,185,"",1,"Y"]
["East Midlands",690035,"Stamford 132/33kV S Stn",5.6000000000000001E-2,null,222,"",3,"Y"]
["East Midlands",690036,"Spalding 132/33kV S Stn",3.4000000000000002E-2,null,147,"",3,"Y"]
["East Midlands",690037,"Sleaford 132/33kV S Stn",0.13700000000000001,null,349,"",3,"Y"]
["East Midlands",690038,"Oakham 132/33kV S Stn",8.6999999999999994E-2,null,413,"",3,"Y"]
["East Midlands",690039,"Bourne West 132/25kV S Stn",0.17399999999999999,null,1366,"",1,"Y"]
["East Midlands",690040,"South Holland 132/33kV S Stn",3.9E-2,null,359,"",3,"Y"]
["East Midlands",690041,"Grantham 132/33kV S Stn",0.3,null,1096,"",3,"Y"]
["East Midlands",690042,"Hawton 132/33kV S Stn",7.0000000000000007E-2,null,469,"",3,"Y"]
["East Midlands",690043,"Boston 132/33kV S Stn",3.9E-2,null,257,"",3,"Y"]
["East Midlands",690044,"Bourne 132/33kV S Stn",0.09,null,844,"",3,"Y"]
["East Midlands",690045,"Stony Stratford 132/33kV S Stn",9.1999999999999998E-2,null,1074,"",3,"Y"]
["East Midlands",690046,"Bletchley 132/33kV S Stn",2.7E-2,null,166,"",3,"Y"]
["East Midlands",690047,"Brackley 132/33kV S Stn",0.1,null,637,"",3,"Y"]
["East Midlands",690048,"Corby North 132kV S Stn",6.5000000000000002E-2,null,1049,"",1,"Y"]
["East Midlands",690049,"Irthlingborough 132/33kV S Stn",6.5000000000000002E-2,null,131,"",3,"Y"]
["East Midlands",690050,"Kettering 132/33kV S Stn",0.02,null,168,"",3,"Y"]
["East Midlands",690051,"Wellingborough 132/33kV S Stn",4.4999999999999998E-2,null,217,"",3,"Y"]
["East Midlands",690052,"Daventry 132/33kV S Stn",4.4999999999999998E-2,null,147,"",3,"Y"]
["East Midlands",690053,"Northampton East 132/33kV S Stn",0.09,null,637,"",3,"Y"]
["East Midlands",690054,"Northampton West 132/33kV S Stn",5.2999999999999999E-2,null,1000,"Y",3,"Y"]
["East Midlands",690055,"Northampton 132/33kV S Stn",5.2999999999999999E-2,null,570,"",3,"Y"]
["East Midlands",690057,"Lincoln Main 132/33/11kV S Stn",0.04,null,236,"",3,"Y"]
["East Midlands",690058,"Lincoln Local 132kV S Stn",7.0000000000000007E-2,null,261,"",1,"Y"]
["East Midlands",690059,"Warwick Grid 132/11kV S Stn",4.1000000000000002E-2,null,274,"",1,"Y"]
["East Midlands",690060,"Willesley 33/11kV S Stn",0.23200000000000001,null,220,"",3,"Y"]
["East Midlands",690061,"East Claydon 400/132kV S Stn",3.9E-2,null,936,"",1,"Y"]
["East Midlands",690063,"North Greetwell 132kV S Stn",0.23200000000000001,null,1392,"",1,"Y"]
["East Midlands",690064,"Hatton Gas Compressor 132kV S Stn",0.15,null,480,"",1,"Y"]
["East Midlands",690067,"Pailton 33kV S Stn",0.19,null,807,"",3,"Y"]
["East Midlands",690068,"Sleaford REP 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["East Midlands",690069,"Clay Lake Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",690070,"Bowbridge STOR Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",690071,"Old Dalby Lodge Wind Farm 33kV S Stn",0.13900000000000001,null,285,"",3,"Y"]
["West Midlands",690072,"Carlton Park 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["East Midlands",690073,"Lincoln No 2 33kV S Stn",0.04,null,236,"",3,"Y"]
["East Midlands",690074,"Raunds 33kV S Stn",0.12,null,190,"",3,"Y"]
["East Midlands",690075,"East Claydon 132/33kV S Stn",3.9E-2,null,936,"",3,"Y"]
["East Midlands",720004,"Lea Marston 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
["West Midlands",720004,"Lea Marston 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
["West Midlands",726003,"Bloxwich Ess 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",735832,"I54 33/11kv S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",735840,"Union Road Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",736099,"Wolverhampton Power 33kv S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",736183,"Hinksford Farm Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",745465,"Henley Solar Farm 33kV S Stn",0.126,null,252,"",3,"Y"]
["West Midlands",745501,"High Point Solar Pv 33kv S Stn",9.8000000000000004E-2,null,128,"",3,"Y"]
["West Midlands",745828,"Rock Farm ESS 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",750002,"Tenbury 33/11kV S Stn",0.16400000000000001,null,379,"",3,"Y"]
["West Midlands",750003,"Craven Arms 33/11kV S Stn",0.15,null,196,"",3,"Y"]
["West Midlands",750004,"Cleobury Mortimer 33/11kV S Stn",0.17199999999999999,null,241,"",3,"Y"]
["West Midlands",756542,"Larport Farm 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",756593,"Witches Solar Park 66kV S Stn",0.21,null,340,"",3,"Y"]
["West Midlands",759000,"Rotherdale Farm 66kv S Stn",0.13,null,270,"",3,"Y"]
["West Midlands",765589,"Hartlebury 66/11kV S Stn",0.28100000000000003,null,281,"",3,"Y"]
["West Midlands",765590,"Northwick Generation 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",770001,"Wribbenhall 33/11kV S Stn",0.26,null,338,"",3,"Y"]
["West Midlands",770002,"Stockton 33/11kV S Stn",0.375,null,348,"",3,"Y"]
["West Midlands",770003,"Quatt 33/11kV S Stn",0.127,null,254,"",3,"Y"]
["West Midlands",770004,"Star Aluminium 33/11kV S Stn",0.19400000000000001,null,139,"",3,"Y"]
["West Midlands",770005,"Kinver 33/11kV S Stn",1.2130000000000001,null,1237,"",3,"Y"]
["West Midlands",778160,"Rotherdale Farm Pv 66kv S Stn",0.13,null,270,"",3,"Y"]
["West Midlands",778880,"Hartlebury EFW 66kV S Stn",0.28100000000000003,null,281,"",3,"Y"]
["West Midlands",778960,"Drayton Farm North 66/11kv S Stn",9.1999999999999998E-2,null,209,"",3,"Y"]
["West Midlands",779071,"Astley Solar Farm 33kv S Stn",0.47,null,351,"",3,"Y"]
["West Midlands",779441,"Howard Road STOR 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",779493,"Upper Meadowly Pv Farm 33kv S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",790001,"Lydney 33/11kV S Stn",0.21,null,712,"",3,"Y"]
["West Midlands",790002,"Tuffley 33/11kV S Stn",2.5999999999999999E-2,null,54,"",3,"Y"]
["West Midlands",790003,"Wapley 33kV S Stn",0.27900000000000003,null,415,"",3,"Y"]
["West Midlands",790004,"Oxbridge 33/11kV S Stn",0.218,null,312,"",3,"Y"]
["West Midlands",790005,"Brockworth 33/11kV S Stn",2.1000000000000001E-2,null,48,"",3,"Y"]
["West Midlands",790007,"Commercial Road 33/11kV S Stn",8.5000000000000006E-2,null,125,"",3,"Y"]
["West Midlands",790008,"Alveston 33/11kV S Stn",1.1000000000000001,null,1716,"",3,"Y"]
["West Midlands",790009,"Dudbridge 33/11kV S Stn",0.17299999999999999,null,237,"",3,"Y"]
["West Midlands",790010,"Cherington 33/11kV S Stn",2.95,null,2183,"",3,"Y"]
["West Midlands",790011,"Cowhorn 33/11kV S Stn",8.7999999999999995E-2,null,120,"",3,"Y"]
["West Midlands",790012,"Naishcombe Hill 33/11kV S Stn",0.66,null,832,"",3,"Y"]
["West Midlands",790013,"Camp 33/11kV S Stn",1.357,null,1154,"",3,"Y"]
["West Midlands",790014,"Mitcheldean 33/11kV S Stn",0.193,null,239,"",3,"Y"]
["West Midlands",790015,"Berkeley 33/11kV S Stn",0.33800000000000002,null,423,"",3,"Y"]
["West Midlands",790016,"Elton 33/11kV S Stn",0.33800000000000002,null,403,"",3,"Y"]
["West Midlands",790017,"Stowfield 33/11kV S Stn",0.246,null,236,"",3,"Y"]
["West Midlands",790018,"Bixhead 33/11kV S Stn",0.38500000000000001,null,454,"",3,"Y"]
["West Midlands",790019,"Wyelands 33kV S Stn",0.42599999999999999,null,443,"",3,"Y"]
["West Midlands",790021,"Dursley 33/11kV S Stn",6.7000000000000004E-2,null,120,"",3,"Y"]
["West Midlands",790022,"Netherhills 33/11kV S Stn",0.27300000000000002,null,380,"",3,"Y"]
["West Midlands",790023,"Mead Lane 33/11kV S Stn",0.08,null,113,"",3,"Y"]
["West Midlands",790024,"Coaley 33kV S Stn",0.23499999999999999,null,411,"",3,"Y"]
["West Midlands",790025,"Hammerley Down 33/11kV S Stn",0.50600000000000001,null,582,"",3,"Y"]
["West Midlands",790026,"Bilson 33/11kV S Stn",0.104,null,260,"",3,"Y"]
["West Midlands",790028,"Princess Royal 33/11kV S Stn",0.28899999999999998,null,390,"",3,"Y"]
["West Midlands",790029,"Rotol 33/11kV S Stn",0.06,null,186,"",3,"Y"]
["West Midlands",795484,"Tower Hill Solar Farm 33kv S Stn",0.874,null,942,"",3,"Y"]
["West Midlands",795644,"Cambridge Solar Power 33kv S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",795651,"Upper Wick Solar Farm 33kv S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",795655,"Upper Huntingford Solar Farm 33kv S Stn",0.1,null,162,"",3,"Y"]
["West Midlands",795658,"Ring O Bells Solar Farm 33kV S Stn",0.14599999999999999,null,203,"",3,"Y"]
["West Midlands",795669,"Hall Farm Pv Awre 33kv S Stn",0.15,null,117,"",3,"Y"]
["West Midlands",795720,"Actrees Solar Farm 33kV S Stn",7.6999999999999999E-2,null,105,"",3,"Y"]
["West Midlands",795721,"Bristol Road 33kV S Stn",0.04,null,84,"",3,"Y"]
["West Midlands",795731,"Yorkley Solar Farm 33kV S Stn",0.19,null,402,"",3,"Y"]
["West Midlands",795794,"Sudmeadow Road STOR Generation 33kV S Stn",0.8,null,1029,"",3,"Y"]
["West Midlands",795870,"EFW Javelin Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",798100,"Say Farm 33kv S Stn",0.22,null,303,"",3,"Y"]
["West Midlands",840002,"Halesfield 33/11kV S Stn",7.3999999999999996E-2,null,198,"",3,"Y"]
["West Midlands",840003,"Worfield 33/11kV S Stn",0.36,null,490,"",3,"Y"]
["West Midlands",840004,"Shifnal 33/11kV S Stn",0.22600000000000001,null,407,"",3,"Y"]
["West Midlands",840005,"Priestweston 33/11kV S Stn",0.81,null,811,"",3,"Y"]
["West Midlands",840006,"Leebotwood 33/11kV S Stn",0.48399999999999999,null,523,"",3,"Y"]
["West Midlands",840007,"Bishops Castle 33/11kV S Stn",0.19,null,134,"",3,"Y"]
["West Midlands",840008,"Easthope 33/11kV S Stn",0.6,null,586,"",3,"Y"]
["West Midlands",840009,"Newport 33/11kV S Stn",0.25,null,407,"",3,"Y"]
["West Midlands",840010,"Donnington 33/11kV S Stn",7.8E-2,null,161,"",3,"Y"]
["West Midlands",840011,"Snedshill 33/11kV S Stn",0.1,null,249,"",3,"Y"]
["West Midlands",840012,"Sankey 33/11kV S Stn",0.27400000000000002,null,403,"",3,"Y"]
["West Midlands",840013,"Bayston Hill 33/11kV S Stn",0.26,null,494,"",3,"Y"]
["West Midlands",840014,"Madeley 33/11kV S Stn",6.5000000000000002E-2,null,83,"",3,"Y"]
["West Midlands",840016,"Leaton 33/11kV S Stn",0.41099999999999998,null,652,"",3,"Y"]
["West Midlands",840017,"Malehurst 33/11kV S Stn",0.23599999999999999,null,354,"",3,"Y"]
["West Midlands",840018,"Berrington 33/11kV S Stn",0.36,null,710,"",3,"Y"]
["West Midlands",840019,"Dothill 33/11kV S Stn",0.20799999999999999,null,386,"",3,"Y"]
["West Midlands",840020,"Roushill 33/11kV S Stn",0.08,null,166,"",3,"Y"]
["West Midlands",840021,"Harlescott 33/11kV S Stn",6.3E-2,null,214,"",3,"Y"]
["West Midlands",840022,"Weir Hill 33/11kV S Stn",0.22,null,493,"",3,"Y"]
["West Midlands",840023,"Broseley 33/11kV S Stn",0.13,null,258,"",3,"Y"]
["West Midlands",840024,"Rowton 33/11kV S Stn",0.34,null,510,"",3,"Y"]
["West Midlands",840025,"Spring Gardens 33/11kV S Stn",0.23,null,368,"",3,"Y"]
["West Midlands",840698,"Battlefield Generation 33kV S Stn",0.14000000000000001,null,98,"",3,"Y"]
["West Midlands",840844,"Hayford Solar Farm 33kV S Stn",0.14000000000000001,null,202,"",3,"Y"]
["West Midlands",841517,"Wrockwardine Farm 33kV S Stn",0.14000000000000001,null,275,"",3,"Y"]
["West Midlands",841546,"Condover Solar Farm 33kV S Stn",0.26,null,284,"",3,"Y"]
["West Midlands",841751,"Pitchford Solar Farm 33kV S Stn",0.19,null,191,"",3,"Y"]
["West Midlands",841809,"Sundorne Solar Farm 33kV S Stn",0.12,null,291,"",3,"Y"]
["West Midlands",841865,"Sheriffhales Solar Farm 33kv S Stn",0.13600000000000001,null,272,"",3,"Y"]
["West Midlands",850001,"Longton 132/33/11kV S Stn",4.7E-2,null,420,"",3,"Y"]
["West Midlands",850002,"Bearstone 33/11kV S Stn",0.42699999999999999,null,427,"",3,"Y"]
["West Midlands",850003,"Hill Chorlton 33/11kV S Stn",0.67700000000000005,null,193,"",3,"Y"]
["West Midlands",850004,"High Offley 33/11kV S Stn",0.5,null,526,"",3,"Y"]
["West Midlands",850005,"Cotes Heath 33/11kV S Stn",0.17,null,425,"",3,"Y"]
["West Midlands",850006,"Hookgate 33/11kV S Stn",0.54,null,1030,"",3,"Y"]
["West Midlands",850007,"Hinstock 33/11kV S Stn",0.56999999999999995,null,689,"",3,"Y"]
["West Midlands",850008,"Market Drayton 33/11kV S Stn",0.21,null,700,"",3,"Y"]
["West Midlands",850009,"Gnosall 33/11kV S Stn",0.16300000000000001,null,152,"",3,"Y"]
["West Midlands",850010,"Eccleshall 33/11kV S Stn",0.20100000000000001,null,228,"",3,"Y"]
["West Midlands",850011,"Stoke CHP 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",850012,"Goldenhill Bank 33/11kV S Stn",0.108,null,169,"",3,"Y"]
["West Midlands",850013,"Talke 33/11kV S Stn",0.08,null,110,"",3,"Y"]
["West Midlands",850014,"Scot Hay 33/11kV S Stn",0.34,null,595,"",3,"Y"]
["West Midlands",850015,"Knypersley 33/11kV S Stn",0.15,null,418,"",3,"Y"]
["West Midlands",850016,"Endon 33/11kV S Stn",0.41299999999999998,null,909,"",3,"Y"]
["West Midlands",850017,"Froghall 33/11kV S Stn",0.19400000000000001,null,238,"",3,"Y"]
["West Midlands",850018,"Kingsley Holt 33/11kV S Stn",0.221,null,351,"",3,"Y"]
["West Midlands",850019,"Tean 33/11kV S Stn",0.2,null,256,"",3,"Y"]
["West Midlands",850020,"Cheddleton 33/11kV S Stn",0.23100000000000001,null,416,"",3,"Y"]
["West Midlands",850021,"Cauldon Cement 33kV S Stn",0.251,null,277,"",3,"Y"]
["West Midlands",850022,"Congleton 33/11kV S Stn",7.5999999999999998E-2,null,115,"",3,"Y"]
["West Midlands",850024,"Cheadle 33/11kV S Stn",0.13700000000000001,null,229,"",3,"Y"]
["West Midlands",850026,"Cauldon 33/11kV S Stn",0.34,null,454,"",3,"Y"]
["West Midlands",850027,"British Industrial Sand 33kV S Stn",0.51200000000000001,null,701,"",3,"Y"]
["West Midlands",850028,"Leek 33/11kV S Stn",0.216,null,307,"",3,"Y"]
["West Midlands",850029,"Simplex 33/11kV S Stn",4.9000000000000002E-2,null,110,"",3,"Y"]
["West Midlands",856887,"Lower Newton Solar Farm 33kV S Stn",0.13,null,185,"",3,"Y"]
["West Midlands",856916,"Swancote AD Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["West Midlands",857114,"Staunch Standby Generation 33kv S Stn",0.89,null,447,"",3,"Y"]
["West Midlands",863412,"Moneystone Quarry PV Farm 33kV S Stn",0.249,null,373,"",3,"Y"]
["West Midlands",863413,"Heywood Grange PV Farm 33kV S Stn",0.21,null,556,"",3,"Y"]
["East Midlands",870004,"Burton South 33kV S Stn",0.1,null,843,"",3,"Y"]
["East Midlands",870005,"Derby South 33kV S Stn",0.05,null,134,"",3,"Y"]
["East Midlands",870006,"Spondon 33kV S Stn",7.1999999999999995E-2,null,984,"",3,"Y"]
["East Midlands",870007,"Heanor 33kV S Stn",9.5000000000000001E-2,null,522,"",3,"Y"]
["East Midlands",870009,"Uttoxeter 33kV S Stn",0.156,null,569,"",3,"Y"]
["East Midlands",870010,"Gresley 33kV S Stn",0.11700000000000001,null,671,"",3,"Y"]
["East Midlands",870011,"Stanton 33kV S Stn",7.3200000000000001E-2,null,457,"",3,"Y"]
["East Midlands",870012,"Derby 33kV S Stn",8.4000000000000005E-2,null,375,"",3,"Y"]
["East Midlands",870013,"Barton Under Needwood 33/11kV S Stn",0.16500000000000001,null,185,"",3,"Y"]
["East Midlands",870014,"Trent Lane 33/11kV S Stn",0.22600000000000001,null,339,"",3,"Y"]
["East Midlands",870015,"Eagle Centre 33/11kV S Stn",0.1,null,95,"",3,"Y"]
["East Midlands",870016,"Bombardier 33kV S Stn",5.3999999999999999E-2,null,127,"",3,"Y"]
["East Midlands",870017,"Melbourne 33/11kV S Stn",0.129,null,249,"",3,"Y"]
["East Midlands",870019,"Sinfin C 33kV S Stn",8.1000000000000003E-2,null,148,"",3,"Y"]
["East Midlands",870022,"Heanor 33/11kV S Stn",9.5000000000000001E-2,null,522,"",3,"Y"]
["East Midlands",870026,"Rocester 33/11kV S Stn",0.13100000000000001,null,197,"",3,"Y"]
["East Midlands",870027,"Church Street 33/11kV S Stn",1.4999999999999999E-2,null,206,"",3,"Y"]
["East Midlands",870028,"Marchington 33/11kV S Stn",0.215,null,338,"",3,"Y"]
["East Midlands",870029,"Wellington Street 33/11kV S Stn",8.5000000000000006E-2,null,172,"",3,"Y"]
["East Midlands",870030,"Ashbourne 33/11kV S Stn",0.125,null,230,"",3,"Y"]
["East Midlands",870031,"Hatton 33/11kV S Stn",4.3999999999999997E-2,null,88,"",3,"Y"]
["East Midlands",870032,"Station Street 33/11kV S Stn",0.26,null,248,"",3,"Y"]
["East Midlands",870033,"Ravensdale Park 33/11kV S Stn",0.20200000000000001,null,290,"",3,"Y"]
["East Midlands",870034,"Bretby 33/11kV S Stn",8.8999999999999996E-2,null,130,"",3,"Y"]
["East Midlands",870035,"Trent Alloys 33/11kV S Stn",0.17399999999999999,null,216,"",3,"Y"]
["East Midlands",870036,"Derby 132/11kV S Stn",8.4000000000000005E-2,null,375,"",1,"Y"]
["East Midlands",870037,"Woodville 33/11kV S Stn",0.28199999999999997,null,333,"",3,"Y"]
["East Midlands",870038,"Mackworth 33/11kV S Stn",9.8000000000000004E-2,null,200,"",3,"Y"]
["East Midlands",870039,"Darley Abbey 33/11kV S Stn",0.09,null,132,"",3,"Y"]
["East Midlands",870040,"Normanton 33/11kV S Stn",0.11899999999999999,null,238,"",3,"Y"]
["East Midlands",870041,"Sinfin Lane 33/11kV S Stn",8.1000000000000003E-2,null,148,"",3,"Y"]
["East Midlands",870042,"Morley 33/11kV S Stn",0.104,null,208,"",3,"Y"]
["East Midlands",870043,"Allenton 33/11kV S Stn",8.1000000000000003E-2,null,229,"",3,"Y"]
["East Midlands",870044,"Chaddesden 33/11kV S Stn",8.7999999999999995E-2,null,205,"",3,"Y"]
["East Midlands",870045,"Osmaston Road 33/6.6kv S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",870046,"Spondon 33/11kV S Stn",7.1999999999999995E-2,null,984,"",3,"Y"]
["East Midlands",870047,"Castle Donington 33/11kV S Stn",0.13600000000000001,null,171,"",3,"Y"]
["East Midlands",870048,"Ilkeston 33/11kV S Stn",0.17,null,276,"",3,"Y"]
["East Midlands",870049,"Little Hallam 33/11kV S Stn",0.17499999999999999,null,315,"",3,"Y"]
["East Midlands",870050,"Long Eaton 33/11kV S Stn",6.4000000000000001E-2,null,115,"",3,"Y"]
["East Midlands",870051,"Sandiacre 33/11kV S Stn",9.8000000000000004E-2,null,190,"",3,"Y"]
["East Midlands",870053,"Gresley 33/11kV S Stn",0.11700000000000001,null,671,"",3,"Y"]
["East Midlands",874558,"Burton 132/11kV S Stn",1.9E-2,null,141,"",1,"Y"]
["East Midlands",874972,"Smith Hall Farm Solar Plant 33kV S Stn",0.28999999999999998,null,235,"",3,"Y"]
["East Midlands",874987,"Aston House Solar Farm 33kV S Stn",0.23499999999999999,null,291,"",3,"Y"]
["East Midlands",874992,"Rolleston Park Solar Farm 33kV S Stn",0.16,null,255,"",3,"Y"]
["East Midlands",875000,"Burton 33kV S Stn",1.9E-2,null,141,"",3,"Y"]
["East Midlands",875036,"Green Lane Marchinton PV 33kV S Stn",0.24,null,411,"",3,"Y"]
["East Midlands",875043,"Moat Farm Draycott-In-The-Clay Solar Site 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",875065,"Holtwood Farm Solar Park 33kV S Stn",0.22,null,274,"",3,"Y"]
["East Midlands",875067,"Drakelow Solar Farm 33kV S Stn",0.18,null,119,"",3,"Y"]
["East Midlands",875073,"Derby Waste Sinfin Lane 33kV S Stn",0.125,null,334,"",3,"Y"]
["East Midlands",875086,"Trafalgar Park Gas Peaking S15 33kV S Stn",0.23,null,406,"",3,"Y"]
["East Midlands",875119,"Dayfields Farm PV 33kV S Stn",0.24,null,278,"",3,"Y"]
["East Midlands",875136,"Infinity Park 33/11kv S Stn",0.14799999999999999,null,410,"",3,"Y"]
["East Midlands",875141,"Taylor Lane STOR 33kV S Stn",2,null,522,"",3,"Y"]
["East Midlands",875155,"Nottingham Road STOR 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",875157,"Breach Farm 33kv S Stn",0.747,null,1141,"",3,"Y"]
["East Midlands",875166,"Twin Oaks STOR 33kV S Stn",0.56999999999999995,null,816,"",3,"Y"]
["East Midlands",880002,"Nottingham East 33kV S Stn",3.2000000000000001E-2,null,275,"",3,"Y"]
["East Midlands",880003,"Nottingham 33kV S Stn",7.6999999999999999E-2,null,601,"",3,"Y"]
["East Midlands",880004,"Toton 33kV S Stn",9.6000000000000002E-2,null,567,"",3,"Y"]
["East Midlands",880005,"Nottingham North 33kV S Stn",1.7999999999999999E-2,null,160,"",3,"Y"]
["East Midlands",880006,"Willoughby 33kV S Stn",7.9000000000000001E-2,null,329,"",3,"Y"]
["East Midlands",880009,"Toton 33/11kV S Stn",9.6000000000000002E-2,null,567,"",3,"Y"]
["East Midlands",880010,"Chilwell 33/11kV S Stn",0.106,null,190,"",3,"Y"]
["East Midlands",880011,"Hucknall 33/11kV S Stn",0.191,null,285,"",3,"Y"]
["East Midlands",880012,"Beeston 33/11kV S Stn",0.1,null,216,"",3,"Y"]
["East Midlands",880013,"Bilborough 33/11kV S Stn",0.13100000000000001,null,277,"",3,"Y"]
["East Midlands",880014,"Lenton 33/11kV S Stn",0.17599999999999999,null,412,"",3,"Y"]
["East Midlands",880015,"Cinderhill 33/11kV S Stn",0.09,null,136,"",3,"Y"]
["East Midlands",880016,"Boots 33/11kV S Stn",0.153,null,384,"",3,"Y"]
["East Midlands",880017,"North Wilford 33/11kV S Stn",6.6000000000000003E-2,null,193,"",3,"Y"]
["East Midlands",880018,"Ratcliffe On Soar 33/11kV S Stn",6.4399999999999999E-2,null,1269,"",3,"Y"]
["East Midlands",880019,"Bulwell 33/11kV S Stn",7.5999999999999998E-2,null,176,"",3,"Y"]
["East Midlands",880020,"Wollaton Road 33/11kV S Stn",6.5000000000000002E-2,null,130,"",3,"Y"]
["East Midlands",880021,"Nottingham North 132/11kV S Stn",1.7999999999999999E-2,null,160,"",1,"Y"]
["East Midlands",880022,"Talbot Street 33/11kV S Stn",0.13500000000000001,null,204,"",3,"Y"]
["East Midlands",880023,"East Leake 33/11kV S Stn",0.14399999999999999,null,215,"",3,"Y"]
["East Midlands",880024,"Clifton 33/11kV S Stn",9.7000000000000003E-2,null,363,"",3,"Y"]
["East Midlands",880025,"Castle Road 33/11kV S Stn",7.2999999999999995E-2,null,194,"",3,"Y"]
["East Midlands",880026,"Marlborough Road 33/11kV S Stn",0.161,null,243,"",3,"Y"]
["East Midlands",880027,"Arnold 33/11kV S Stn",0.16700000000000001,null,326,"",3,"Y"]
["East Midlands",880028,"West Bridgford 33/11kV S Stn",7.8E-2,null,118,"",3,"Y"]
["East Midlands",880029,"Mapperley 33/11kV S Stn",9.6000000000000002E-2,null,145,"",3,"Y"]
["East Midlands",880030,"Sneinton 33/11kV S Stn",9.1999999999999998E-2,null,141,"",3,"Y"]
["East Midlands",880031,"Calverton 33/11kV S Stn",0.27700000000000002,null,300,"",3,"Y"]
["East Midlands",880032,"Willoughby 33/11kV S Stn",7.9000000000000001E-2,null,329,"",3,"Y"]
["East Midlands",880033,"Keyworth 33/11kV S Stn",0.105,null,211,"",3,"Y"]
["East Midlands",880034,"Gedling 33/11kV S Stn",8.7999999999999995E-2,null,215,"",3,"Y"]
["East Midlands",880035,"Colwick 33/11kV S Stn",2.1999999999999999E-2,null,175,"",3,"Y"]
["East Midlands",880036,"Cotgrave 33/11kV S Stn",0.126,null,177,"",3,"Y"]
["East Midlands",880037,"Caythorpe 33/11kV S Stn",0.30499999999999999,null,573,"",3,"Y"]
["East Midlands",880038,"Sibthorpe 33/11kV S Stn",0.23,null,414,"",3,"Y"]
["East Midlands",880039,"Bingham 33/11kV S Stn",6.0999999999999999E-2,null,73,"",3,"Y"]
["East Midlands",880040,"St Anns 33/11kV S Stn",0.218,null,294,"",3,"Y"]
["East Midlands",880042,"London Road Heat Station 33kV S Stn",3.1E-2,null,47,"",3,"Y"]
["East Midlands",883330,"Willoughby STOR 33kV S Stn",7.9000000000000001E-2,null,500,"Y",3,"Y"]
["East Midlands",883349,"Lodge Farm Solar Park 33kV S Stn",0.09,null,132,"",3,"Y"]
["East Midlands",883362,"Watnall Primary 33/11kV S Stn",1.04,null,592,"",3,"Y"]
["East Midlands",883446,"Langar Solar Switch Room 33kV S Stn",0.16400000000000001,null,198,"",3,"Y"]
["East Midlands",883447,"Redfield Road 1 STOR 33kV S Stn",0.42,null,593,"",3,"Y"]
["East Midlands",883456,"Shelton Lodge Solar Generation 33kV S Stn",0.20300000000000001,null,285,"",3,"Y"]
["East Midlands",883465,"Stragglethorpe Road Pv Solar Park 33kv S Stn",0.128,null,236,"",3,"Y"]
["East Midlands",883503,"Redfield Road 2 STOR 33kV S Stn",0.36,null,683,"",3,"Y"]
["East Midlands",883570,"Private Road No 5 Colwick STOR 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",890003,"West Burton 400/132kV S Stn",3.7199999999999997E-2,null,599,"",1,"Y"]
["East Midlands",890006,"Clipstone 33kV S Stn",0.18,null,477,"",3,"Y"]
["East Midlands",890007,"Annesley 33kV S Stn",8.2000000000000003E-2,null,370,"",3,"Y"]
["East Midlands",890008,"Mansfield 33kV S Stn",0.1,null,383,"",3,"Y"]
["East Midlands",890009,"Whitwell 33kV S Stn",0.42699999999999999,null,1320,"",3,"Y"]
["East Midlands",890010,"Checkerhouse 33/11kV S Stn",0.21,null,685,"",3,"Y"]
["East Midlands",890011,"Worksop 33kV S Stn",0.14399999999999999,null,586,"",3,"Y"]
["East Midlands",890013,"Winster 33kV S Stn",0.17899999999999999,null,565,"",3,"Y"]
["East Midlands",890014,"Alfreton 33kV S Stn",0.193,null,752,"",3,"Y"]
["East Midlands",890015,"Staveley 33kV S Stn",4.8599999999999997E-2,null,372,"",3,"Y"]
["East Midlands",890016,"Goitside 33kV S Stn",9.1999999999999998E-2,null,88,"",3,"Y"]
["East Midlands",890017,"Daneshill Generation 33kV S Stn",0.28999999999999998,null,335,"",3,"Y"]
["East Midlands",890021,"Pinxton 132/11kV S Stn",0.13400000000000001,null,601,"",1,"Y"]
["East Midlands",890022,"Lindhurst Wind Farm 33kV S Stn",0.40400000000000003,null,553,"",3,"Y"]
["East Midlands",890023,"Sheepbridge 33/11kV S Stn",0.112,null,318,"",3,"Y"]
["East Midlands",890025,"Moorgreen 33/11kV S Stn",0.114,null,251,"",3,"Y"]
["East Midlands",890026,"Blackwell 33/11kV S Stn",0.114,null,201,"",3,"Y"]
["East Midlands",890027,"Huthwaite 33/11kV S Stn",7.9000000000000001E-2,null,132,"",3,"Y"]
["East Midlands",890028,"Westwood 33/11kV S Stn",0.219,null,314,"",3,"Y"]
["East Midlands",890029,"Teversal 33/11kV S Stn",0.105,null,205,"",3,"Y"]
["East Midlands",890030,"Skegby Lane 33/11kV S Stn",7.0000000000000007E-2,null,221,"",3,"Y"]
["East Midlands",890031,"Sutton Junction 33/11kV S Stn",0.10100000000000001,null,225,"",3,"Y"]
["East Midlands",890032,"Craggs Lane 33/11kV S Stn",0.156,null,293,"",3,"Y"]
["East Midlands",890033,"Annesley 33/11kV S Stn",8.2000000000000003E-2,null,370,"",3,"Y"]
["East Midlands",890034,"Shirebrook 33/11kV S Stn",0.23699999999999999,null,332,"",3,"Y"]
["East Midlands",890035,"Acreage Lane 33/11kV S Stn",0.59599999999999997,null,1173,"",3,"Y"]
["East Midlands",890036,"Mansfield 33/11kV S Stn",0.1,null,383,"",3,"Y"]
["East Midlands",890037,"Crown Farm 33/11kV S Stn",2.5999999999999999E-2,null,487,"",3,"Y"]
["East Midlands",890038,"Worksop West 33/11kV S Stn",0.157,null,308,"",3,"Y"]
["East Midlands",890039,"Lime Tree Place 33/11kV S Stn",0.154,null,233,"",3,"Y"]
["East Midlands",890040,"Clipstone 33/11kV S Stn",0.18,null,477,"",3,"Y"]
["East Midlands",890041,"Blidworth 33/11kV S Stn",0.64400000000000002,null,1173,"",3,"Y"]
["East Midlands",890042,"Holme Carr 33/11kV S Stn",0.314,null,566,"",3,"Y"]
["East Midlands",890043,"Kilton Road 33/11kV S Stn",0.23799999999999999,null,395,"",3,"Y"]
["East Midlands",890044,"Manton 33/11kV S Stn",0.27,null,385,"",3,"Y"]
["East Midlands",890045,"Budby 33/11kV S Stn",0.51200000000000001,null,737,"",3,"Y"]
["East Midlands",890046,"Warsop 33/11kV S Stn",0.25600000000000001,null,536,"",3,"Y"]
["East Midlands",890047,"Rufford 33/11kV S Stn",0.79200000000000004,null,1052,"",3,"Y"]
["East Midlands",890048,"Thoresby 33/11kV S Stn",0.31,null,2814,"",3,"Y"]
["East Midlands",890049,"Misson 33/11kV S Stn",0.17799999999999999,null,343,"",3,"Y"]
["East Midlands",890050,"Checkerhouse 33kV S Stn",0.21,null,685,"",3,"Y"]
["East Midlands",890051,"Ollerton 33/11kV S Stn",0.19,null,376,"",3,"Y"]
["East Midlands",890052,"Hallcroft Road 33/11kV S Stn",0.20599999999999999,null,225,"",3,"Y"]
["East Midlands",890053,"Ordsall Road 33/11kV S Stn",0.19400000000000001,null,360,"",3,"Y"]
["East Midlands",890054,"Bilsthorpe 33/11kV S Stn",0.2,null,396,"",3,"Y"]
["East Midlands",890055,"Bevercotes 33/11kV S Stn",0.17100000000000001,null,171,"",3,"Y"]
["East Midlands",890056,"Farnsfield 33/11kV S Stn",0.38700000000000001,null,766,"",3,"Y"]
["East Midlands",890057,"North Wheatley 33/11kV S Stn",0.53400000000000003,null,555,"",3,"Y"]
["East Midlands",890058,"Tuxford 33/11kV S Stn",0.23400000000000001,null,185,"",3,"Y"]
["East Midlands",890059,"Southwell 33/11kV S Stn",0.153,null,289,"",3,"Y"]
["East Midlands",890060,"Misterton 33/11kV S Stn",0.30099999999999999,null,286,"",3,"Y"]
["East Midlands",890061,"Carlton On Trent 33/11kV S Stn",0.67500000000000004,null,989,"",3,"Y"]
["East Midlands",890062,"Woodbeck 33/11kV S Stn",0.499,null,528,"",3,"Y"]
["East Midlands",890063,"Hindlow 33/11kV S Stn",1.3,null,2200,"",3,"Y"]
["East Midlands",890064,"Flagg 33/11kV S Stn",2.2000000000000002,null,2640,"",3,"Y"]
["East Midlands",890065,"Bakewell 33/11kV S Stn",0.3,null,268,"",3,"Y"]
["East Midlands",890066,"Eyam 33/11kV S Stn",0.5,null,685,"",3,"Y"]
["East Midlands",890067,"Longcliffe 33/11kV S Stn",0.65,null,1276,"",3,"Y"]
["East Midlands",890068,"Millclose 33/11kV S Stn",0.16400000000000001,null,273,"",3,"Y"]
["East Midlands",890069,"Robin Hood 33/11kV S Stn",0.26800000000000002,null,359,"",3,"Y"]
["East Midlands",890070,"Sheffield Road 33/11/6.6kV S Stn",0.13500000000000001,null,266,"",3,"Y"]
["East Midlands",890071,"Hopton 33/11kV S Stn",1.1970000000000001,null,1831,"",3,"Y"]
["East Midlands",890072,"Wingerworth 33/11kV S Stn",4.2999999999999997E-2,null,117,"",3,"Y"]
["East Midlands",890073,"Cromford 33/11kV S Stn",0.21,null,422,"",3,"Y"]
["East Midlands",890074,"Matlock 33/11kV S Stn",0.106,null,165,"",3,"Y"]
["East Midlands",890075,"Goitside 33/6.6kV S Stn",9.1999999999999998E-2,null,88,"",3,"Y"]
["East Midlands",890076,"Belper 33/11kV S Stn",8.3000000000000004E-2,null,120,"",3,"Y"]
["East Midlands",890077,"Ambergate 33/11kV S Stn",6.5000000000000002E-2,null,75,"",3,"Y"]
["East Midlands",890078,"Walton 33/11kV S Stn",0.16300000000000001,null,199,"",3,"Y"]
["East Midlands",890079,"Queens Park 33/11kV S Stn",0.1,null,159,"",3,"Y"]
["East Midlands",890080,"Staveley 33/11kV S Stn",4.8599999999999997E-2,null,372,"",3,"Y"]
["East Midlands",890081,"Robert Hyde 33/11kV S Stn",0.17699999999999999,null,350,"",3,"Y"]
["East Midlands",890082,"Denby 33/11kV S Stn",0.11799999999999999,null,250,"",3,"Y"]
["East Midlands",890083,"Eckington 33/11kV S Stn",0.122,null,262,"",3,"Y"]
["East Midlands",890084,"Grassmoor 33/11kV S Stn",0.08,null,182,"",3,"Y"]
["East Midlands",890085,"Clowne 33/11kV S Stn",0.5,null,884,"",3,"Y"]
["East Midlands",890086,"Somercotes 33/11kV S Stn",9.2999999999999999E-2,null,147,"",3,"Y"]
["East Midlands",890087,"Wessington 33/11kV S Stn",0.219,null,350,"",3,"Y"]
["East Midlands",890088,"Ripley 33/11kV S Stn",0.16300000000000001,null,319,"",3,"Y"]
["East Midlands",890089,"Halfway 33/11kV S Stn",0.11799999999999999,null,184,"",3,"Y"]
["East Midlands",890090,"Meadow Lane 33/11kV S Stn",0.215,null,424,"",3,"Y"]
["East Midlands",890091,"Westhorpe 33/11kV S Stn",6.5000000000000002E-2,null,205,"",3,"Y"]
["East Midlands",890093,"Bolsover 33/11kV S Stn",0.15,null,225,"",3,"Y"]
["East Midlands",890094,"Danesmoor 33/11kV S Stn",0.26300000000000001,null,108,"",3,"Y"]
["East Midlands",890095,"Biwaters 33/11kV S Stn",0.26200000000000001,null,349,"",3,"Y"]
["East Midlands",890098,"Staveley Works 33kV S Stn",6.3E-2,null,156,"",3,"Y"]
["East Midlands",890099,"Sherwood Park 33/11kV S Stn",0.14099999999999999,null,190,"",3,"Y"]
["East Midlands",897792,"Low Farm AD 33kV S Stn",0.27300000000000002,null,355,"",3,"Y"]
["East Midlands",898163,"Bentinck Generating Station 33kV S Stn",1.3,null,2275,"",3,"Y"]
["East Midlands",898181,"Stonish Hill Windfarm 33kV S Stn",0.14000000000000001,null,278,"",3,"Y"]
["East Midlands",898284,"Little Morton Solar Farm 33kV S Stn",8.5000000000000006E-2,null,134,"",3,"Y"]
["East Midlands",898308,"Welbeck Colliery Solar Generation 33kV S Stn",0.15,null,420,"",3,"Y"]
["East Midlands",898324,"Moat Farm Solar Farm 33kV S Stn",0.43,null,305,"",3,"Y"]
["East Midlands",898326,"Bilsthorpe Solar 33kV S Stn",0.27,null,208,"",3,"Y"]
["East Midlands",898340,"Eakring Solar Farm 33kV S Stn",0.22,null,395,"",3,"Y"]
["East Midlands",898344,"Welbeck Solar Farm 33kV S Stn",0.41,null,712,"",3,"Y"]
["East Midlands",898347,"Tiln Farm Solar Generation 33kV S Stn",0.19,null,246,"",3,"Y"]
["East Midlands",898350,"Thoresby Solar Farm 33kV S Stn",0.24,null,432,"",3,"Y"]
["East Midlands",898357,"Walkers Wood Solar Farm 33kV S Stn",0.35,null,581,"",3,"Y"]
["East Midlands",898371,"Cobb Farm Solar Generation 33kV S Stn",0.19600000000000001,null,175,"",3,"Y"]
["East Midlands",898432,"Lodge Farm Solar 33kV S Stn",0.09,null,132,"",3,"Y"]
["East Midlands",898435,"West End Farm Solar Generation 33kV S Stn",0.2,null,235,"",3,"Y"]
["East Midlands",898436,"Arkwright Solar 33kV S Stn",0.49,null,821,"",3,"Y"]
["East Midlands",898444,"Averill Solar Farm 33kV S Stn",0.13,null,150,"",3,"Y"]
["East Midlands",898460,"The Brek Solar 33kv S Stn",0.14199999999999999,null,404,"",3,"Y"]
["East Midlands",898475,"Littlewood Farm PV 33kV S Stn",0.28999999999999998,null,442,"",3,"Y"]
["East Midlands",898478,"Oxcroft Solar Farm 33kV S Stn",0.11899999999999999,null,204,"",3,"Y"]
["East Midlands",898482,"Twin Yards Solar Farm 33kV S Stn",0.23,null,283,"",3,"Y"]
["East Midlands",898483,"Retford Road Solar Generation 33kV S Stn",0.53,null,695,"",3,"Y"]
["East Midlands",898500,"Erin Road 33/11kV S Stn",0.25,null,397,"",3,"Y"]
["East Midlands",898530,"Garnham Close STOR 33kV S Stn",0.2,null,102,"",3,"Y"]
["East Midlands",898541,"Hermitage Lane Generation 33kV S Stn",0.61,null,325,"",3,"Y"]
["East Midlands",898555,"Bilsthorpe P V Generation 33kV S Stn",0.24,null,496,"",3,"Y"]
["East Midlands",898563,"Bolsover Moor Quarry PV Solar Farm 33kV S Stn",0.35,null,487,"",3,"Y"]
["East Midlands",898663,"Asher Lane STOR 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",900002,"Lincoln No 1 33kV S Stn",0.04,null,236,"",3,"Y"]
["East Midlands",900003,"Hawton 33kV S Stn",7.0000000000000007E-2,null,469,"",3,"Y"]
["East Midlands",900004,"Boston 33kV S Stn",3.9E-2,null,257,"",3,"Y"]
["East Midlands",900005,"Skegness 33kV S Stn",5.0999999999999997E-2,null,192,"",3,"Y"]
["East Midlands",900006,"Sleaford Road, Boston 33kV S Stn",0.11,null,330,"",3,"Y"]
["East Midlands",900007,"Marsh Lane 33/11kV S Stn",0.105,null,230,"",3,"Y"]
["East Midlands",900008,"Bambers Farm Wind Generation 33kV S Stn",0.2,null,272,"",3,"Y"]
["East Midlands",900009,"Beevor Street 33/11kV S Stn",0.15,null,300,"",3,"Y"]
["East Midlands",900010,"The Hollies Wind Farm 33kV S Stn",7.0000000000000007E-2,null,165,"",3,"Y"]
["East Midlands",900011,"Fernwood 33/11kV S Stn",0.13200000000000001,null,318,"",3,"Y"]
["East Midlands",900012,"Trusthorpe 33/11kV S Stn",0.115,null,230,"",3,"Y"]
["East Midlands",900013,"Horncastle 33/11kV S Stn",0.127,null,251,"",3,"Y"]
["East Midlands",900014,"Alford 33/11kV S Stn",0.26500000000000001,null,441,"",3,"Y"]
["East Midlands",900015,"Chapel St Leonards 33/11kV S Stn",0.219,null,438,"",3,"Y"]
["East Midlands",900016,"Spilsby 33kV S Stn",0.20300000000000001,null,357,"",3,"Y"]
["East Midlands",900017,"Ingoldmells 33/11kV S Stn",0.105,null,210,"",3,"Y"]
["East Midlands",900018,"Warth Lane 33/11kV S Stn",0.12,null,360,"",3,"Y"]
["East Midlands",900019,"Wrangle 33/11kV S Stn",0.17299999999999999,null,322,"",3,"Y"]
["East Midlands",900020,"Stickney 33kV S Stn",0.27200000000000002,null,310,"",3,"Y"]
["East Midlands",900021,"Langrick 33/11kV S Stn",0.22900000000000001,null,307,"",3,"Y"]
["East Midlands",900022,"Mount Bridge 33/11kV S Stn",0.08,null,151,"",3,"Y"]
["East Midlands",900023,"Great Hale 33/11kV S Stn",0.19600000000000001,null,226,"",3,"Y"]
["East Midlands",900024,"Newark Junction 33/11kV S Stn",0.161,null,240,"",3,"Y"]
["East Midlands",900025,"Swinderby 33/11kV S Stn",0.27200000000000002,null,266,"",3,"Y"]
["East Midlands",900026,"Hawton 33/11kV S Stn",7.0000000000000007E-2,null,469,"",3,"Y"]
["East Midlands",900027,"South Carlton 33kV S Stn",0.129,null,249,"",3,"Y"]
["East Midlands",900028,"Doddington Park 33/11kV S Stn",7.9000000000000001E-2,null,146,"",3,"Y"]
["East Midlands",900029,"North Hykeham 33/11kV S Stn",9.4E-2,null,150,"",3,"Y"]
["East Midlands",900030,"Rookery Lane 33/11kV S Stn",0.13,null,208,"",3,"Y"]
["East Midlands",900031,"Ruston & Hornsby 33/11kV S Stn",6.4000000000000001E-2,null,278,"",3,"Y"]
["East Midlands",900032,"Anderson Lane 33/11kV S Stn",0.121,null,369,"",3,"Y"]
["East Midlands",900033,"Waddington 33/11kV S Stn",0.13300000000000001,null,219,"",3,"Y"]
["East Midlands",900034,"Lincoln Local No 2 132/11kV S Stn",7.0000000000000007E-2,null,260,"",1,"Y"]
["East Midlands",900035,"Fiskerton 33/11kV S Stn",0.19,null,392,"",3,"Y"]
["East Midlands",900036,"Wragby 33/11kV S Stn",6.7000000000000004E-2,null,122,"",3,"Y"]
["East Midlands",900037,"Metheringham 33/11kV S Stn",0.13,null,250,"",3,"Y"]
["East Midlands",900038,"Woodhall Spa 33/11kV S Stn",0.219,null,799,"",3,"Y"]
["East Midlands",900039,"Tattershall 33/11kV S Stn",0.09,null,180,"",3,"Y"]
["East Midlands",900040,"Lincoln No 5 132/11kV S Stn",0.04,null,236,"",1,"Y"]
["East Midlands",904540,"EFW Paving Way 33kV S Stn",7.3999999999999996E-2,null,164,"",3,"Y"]
["East Midlands",905191,"Croft End Solar Farm 33kV S Stn",7.0000000000000007E-2,null,165,"",3,"Y"]
["East Midlands",905663,"Burton Pedwardine Solar Park 1 33kV S Stn",0.17799999999999999,null,267,"",3,"Y"]
["East Midlands",906124,"Whitecross Lane Solar Park Burton Pedwardine 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",906126,"Leverton Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",906387,"Fiskerton Solar Farm 33kV S Stn",8.4000000000000005E-2,null,229,"",3,"Y"]
["East Midlands",906537,"Grange Farm Solar Kirkby On Bain 33kV S Stn",5.1999999999999998E-2,null,46,"",3,"Y"]
["East Midlands",906775,"Canopus Solar Farm 33kV S Stn",5.8000000000000003E-2,null,119,"",3,"Y"]
["East Midlands",906936,"Lincoln Farm Solar 33kV S Stn",0.14799999999999999,null,359,"",3,"Y"]
["East Midlands",906972,"Hawton Wind Farm 33kV S Stn",0.27,null,684,"",3,"Y"]
["East Midlands",907000,"Lincoln Local No 4 132/11kV S Stn",7.0000000000000007E-2,null,261,"",1,"Y"]
["East Midlands",907046,"Leverton Battery Storage 33kV S Stn",0.91200000000000003,null,218,"",3,"Y"]
["East Midlands",907058,"Boston Biomass Generation 33kV S Stn",9.6000000000000002E-2,null,261,"",3,"Y"]
["East Midlands",907556,"Branston South Solar Farm 33kV S Stn",0.22,null,418,"",3,"Y"]
["East Midlands",910003,"Grantham 33kV S Stn",0.3,null,1096,"",3,"Y"]
["East Midlands",910004,"Stamford 33kV S Stn",5.6000000000000001E-2,null,222,"",3,"Y"]
["East Midlands",910005,"Bourne 33kV S Stn",0.09,null,844,"",3,"Y"]
["East Midlands",910006,"Melton Mowbray 33kV S Stn",4.2999999999999997E-2,null,242,"",3,"Y"]
["East Midlands",910007,"Oakham 33kV S Stn",8.6999999999999994E-2,null,413,"",3,"Y"]
["East Midlands",910008,"Sleaford 33kV S Stn",0.13700000000000001,null,349,"",3,"Y"]
["East Midlands",910009,"Spalding Clay Lake 33kV S Stn",3.4000000000000002E-2,null,145,"",3,"Y"]
["East Midlands",910010,"South Holland 33kV S Stn",3.9E-2,null,359,"",3,"Y"]
["East Midlands",910015,"Deeping St Nicholas Wind Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",910016,"Redhouse Farm Wind Farm Gedney 33kV S Stn",4.8000000000000001E-2,null,50,"",3,"Y"]
["East Midlands",910017,"Wardentree Park 33/11kV S Stn",0.18,null,266,"",3,"Y"]
["East Midlands",910018,"Grantham North 132/11kV S Stn",0.104,null,376,"",1,"Y"]
["East Midlands",910019,"Bicker Fen Wind Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",910021,"Sleaford 33/11kV S Stn",0.13700000000000001,null,349,"",3,"Y"]
["East Midlands",910022,"Kirton 33/11kV S Stn",9.6000000000000002E-2,null,192,"",3,"Y"]
["East Midlands",910023,"Spalding Park Road 33/11kV S Stn",0.06,null,90,"",3,"Y"]
["East Midlands",910024,"Donington 33/11kV S Stn",0.128,null,192,"",3,"Y"]
["East Midlands",910025,"Dowsby Fen 33/11kV S Stn",0.154,null,394,"",3,"Y"]
["East Midlands",910026,"Holbeach 33/11kV S Stn",7.5999999999999998E-2,null,111,"",3,"Y"]
["East Midlands",910027,"Long Sutton 33/11kV S Stn",0.13400000000000001,null,257,"",3,"Y"]
["East Midlands",910028,"Spalding Clay Lake 33/11kV S Stn",3.4000000000000002E-2,null,145,"",3,"Y"]
["East Midlands",910029,"Crowland 33/11kV S Stn",0.13800000000000001,null,215,"",3,"Y"]
["East Midlands",910030,"Whaplode Drove 33/11kV S Stn",0.27800000000000002,null,325,"",3,"Y"]
["East Midlands",910031,"Cranwell 33/11kV S Stn",0.11,null,220,"",3,"Y"]
["East Midlands",910032,"Bourne 33/11kV S Stn",0.09,null,844,"",3,"Y"]
["East Midlands",910033,"Ruskington 33/11kV S Stn",0.129,null,235,"",3,"Y"]
["East Midlands",910034,"New Beacon Road 33/11kV S Stn",0.08,null,102,"",3,"Y"]
["East Midlands",910035,"Billingborough 33/11kV S Stn",0.32300000000000001,null,633,"",3,"Y"]
["East Midlands",910036,"Grantham South 132/11kV S Stn",0.2,null,700,"",1,"Y"]
["East Midlands",910037,"Westborough 33/11kV S Stn",0.29699999999999999,null,425,"",3,"Y"]
["East Midlands",910038,"Bottesford 33/11kV S Stn",0.217,null,260,"",3,"Y"]
["East Midlands",910039,"Melton Mowbray 33/11kV S Stn",4.2999999999999997E-2,null,242,"",3,"Y"]
["East Midlands",910040,"Skillington 33/11kV S Stn",0.433,null,550,"",3,"Y"]
["East Midlands",910041,"Easton 33/11kV S Stn",0.113,null,90,"",3,"Y"]
["East Midlands",910042,"Tunnel Bank 33/11kV S Stn",0.17,null,340,"",3,"Y"]
["East Midlands",910043,"Old Dalby 33/11kV S Stn",0.26100000000000001,null,381,"",3,"Y"]
["East Midlands",910044,"Holwell 33/11kV S Stn",7.6999999999999999E-2,null,106,"",3,"Y"]
["East Midlands",910045,"Market Deeping 33/11kV S Stn",0.19,null,258,"",3,"Y"]
["East Midlands",910046,"West Deeping 33/11kV S Stn",0.41499999999999998,null,872,"",3,"Y"]
["East Midlands",910047,"Asfordby 132/11kV S Stn",9.5000000000000001E-2,null,185,"",1,"Y"]
["East Midlands",910048,"Market Overton 33/11kV S Stn",0.23200000000000001,null,282,"",3,"Y"]
["East Midlands",910049,"Regent Street 33/11kV S Stn",0.21,null,414,"",3,"Y"]
["East Midlands",910050,"Stamford 33/11kV S Stn",5.6000000000000001E-2,null,222,"",3,"Y"]
["East Midlands",910051,"Ketton Cement 33/11kV S Stn",0.17299999999999999,null,284,"",3,"Y"]
["East Midlands",910052,"Exton 33/11kV S Stn",0.52800000000000002,null,737,"",3,"Y"]
["East Midlands",910053,"Wittering 33/11kV S Stn",0.08,null,98,"",3,"Y"]
["East Midlands",910054,"Tinwell Road 33/11kV S Stn",0.17299999999999999,null,268,"",3,"Y"]
["East Midlands",910055,"Oakham 33/11kV S Stn",8.6999999999999994E-2,null,413,"",3,"Y"]
["East Midlands",910056,"Empingham 33/11kV S Stn",0.10100000000000001,null,148,"",3,"Y"]
["East Midlands",910057,"Uppingham 33/11kV S Stn",0.24399999999999999,null,435,"",3,"Y"]
["East Midlands",910058,"Leadenham 33/11kV S Stn",8.5999999999999993E-2,null,248,"",3,"Y"]
["East Midlands",916813,"Ermine Farm Solar Farm 33kV S Stn",0.16,null,500,"Y",3,"Y"]
["East Midlands",917435,"Deepdale Solar Farm 33kV S Stn",0.12,null,123,"",3,"Y"]
["East Midlands",917515,"The Grange Windfarm 33kV S Stn",5.1999999999999998E-2,null,81,"",3,"Y"]
["East Midlands",917543,"Nowhere Farm PV 33kV S Stn",0.05,null,60,"",3,"Y"]
["East Midlands",917572,"Decoy Farm Generation 33kV S Stn",0.251,null,314,"",3,"Y"]
["East Midlands",917574,"Horsemoor Drove Solar 33kV S Stn",0.06,null,121,"",3,"Y"]
["East Midlands",917592,"Copley Farm Solar Generation 33kV S Stn",0.15,null,290,"",3,"Y"]
["East Midlands",917647,"Mill Farm Solar Boothby Great Wood 33kV S Stn",0.21299999999999999,null,234,"",3,"Y"]
["East Midlands",917670,"French Farm Wind Farm 33kV S Stn",0.105,null,234,"",3,"Y"]
["East Midlands",917673,"Equitix ESI CHP Notts 33kV S Stn",0.13,null,323,"",3,"Y"]
["East Midlands",917678,"RAF Cranwell High G Facility 33kV S Stn",1.04,null,1372,"",3,"Y"]
["East Midlands",917757,"Mill Farm Battery Storage 33kV S Stn",0.57499999999999996,null,642,"",3,"Y"]
["East Midlands",917778,"North Rauceby 33kV S Stn",0.93,null,252,"",3,"Y"]
["East Midlands",920001,"Kibworth 33kV S Stn",9.5000000000000001E-2,null,319,"",3,"Y"]
["East Midlands",920002,"Loughborough 33kV S Stn",9.1999999999999998E-2,null,436,"",3,"Y"]
["East Midlands",920003,"Leicester North 33kV S Stn",0.1,null,113,"",3,"Y"]
["East Midlands",920004,"Leicester East 33kV S Stn",3.6999999999999998E-2,null,35,"",3,"Y"]
["East Midlands",920005,"Wigston 33kV S Stn",6.0999999999999999E-2,null,393,"",3,"Y"]
["East Midlands",920006,"Leicester 33kV S Stn",4.2999999999999997E-2,null,524,"",1,"Y"]
["East Midlands",920007,"Corby No2 33kV S Stn",7.3999999999999996E-2,null,1221,"",3,"Y"]
["East Midlands",920008,"Kettering 33kV S Stn",0.02,null,168,"",3,"Y"]
["East Midlands",920009,"Pytchley Road 33/11kV S Stn",7.5999999999999998E-2,null,131,"",3,"Y"]
["East Midlands",920010,"Wymington Wykes Generation 33kV S Stn",4.8000000000000001E-2,null,78,"",3,"Y"]
["East Midlands",920011,"Weldon Shanks Generation 33kV S Stn",0.74,null,1110,"",3,"Y"]
["East Midlands",920012,"Burton Wold Wind Farm Generation 33kV S Stn",0.13600000000000001,null,256,"",3,"Y"]
["East Midlands",920013,"Kettering North 33/11kV S Stn",5.8999999999999997E-2,null,142,"",3,"Y"]
["East Midlands",920016,"Wellingborough 132/11kV S Stn",4.4999999999999998E-2,null,217,"",1,"Y"]
["East Midlands",920017,"Wigston Magna 33/11kV S Stn",7.9000000000000001E-2,null,34,"",3,"Y"]
["East Midlands",920018,"British Gypsum 33/11kV S Stn",0.113,null,219,"",3,"Y"]
["East Midlands",920019,"Shepshed 33/11kV S Stn",0.08,null,154,"",3,"Y"]
["East Midlands",920020,"Loughborough 132/11kV S Stn",9.1999999999999998E-2,null,436,"",1,"Y"]
["East Midlands",920021,"Brush 33/11kV S Stn",0.09,null,176,"",3,"Y"]
["East Midlands",920022,"Quorn 33/11kV S Stn",0.20100000000000001,null,390,"",3,"Y"]
["East Midlands",920023,"Lero 33/6.6kV S Stn",0.09,null,166,"",3,"Y"]
["East Midlands",920024,"Mansfield Street 33/11kV S Stn",0.157,null,393,"",3,"Y"]
["East Midlands",920025,"Mountsorrel 33/11kV S Stn",0.192,null,369,"",3,"Y"]
["East Midlands",920026,"Beaumont Leys 33/11kV S Stn",0.13,null,275,"",3,"Y"]
["East Midlands",920027,"Groby Road 33/11kV S Stn",8.4000000000000005E-2,null,164,"",3,"Y"]
["East Midlands",920028,"Jupiter 33/11kV S Stn",7.4999999999999997E-2,null,153,"",3,"Y"]
["East Midlands",920029,"Birstall 33/11kV S Stn",7.6999999999999999E-2,null,182,"",3,"Y"]
["East Midlands",920030,"Leicester North 33/11kV S Stn",0.1,null,113,"",3,"Y"]
["East Midlands",920031,"Braunstone 33/11kV S Stn",9.2999999999999999E-2,null,55,"",3,"Y"]
["East Midlands",920032,"Redcross Street 33/11kV S Stn",9.7000000000000003E-2,null,148,"",3,"Y"]
["East Midlands",920033,"Leicester 33/11kV S Stn",4.2999999999999997E-2,null,524,"",1,"Y"]
["East Midlands",920034,"Thurmaston 33/11kV S Stn",5.6000000000000001E-2,null,110,"",3,"Y"]
["East Midlands",920035,"Syston 33/11kV S Stn",6.5000000000000002E-2,null,70,"",3,"Y"]
["East Midlands",920036,"Highfields 33/11kV S Stn",9.8000000000000004E-2,null,318,"",3,"Y"]
["East Midlands",920037,"Salutation 33/6.6kV S Stn",5.8000000000000003E-2,null,211,"",3,"Y"]
["East Midlands",920038,"Stoneygate 33/6.6kV S Stn",6.9000000000000006E-2,null,111,"",3,"Y"]
["East Midlands",920039,"Wigston 132/11kV S Stn",6.0999999999999999E-2,null,393,"",1,"Y"]
["East Midlands",920040,"Leicester East 33/6.6kV S Stn",3.6999999999999998E-2,null,35,"",3,"Y"]
["East Midlands",920041,"South Croxton 33/11kV S Stn",0.183,null,207,"",3,"Y"]
["East Midlands",920042,"Thurnby 33/11kV S Stn",5.1999999999999998E-2,null,140,"",3,"Y"]
["East Midlands",920043,"Kibworth 33/11kV S Stn",9.5000000000000001E-2,null,319,"",3,"Y"]
["East Midlands",920044,"Hamilton 33/11kV S Stn",7.8E-2,null,204,"",3,"Y"]
["East Midlands",920045,"Field Street 33/11kV S Stn",4.9000000000000002E-2,null,124,"",3,"Y"]
["East Midlands",920046,"Farndon Road 33/11kV S Stn",5.6000000000000001E-2,null,134,"",3,"Y"]
["East Midlands",920047,"Market Harborough 33/11kV S Stn",0.17,null,262,"",3,"Y"]
["East Midlands",920048,"Desborough 33/11kV S Stn",6.4000000000000001E-2,null,100,"",3,"Y"]
["East Midlands",920049,"Corby Central 33/11kV S Stn",0.151,null,313,"",3,"Y"]
["East Midlands",920050,"Hazelwood 33/11kV S Stn",0.13,null,2117,"",3,"Y"]
["East Midlands",920051,"Oakley 33/11kV S Stn",0.05,null,97,"",3,"Y"]
["East Midlands",920052,"Earlstrees 33/11kV S Stn",6.3E-2,null,118,"",3,"Y"]
["East Midlands",920053,"Corby No2 33/11kV S Stn",7.3999999999999996E-2,null,1221,"",3,"Y"]
["East Midlands",920054,"Burton Latimer 33/11kV S Stn",6.2E-2,null,106,"",3,"Y"]
["East Midlands",920055,"Oundle 33/11kV S Stn",0.28000000000000003,null,409,"",3,"Y"]
["East Midlands",920056,"Rushden 33/11kV S Stn",0.13800000000000001,null,236,"",3,"Y"]
["East Midlands",920057,"Sharnbrook 33/11kV S Stn",0.06,null,103,"",3,"Y"]
["East Midlands",920058,"Cannon Street 33/11kV S Stn",4.8000000000000001E-2,null,123,"",3,"Y"]
["East Midlands",920059,"Thrapston 33/11kV S Stn",0.22,null,420,"",3,"Y"]
["East Midlands",920060,"Little Irchester 33/11kV S Stn",0.14000000000000001,null,420,"",3,"Y"]
["East Midlands",920061,"Harrold 33/11kV S Stn",0.156,null,232,"",3,"Y"]
["East Midlands",920062,"Raunds 33/11kV S Stn",0.12,null,190,"",3,"Y"]
["East Midlands",920063,"Corby North 33kV S Stn",6.5000000000000002E-2,null,1049,"",3,"Y"]
["East Midlands",920064,"ABR Foods 33kV S Stn",0.36,null,734,"",3,"Y"]
["East Midlands",920065,"Park Farm 33/11kV S Stn",9.6000000000000002E-2,null,188,"",3,"Y"]
["East Midlands",920066,"Astrazeneca 33/11kV S Stn",9.2999999999999999E-2,null,180,"",3,"Y"]
["East Midlands",921092,"Irthlingborough 33/11kV S Stn",6.5000000000000002E-2,null,131,"",3,"Y"]
["East Midlands",923189,"Burton Wold Wind Farm South 33kV S Stn",0.16600000000000001,null,187,"",3,"Y"]
["East Midlands",925737,"Burton Wold North 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",926096,"Wymeswold Airfield PV Farm 33kV S Stn",0.1,null,148,"",3,"Y"]
["East Midlands",926100,"Rockingham Data Centre 33kV S Stn",0.25,null,408,"",3,"Y"]
["East Midlands",926142,"The Ridge Solar Park 33kV S Stn",8.6999999999999994E-2,null,235,"",3,"Y"]
["East Midlands",926144,"Hockley Farm Road 33/11kV S Stn",0.1,null,331,"",3,"Y"]
["East Midlands",926184,"Airfield Farm Windfarm 33kV S Stn",0.17,null,391,"",3,"Y"]
["East Midlands",926186,"New Albion Wind Farm 33kV S Stn",0.182,null,275,"",3,"Y"]
["East Midlands",926202,"Pipewell Road PV 33kV S Stn",0.13,null,202,"",3,"Y"]
["East Midlands",926220,"Ragdale PV Solar Park 33kV S Stn",9.7000000000000003E-2,null,106,"",3,"Y"]
["East Midlands",926237,"Chelveston Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",926242,"Glebe Farm Solar Park 33kV S Stn",0.08,null,52,"",3,"Y"]
["East Midlands",926263,"Kelmarsh Wind Farm 33kV S Stn",0.15,null,329,"",3,"Y"]
["East Midlands",926264,"Higham Ferrers Switching Station 33kV S Stn",0.27,null,331,"",3,"Y"]
["East Midlands",926300,"Wide Lane Wymeswold Solar Farm 33kV S Stn",7.2999999999999995E-2,null,164,"",3,"Y"]
["East Midlands",926308,"Sywell PV 33kV S Stn",0.193,null,122,"",3,"Y"]
["East Midlands",926349,"Irchester Road Switching Station 33kV S Stn",0.309,null,200,"",3,"Y"]
["East Midlands",926406,"Meadow Farm Solar 33kV S Stn",0.18,null,217,"",3,"Y"]
["East Midlands",926431,"Gypsum Solar Farm 33kV S Stn",0.08,null,112,"",3,"Y"]
["East Midlands",927000,"Chelveston Energy Park 33kV S Stn",0.12,null,211,"",3,"Y"]
["East Midlands",928000,"Irthlingborough 33kV S Stn",6.5000000000000002E-2,null,131,"",3,"Y"]
["East Midlands",930004,"Nuneaton 33kV S Stn",8.5000000000000006E-2,null,632,"",3,"Y"]
["East Midlands",930005,"Tamworth Town 33kV S Stn",3.4000000000000002E-2,null,217,"",3,"Y"]
["East Midlands",930006,"Rugby 33kV S Stn",4.2000000000000003E-2,null,361,"",3,"Y"]
["East Midlands",930007,"Warwick 33kV S Stn",4.1000000000000002E-2,null,274,"",3,"Y"]
["East Midlands",930008,"Whitley 33kV S Stn",7.0000000000000007E-2,null,574,"",3,"Y"]
["East Midlands",930009,"Coventry North 33kV S Stn",7.2999999999999995E-2,null,752,"",3,"Y"]
["East Midlands",930010,"Tamworth 33kV S Stn",4.7E-2,null,301,"",3,"Y"]
["East Midlands",930011,"Harbury 33kV S Stn",0.06,null,281,"",3,"Y"]
["East Midlands",930012,"Coventry South 33kV S Stn",5.7000000000000002E-2,null,553,"",3,"Y"]
["East Midlands",930013,"Coventry Central 33kV S Stn",9.2999999999999999E-2,null,331,"",3,"Y"]
["East Midlands",930014,"Coventry West 33kV S Stn",0.12,null,1161,"",3,"Y"]
["East Midlands",930015,"Tamworth Br 132/25kV S Stn",9.2999999999999999E-2,null,579,"",1,"Y"]
["East Midlands",930016,"Whitley 132/33kV S Stn",7.0000000000000007E-2,null,357,"",3,"Y"]
["East Midlands",930018,"Pailton 132/33kV S Stn",0.19,null,807,"",3,"Y"]
["East Midlands",930019,"Hinckley 33kV S Stn",0.159,null,872,"",3,"Y"]
["East Midlands",930020,"Coalville 33kV S Stn",0.109,null,382,"",3,"Y"]
["East Midlands",930021,"Rugby Portland Cement 33kV S Stn",4.2000000000000003E-2,null,361,"",3,"Y"]
["East Midlands",930025,"Coventry West 33/6.6kV S Stn",0.12,null,1161,"",3,"Y"]
["West Midlands",930026,"Courtaulds 33/6.6kV S Stn",0.13900000000000001,null,209,"",3,"Y"]
["East Midlands",930027,"London Road 33/6.6kV S Stn",8.4000000000000005E-2,null,82,"",3,"Y"]
["East Midlands",930028,"Hawkesmill Lane 33/6.6kV S Stn",0.152,null,269,"",3,"Y"]
["East Midlands",930029,"Jaguar Browns Lane 33/11kv S Stn",9.2999999999999999E-2,null,160,"",3,"Y"]
["East Midlands",930030,"Torrington Avenue 33/11kV S Stn",8.4000000000000005E-2,null,219,"",3,"Y"]
["East Midlands",930031,"Cox Street 33/6.6 Kv S Stn",9.0999999999999998E-2,null,224,"",3,"Y"]
["East Midlands",930032,"Coventry South 33/11kV S Stn",5.7000000000000002E-2,null,553,"",3,"Y"]
["East Midlands",930033,"Courthouse Green 33/11kV S Stn",0.127,null,70,"",3,"Y"]
["East Midlands",930034,"University Of Warwick 33/11kV S Stn",0.04,null,270,"",3,"Y"]
["East Midlands",930035,"Courthouse Green 33/6.6kV S Stn",0.127,null,70,"",3,"Y"]
["East Midlands",930036,"Coventry Colliery 33/11kV S Stn",0.13300000000000001,null,262,"",3,"Y"]
["East Midlands",930037,"Holyhead Road 33/11kV S Stn",5.1999999999999998E-2,null,90,"",3,"Y"]
["East Midlands",930038,"Holbrook Lane 33/6.6kV S Stn",0.04,null,73,"",3,"Y"]
["East Midlands",930039,"Dunlop 33/6.6kV S Stn",9.8000000000000004E-2,null,218,"",3,"Y"]
["East Midlands",930040,"Sandy Lane 33/6.6kV S Stn",6.4000000000000001E-2,null,100,"",3,"Y"]
["East Midlands",930041,"Spon Street 33/6.6kV S Stn",0.1,null,200,"",3,"Y"]
["East Midlands",930042,"Dillotford Avenue 33/11kV S Stn",6.7000000000000004E-2,null,162,"",3,"Y"]
["East Midlands",930043,"Gulson Road 33/6.6kV S Stn",9.8000000000000004E-2,null,206,"",3,"Y"]
["East Midlands",930044,"Copsewood 33/11kV S Stn",0.104,null,253,"",3,"Y"]
["East Midlands",930045,"Whitley 33/11kV S Stn",7.0000000000000007E-2,null,357,"",3,"Y"]
["East Midlands",930046,"Coventry North 33/11kV S Stn",7.2999999999999995E-2,null,752,"",3,"Y"]
["East Midlands",930047,"Walsgrave 33/11kV S Stn",0.16,null,128,"",3,"Y"]
["East Midlands",930048,"Claverdon 33/11kV S Stn",0.129,null,187,"",3,"Y"]
["East Midlands",930049,"Ryton 33/11kV S Stn",5.0999999999999997E-2,null,82,"",3,"Y"]
["East Midlands",930050,"Kenilworth 33/11kV S Stn",0.08,null,142,"",3,"Y"]
["East Midlands",930051,"Banbury Road 33/11kV S Stn",0.123,null,224,"",3,"Y"]
["East Midlands",930053,"Campion Hills 33/11kV S Stn",0.11700000000000001,null,220,"",3,"Y"]
["East Midlands",930054,"Wise Street 33/11kV S Stn",0.05,null,73,"",3,"Y"]
["East Midlands",930055,"Lawford 33/11kV S Stn",5.1999999999999998E-2,null,134,"",3,"Y"]
["East Midlands",930056,"Lockheed 33/11kV S Stn",0.11700000000000001,null,22,"",3,"Y"]
["East Midlands",930057,"Gaydon 33/11kV S Stn",0.28999999999999998,null,286,"",3,"Y"]
["East Midlands",930058,"Harbury 33/11kV S Stn",0.06,null,281,"",3,"Y"]
["East Midlands",930059,"Princethorpe 33/11kV S Stn",0.2,null,342,"",3,"Y"]
["East Midlands",930060,"Southam 33/11kV S Stn",0.10199999999999999,null,168,"",3,"Y"]
["East Midlands",930061,"Ansty 33/11kV S Stn",9.5000000000000001E-2,null,235,"",3,"Y"]
["East Midlands",930062,"Lutterworth 33/11kV S Stn",7.1999999999999995E-2,null,122,"",3,"Y"]
["East Midlands",930063,"English Electric 33/11kV S Stn",6.4000000000000001E-2,null,170,"",3,"Y"]
["East Midlands",930064,"Rugby 132/11kV S Stn",4.2000000000000003E-2,null,361,"",1,"Y"]
["East Midlands",930065,"Union Street 33/11kV S Stn",5.2999999999999999E-2,null,80,"",3,"Y"]
["East Midlands",930066,"Brownsover 33/11kV S Stn",0.151,null,411,"",3,"Y"]
["East Midlands",930067,"Hillmorton 33/11kV S Stn",7.0000000000000007E-2,null,182,"",3,"Y"]
["East Midlands",930068,"Apollo 33/11kV S Stn",0.107,null,261,"",3,"Y"]
["East Midlands",930069,"Coton Road 33/6.6kV S Stn",0.109,null,222,"",3,"Y"]
["East Midlands",930070,"Tamworth Town 132/11kV S Stn",3.4000000000000002E-2,null,217,"",1,"Y"]
["East Midlands",930071,"Tamworth Grid 33/11kV S Stn",4.7E-2,null,301,"",3,"Y"]
["East Midlands",930072,"Polesworth 33/11kV S Stn",0.11,null,259,"",3,"Y"]
["East Midlands",930073,"Wood End 33/11kV S Stn",0.16500000000000001,null,383,"",3,"Y"]
["East Midlands",930074,"Whittleford 33/11kV S Stn",8.2000000000000003E-2,null,162,"",3,"Y"]
["East Midlands",930076,"Atherstone 33/11kV S Stn",5.1999999999999998E-2,null,90,"",3,"Y"]
["East Midlands",930077,"Nuneaton 33/11kV S Stn",8.5000000000000006E-2,null,632,"",3,"Y"]
["East Midlands",930078,"Arley 33/11kV S Stn",0.14000000000000001,null,217,"",3,"Y"]
["East Midlands",930079,"Newdigate 33/11kV S Stn",0.23,null,390,"",3,"Y"]
["East Midlands",930080,"Gipsy Lane 33/11kV S Stn",6.8000000000000005E-2,null,122,"",3,"Y"]
["East Midlands",930081,"Langdale Drive 33/11kV S Stn",0.112,null,202,"",3,"Y"]
["East Midlands",930082,"Coventry Waste Reduction 33kV S Stn",8.6999999999999994E-2,null,232,"",3,"Y"]
["East Midlands",930083,"Coventry Arena 33/11kV S Stn",0.23,null,202,"",3,"Y"]
["East Midlands",930084,"Interlink Park 33/11 Kv S Stn",0.17100000000000001,null,380,"",3,"Y"]
["East Midlands",930086,"Churchover 33/11kV S Stn",0.19,null,190,"",3,"Y"]
["East Midlands",930087,"Tournament Fields 33/11kV S Stn",0.95,null,441,"",3,"Y"]
["East Midlands",930088,"Middlefield 33/11kV S Stn",0.19700000000000001,null,388,"",3,"Y"]
["East Midlands",930089,"Sapcote 33/11kV S Stn",0.13300000000000001,null,254,"",3,"Y"]
["East Midlands",930090,"Gec Test Bed Whetstone 33kV S Stn",0.33,null,521,"",3,"Y"]
["East Midlands",930091,"Bardon 33/11kV S Stn",0.25700000000000001,null,540,"",3,"Y"]
["East Midlands",930092,"Coalville 33/11kV S Stn",0.109,null,382,"",3,"Y"]
["East Midlands",930093,"Desford 33/11kV S Stn",0.111,null,216,"",3,"Y"]
["East Midlands",930094,"Caterpillar Desford 33/11kV S Stn",0.109,null,124,"",3,"Y"]
["East Midlands",930095,"Alliance & Leicester 33/11kV S Stn",0.17,null,357,"",3,"Y"]
["East Midlands",930096,"Whetstone 33/11kV S Stn",7.1999999999999995E-2,null,142,"",3,"Y"]
["East Midlands",930097,"Nailstone 33/11kV S Stn",0.49399999999999999,null,935,"",3,"Y"]
["East Midlands",930098,"Mantle Lane 33/11kV S Stn",0.05,null,80,"",3,"Y"]
["East Midlands",930099,"Barwell 33/11kV S Stn",0.27100000000000002,null,473,"",3,"Y"]
["East Midlands",930100,"Osbaston 33/11kV S Stn",0.35,null,603,"",3,"Y"]
["East Midlands",930101,"Ashby De La Zouch 33/11kV S Stn",0.107,null,198,"",3,"Y"]
["East Midlands",930102,"Moira 33/11kV S Stn",0.14599999999999999,null,283,"",3,"Y"]
["East Midlands",930103,"Hinckley 132/11kV S Stn",0.159,null,872,"",1,"Y"]
["East Midlands",930104,"Worthington 33/11kV S Stn",0.253,null,314,"",3,"Y"]
["East Midlands",930105,"Bruntingthorpe 33/11kV S Stn",0.21,null,276,"",3,"Y"]
["East Midlands",930107,"Magna Park 33/11kV S Stn",0.127,null,245,"",3,"Y"]
["East Midlands",938836,"Rugby Gateway 33/11kV S Stn",0.25,null,265,"",3,"Y"]
["East Midlands",938992,"Low Spinney Wind Farm 33kV S Stn",0.1,null,140,"",3,"Y"]
["East Midlands",939003,"Swinford Windfarm 33kV S Stn",0.192,null,536,"",3,"Y"]
["East Midlands",939062,"Wood Lane 33/11kV S Stn",0.2,null,226,"",3,"Y"]
["East Midlands",939122,"Hall Farm Newbold Verdon 33kV S Stn",0.22500000000000001,null,338,"",3,"Y"]
["East Midlands",939140,"Atherstone Solar Farm 33kV S Stn",0.215,null,381,"",3,"Y"]
["East Midlands",939146,"Babelake St Packington 33kv S Stn",0.2,null,248,"",3,"Y"]
["East Midlands",939150,"Prestop Fm Burton Rd Ashby 33kv S Stn",0.129,null,500,"Y",3,"Y"]
["East Midlands",939156,"Elms Farm Southam Solar Farm 33kV S Stn",0.2,null,290,"",3,"Y"]
["East Midlands",939208,"Pebble Hall Generation 33kV S Stn",0.182,null,355,"",3,"Y"]
["East Midlands",939242,"Fields Farm Southam Solar Farm 33kV S Stn",0.1,null,138,"",3,"Y"]
["East Midlands",939263,"Lindridge Farm Solar Park 33kV S Stn",0.13700000000000001,null,278,"",3,"Y"]
["East Midlands",939300,"Victoria Road PV Ellistown 33kV S Stn",7.2999999999999995E-2,null,238,"",3,"Y"]
["East Midlands",939301,"Fosse Way Radford Semele Solar Farm 33kV S Stn",0.08,null,100,"",3,"Y"]
["East Midlands",939305,"Jaguar Land Rover 33/11kV S Stn",0.28999999999999998,null,286,"",3,"Y"]
["East Midlands",939417,"Baddesley Energy Park 33kV S Stn",0.30599999999999999,null,727,"",3,"Y"]
["East Midlands",939424,"Wellesbourne 33/11kV S Stn",0.2,null,421,"",3,"Y"]
["East Midlands",939476,"Hill Farm Battery Generation 33kV S Stn",0.38700000000000001,null,617,"",3,"Y"]
["East Midlands",939482,"JLR Whitley 33/11kV S Stn",0.7,null,340,"",3,"Y"]
["East Midlands",939800,"Birch Coppice 33/11kv S Stn",0.13300000000000001,null,189,"",3,"Y"]
["East Midlands",940005,"Stony Stratford 33kV S Stn",9.1999999999999998E-2,null,1074,"",3,"Y"]
["East Midlands",940006,"Bradwell Abbey 33kV S Stn",9.4E-2,null,486,"",3,"Y"]
["East Midlands",940008,"Daventry 33kV S Stn",4.4999999999999998E-2,null,147,"",3,"Y"]
["East Midlands",940009,"Northampton 33kV S Stn",5.2999999999999999E-2,null,570,"",3,"Y"]
["East Midlands",940010,"Northampton East 33kV S Stn",0.09,null,637,"",3,"Y"]
["East Midlands",940011,"Wellingborough 33kV S Stn",4.4999999999999998E-2,null,217,"",3,"Y"]
["East Midlands",940012,"Northampton West 33kV S Stn",5.2999999999999999E-2,null,375,"",3,"Y"]
["East Midlands",940013,"Bletchley 33kV S Stn",2.7E-2,null,166,"",3,"Y"]
["East Midlands",940015,"Wolverton 132/25kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
["East Midlands",940017,"Shanks Generation 33kV S Stn",0.06,null,68,"",3,"Y"]
["East Midlands",940020,"Bletchley Landfill 33kV S Stn",0.192,null,416,"",3,"Y"]
["East Midlands",940021,"Pineham 33/11kV S Stn",0.22800000000000001,null,392,"",3,"Y"]
["East Midlands",940022,"Hanslope Park 33/11kV S Stn",0.13100000000000001,null,192,"",3,"Y"]
["East Midlands",940023,"Fen Farm 33/11kV S Stn",9.0999999999999998E-2,null,194,"",3,"Y"]
["East Midlands",940024,"Petsoe Manor Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",940025,"Secklow Gate 33/11kV S Stn",6.3E-2,null,137,"",3,"Y"]
["East Midlands",940026,"Thenford 33/11kV S Stn",0.59,null,965,"",3,"Y"]
["East Midlands",940027,"Woodford Halse 33/11kV S Stn",8.5999999999999993E-2,null,157,"",3,"Y"]
["East Midlands",940028,"Brackley Town 33/11kV S Stn",4.1000000000000002E-2,null,80,"",3,"Y"]
["East Midlands",940029,"Buckingham 33/11kV S Stn",6.7000000000000004E-2,null,99,"",3,"Y"]
["East Midlands",940030,"Calvert 33/11kV S Stn",0.111,null,173,"",3,"Y"]
["East Midlands",940031,"Towcester 33/11kV S Stn",6.9000000000000006E-2,null,98,"",3,"Y"]
["East Midlands",940032,"Silverstone 33/11kV S Stn",0.19400000000000001,null,198,"",3,"Y"]
["East Midlands",940033,"Wicken 33/11kV S Stn",0.45,null,878,"",3,"Y"]
["East Midlands",940034,"Kiln Farm 33/11kV S Stn",3.5000000000000003E-2,null,93,"",3,"Y"]
["East Midlands",940035,"Winslow 33/11kV S Stn",8.3000000000000004E-2,null,160,"",3,"Y"]
["East Midlands",940036,"Wolverton 33/11kV S Stn",6.8000000000000005E-2,null,351,"",3,"Y"]
["East Midlands",940037,"Marlborough Street 33/11kV S Stn",8.1000000000000003E-2,null,230,"",3,"Y"]
["East Midlands",940038,"Portway 33/11kV S Stn",3.3000000000000002E-2,null,65,"",3,"Y"]
["East Midlands",940039,"Childs Way 33/11kV S Stn",0.05,null,125,"",3,"Y"]
["East Midlands",940040,"Newton Road 33/11kV S Stn",0.109,null,167,"",3,"Y"]
["East Midlands",940041,"Newport Pagnell 33/11kV S Stn",0.13100000000000001,null,271,"",3,"Y"]
["East Midlands",940042,"Bletchley 33/11kV S Stn",2.7E-2,null,166,"",3,"Y"]
["East Midlands",940043,"Fox Milne 33/11kV S Stn",4.1000000000000002E-2,null,47,"",3,"Y"]
["East Midlands",940044,"Victoria Road 33/11kV S Stn",8.3000000000000004E-2,null,125,"",3,"Y"]
["East Midlands",940045,"Olney 33/11kV S Stn",0.09,null,137,"",3,"Y"]
["East Midlands",940046,"Wavendon Gate 33/11kV S Stn",0.04,null,78,"",3,"Y"]
["East Midlands",940047,"Braunston Road 33/11kV S Stn",9.8000000000000004E-2,null,245,"",3,"Y"]
["East Midlands",940048,"Welton 33/11kV S Stn",0.13100000000000001,null,262,"",3,"Y"]
["East Midlands",940049,"Daventry 33/11kV S Stn",4.4999999999999998E-2,null,147,"",3,"Y"]
["East Midlands",940050,"Weedon 33/11kV S Stn",0.10100000000000001,null,164,"",3,"Y"]
["East Midlands",940051,"West Haddon 33/11kV S Stn",0.33200000000000002,null,637,"",3,"Y"]
["East Midlands",940052,"Bugbrooke 33/11kV S Stn",0.104,null,151,"",3,"Y"]
["East Midlands",940053,"Earls Barton 33/11kV S Stn",0.15,null,267,"",3,"Y"]
["East Midlands",940054,"Northampton West 33/11kV S Stn",5.2999999999999999E-2,null,43,"",3,"Y"]
["East Midlands",940055,"Ellesmere Avenue 33/11kV S Stn",0.121,null,227,"",3,"Y"]
["East Midlands",940056,"Chapel Brampton 33/11kV S Stn",8.3000000000000004E-2,null,128,"",3,"Y"]
["East Midlands",940057,"Abington 33/11kV S Stn",0.14000000000000001,null,334,"",3,"Y"]
["East Midlands",940058,"Banbury Lane 33/11kV S Stn",0.56999999999999995,null,96,"",3,"Y"]
["East Midlands",940059,"Campbell Street 33/11kV S Stn",0.152,null,391,"",3,"Y"]
["East Midlands",940060,"Kingsthorpe 33/11kV S Stn",0.11899999999999999,null,223,"",3,"Y"]
["East Midlands",940061,"Northampton 33/11kV S Stn",5.2999999999999999E-2,null,570,"",3,"Y"]
["East Midlands",940062,"Wootton 33/11kV S Stn",0.14000000000000001,null,140,"",3,"Y"]
["East Midlands",940063,"Roade 33/11kV S Stn",0.111,null,179,"",3,"Y"]
["East Midlands",940064,"Wellingborough Road 33/11kV S Stn",0.05,null,970,"",3,"Y"]
["East Midlands",940065,"Boothville 33/11kV S Stn",0.06,null,138,"",3,"Y"]
["East Midlands",940066,"Denton 33/11kV S Stn",0.28000000000000003,null,425,"",3,"Y"]
["East Midlands",940067,"Campbell Park 33/11kV S Stn",0.05,null,75,"",3,"Y"]
["East Midlands",940068,"Crick 33/11kV S Stn",8.2000000000000003E-2,null,158,"",3,"Y"]
["East Midlands",940069,"Shenley Wood 33/11kV S Stn",6.4000000000000001E-2,null,124,"",3,"Y"]
["East Midlands",940070,"Kingston 33/11kV S Stn",0.06,null,136,"",3,"Y"]
["East Midlands",940071,"Eldergate 33/11kV S Stn",0.05,null,75,"",3,"Y"]
["East Midlands",940072,"Brackmills 33/11kV S Stn",0.06,null,160,"",3,"Y"]
["East Midlands",945510,"Beachampton Solar Farm 33kV S Stn",7.0000000000000007E-2,null,105,"",3,"Y"]
["East Midlands",945674,"Roade Wind Farm 33kV S Stn",0.12,null,194,"",3,"Y"]
["East Midlands",945675,"Maxwell House Data Centre 33/11kV S Stn",0.23,null,208,"",3,"Y"]
["East Midlands",945726,"Turweston Airfield Solar Farm 33kV S Stn",0.1,null,126,"",3,"Y"]
["East Midlands",945977,"Watford Lodge Windfarm 33kV S Stn",0.13,null,250,"",3,"Y"]
["East Midlands",945978,"Winwick Windfarm 33kV S Stn",0.13,null,145,"",3,"Y"]
["East Midlands",946045,"Northampton East 33/11kV S Stn",0.09,null,637,"",3,"Y"]
["East Midlands",946060,"Whittlebury Road PV 33kV S Stn",6.3E-2,null,56,"",3,"Y"]
["East Midlands",946091,"Yelvertoft Windfarm 33kV S Stn",0.2,null,135,"",3,"Y"]
["East Midlands",946100,"Brackley 33kV S Stn",0.1,null,637,"",3,"Y"]
["East Midlands",946139,"Hartwell Road 33kV S Stn",6.9000000000000006E-2,null,142,"",3,"Y"]
["East Midlands",946140,"Eakley Lanes North PV 33kV S Stn",0.152,null,156,"",3,"Y"]
["East Midlands",946141,"Eakley Lanes South PV 33kV S Stn",7.0000000000000007E-2,null,72,"",3,"Y"]
["East Midlands",946154,"Gawcott Fields Solar Park 33kV S Stn",7.4999999999999997E-2,null,69,"",3,"Y"]
["East Midlands",946165,"Lilbourne Wind Farm 33kV S Stn",0.18,null,257,"",3,"Y"]
["East Midlands",946174,"Mount Mill Solar Park 33kV S Stn",0.09,null,203,"",3,"Y"]
["East Midlands",946176,"Homestead Solar Park 33kV S Stn",0.27100000000000002,null,306,"",3,"Y"]
["East Midlands",946180,"Handley Park Solar Park 33kv S Stn",0.11,null,109,"",3,"Y"]
["East Midlands",946198,"Littlewood Farm Solar 33kV S Stn",0.28000000000000003,null,101,"",3,"Y"]
["East Midlands",946213,"Emberton Pv 33kv S Stn",9.6000000000000002E-2,null,108,"",3,"Y"]
["East Midlands",946240,"Greatmoor Efw Calvert 33kv S Stn",0.05,null,154,"",3,"Y"]
["East Midlands",946268,"Tattenhoe 33/11kV S Stn",0.13,null,420,"",3,"Y"]
["East Midlands",946270,"Manor Farm PV Horton 33kV S Stn",0.11,null,165,"",3,"Y"]
["East Midlands",946271,"Thornborough Grounds Pv 33kv S Stn",0.20699999999999999,null,261,"",3,"Y"]
["East Midlands",946276,"Brafield On The Green PV 33kv S Stn",0.16300000000000001,null,263,"",3,"Y"]
["East Midlands",946329,"Olney Hyde Farm Solar 33kV S Stn",8.8999999999999996E-2,null,137,"",3,"Y"]
["East Midlands",946411,"Lyon Road Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
["East Midlands",947000,"Brackley 33/11kV S Stn",0.1,null,637,"",3,"Y"]

{"sheet":"Source-Name","index":13,"n_rows":1990,"n_cols":10,"rows_kept":1990,"cut":false,"hidden":true,"merged":[]}
[null,null,1,2,3,4,5,6,7,8]
["AREA","SUBSTATION_NAME","SUBSTATION_NAME_TRUNC","SUBSTATION_NUMBER","ZE","Assumed ZE","UE","Assumed UE","t","Assumed t"]
["South West","Aaronsons 33kV S Stn","Aaronsons33kVSStn",260580,0.32,null,322,"",3,"Y"]
["South West","Abbeywood 33/11kV S Stn","Abbeywood33/11kVSStn",113884,0.77900000000000003,null,265,"",3,"Y"]
["South Wales","Aberaeron 33/11kV S Stn","Aberaeron33/11kVSStn",590052,0.59,null,500,"Y",3,"Y"]
["South Wales","Aberaman Industrial No.1 33kV S Stn","AberamanIndustrialNo.133kVSStn",550384,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Aberaman Park 33kV S Stn","AberamanPark33kVSStn",550313,0.63700000000000001,null,500,"Y",3,"Y"]
["South Wales","Abercrave 33/11kV S Stn","Abercrave33/11kVSStn",560053,0.92,null,500,"Y",3,"Y"]
["South Wales","Aberdare 33/11kV S Stn","Aberdare33/11kVSStn",550267,0.13,null,500,"Y",3,"Y"]
["South Wales","Abergavenny 132/66kV S Stn","Abergavenny132/66kVSStn",530001,7.8E-2,null,271,null,1,"Y"]
["South Wales","Abergelli PV Generation Site 33kV S Stn","AbergelliPVGenerationSite33kVSStn",520381,0.36,null,500,"Y",3,"Y"]
["South Wales","Aberpergwm 33/11kV S Stn","Aberpergwm33/11kVSStn",560055,0.30199999999999999,null,500,"Y",3,"Y"]
["South Wales","Abersychan 66/11kV S Stn","Abersychan66/11kVSStn",530056,0.20599999999999999,null,244,null,3,"Y"]
["South Wales","Aberthaw Power Station 275/132kV S Stn","AberthawPowerStation275/132kVSStn",510049,0.2,"Y",2152,"",1,"Y"]
["South Wales","Abertillery 33/11kV S Stn","Abertillery33/11kVSStn",550060,0.16400000000000001,null,500,"Y",3,"Y"]
["South Wales","Abertysswg 33/11kV S Stn","Abertysswg33/11kVSStn",550061,0.1111,null,500,"Y",3,"Y"]
["South West","Abham 400/132kV S Stn","Abham400/132kVSStn",306004,0.2,"Y",6635,"",1,"Y"]
["East Midlands","Abington 33/11kV S Stn","Abington33/11kVSStn",940057,0.14000000000000001,null,334,"",3,"Y"]
["East Midlands","ABR Foods 33kV S Stn","ABRFoods33kVSStn",920064,0.36,null,734,"",3,"Y"]
["West Midlands","Abson 33kV S Stn","Abson33kVSStn",670084,0.25900000000000001,null,328,"",3,"Y"]
["East Midlands","Acreage Lane 33/11kV S Stn","AcreageLane33/11kVSStn",890035,0.59599999999999997,null,1173,"",3,"Y"]
["West Midlands","Actrees Solar Farm 33kV S Stn","ActreesSolarFarm33kVSStn",795720,7.6999999999999999E-2,null,105,"",3,"Y"]
["South West","Adelaide Road 33/11kV S Stn","AdelaideRoad33/11kVSStn",330014,0.47,null,85,"",3,"Y"]
["South Wales","Afan Way Stor Generation 33kV S Stn","AfanWayStorGeneration33kVSStn",560440,0.11700000000000001,null,500,"Y",3,"Y"]
["East Midlands","Airfield Farm Windfarm 33kV S Stn","AirfieldFarmWindfarm33kVSStn",926184,0.17,null,391,"",3,"Y"]
["West Midlands","Air Liquide 132kV S Stn","AirLiquide132kVSStn",670161,0.2,"Y",1000,"Y",1,"Y"]
["West Midlands","Albrighton 33/11kV S Stn","Albrighton33/11kVSStn",670122,0.16,null,200,"",3,"Y"]
["South West","Alcombe 33/11kV S Stn","Alcombe33/11kVSStn",210190,0.107,null,103,"",3,"Y"]
["South West","Alders Way STOR 33kV S Stn","AldersWaySTOR33kVSStn",348182,0.42799999999999999,null,500,"Y",3,"Y"]
["West Midlands","Alderton 66/11kV S Stn","Alderton66/11kVSStn",670088,0.13,null,179,"",3,"Y"]
["West Midlands","Aldridge 33/6.6kV S Stn","Aldridge33/6.6kVSStn",670125,6.2E-2,null,133,"",3,"Y"]
["South West","Alexandra Road 33/11kV S Stn","AlexandraRoad33/11kVSStn",330018,0.36,null,113,"",3,"Y"]
["East Midlands","Alford 33/11kV S Stn","Alford33/11kVSStn",900014,0.26500000000000001,null,441,"",3,"Y"]
["East Midlands","Alfreton 132/33kV S Stn","Alfreton132/33kVSStn",680037,0.193,null,752,"",3,"Y"]
["East Midlands","Alfreton 33kV S Stn","Alfreton33kVSStn",890014,0.193,null,752,"",3,"Y"]
["East Midlands","Allenton 33/11kV S Stn","Allenton33/11kVSStn",870043,8.1000000000000003E-2,null,229,"",3,"Y"]
["South West","Aller Court Solar Farm 33kV S Stn","AllerCourtSolarFarm33kVSStn",218071,0.17,null,500,"Y",3,"Y"]
["East Midlands","Alliance & Leicester 33/11kV S Stn","Alliance&Leicester33/11kVSStn",930095,0.17,null,357,"",3,"Y"]
["South West","Alma Road 33/11kV S Stn","AlmaRoad33/11kVSStn",330020,0.16500000000000001,null,244,"",3,"Y"]
["South West","Almondsbury 33/11kV S Stn","Almondsbury33/11kVSStn",111935,0.121,null,143,"",3,"Y"]
["South West","Alverdiscott 400/132kV S Stn","Alverdiscott400/132kVSStn",206001,0.2,"Y",2028,"",1,"Y"]
["South West","Alverdiscott Wind Farm 33kV S Stn","AlverdiscottWindFarm33kVSStn",358079,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Alveston 33/11kV S Stn","Alveston33/11kVSStn",790008,1.1000000000000001,null,1716,"",3,"Y"]
["East Midlands","Ambergate 33/11kV S Stn","Ambergate33/11kVSStn",890077,6.5000000000000002E-2,null,75,"",3,"Y"]
["South Wales","Ammanford Grid 132/33kV S Stn","AmmanfordGrid132/33kVSStn",520002,0.41699999999999998,null,1000,"Y",3,"Y"]
["East Midlands","Anderson Lane 33/11kV S Stn","AndersonLane33/11kVSStn",900032,0.121,null,369,"",3,"Y"]
["East Midlands","Annesley 132/33kV S Stn","Annesley132/33kVSStn",680011,8.2000000000000003E-2,null,370,"",3,"Y"]
["East Midlands","Annesley 33/11kV S Stn","Annesley33/11kVSStn",890033,8.2000000000000003E-2,null,370,"",3,"Y"]
["East Midlands","Annesley 33kV S Stn","Annesley33kVSStn",890007,8.2000000000000003E-2,null,370,"",3,"Y"]
["East Midlands","Ansty 33/11kV S Stn","Ansty33/11kVSStn",930061,9.5000000000000001E-2,null,235,"",3,"Y"]
["East Midlands","Apollo 33/11kV S Stn","Apollo33/11kVSStn",930068,0.107,null,261,"",3,"Y"]
["South Wales","Argoed Tregaron 33/11kV S Stn","ArgoedTregaron33/11kVSStn",590246,3.3,null,500,"Y",3,"Y"]
["East Midlands","Arkwright Solar 33kV S Stn","ArkwrightSolar33kVSStn",898436,0.49,null,821,"",3,"Y"]
["East Midlands","Arley 33/11kV S Stn","Arley33/11kVSStn",930078,0.14000000000000001,null,217,"",3,"Y"]
["West Midlands","Arley 33kV S Stn","Arley33kVSStn",670107,1.79,null,1545,"",3,"Y"]
["South West","Armada Street 33/11kV S Stn","ArmadaStreet33/11kVSStn",330021,0.27,null,113,"",3,"Y"]
["East Midlands","Arnold 33/11kV S Stn","Arnold33/11kVSStn",880027,0.16700000000000001,null,326,"",3,"Y"]
["East Midlands","Asfordby 132/11kV S Stn","Asfordby132/11kVSStn",910047,9.5000000000000001E-2,null,185,"",1,"Y"]
["East Midlands","Asfordby 132kV S Stn","Asfordby132kVSStn",690034,9.5000000000000001E-2,null,185,"",1,"Y"]
["East Midlands","Ashbourne 33/11kV S Stn","Ashbourne33/11kVSStn",870030,0.125,null,230,"",3,"Y"]
["South West","Ashburton 33/11kV S Stn","Ashburton33/11kVSStn",340013,0.34,null,481,"",3,"Y"]
["East Midlands","Ashby De La Zouch 33/11kV S Stn","AshbyDeLaZouch33/11kVSStn",930101,0.107,null,198,"",3,"Y"]
["South West","Ashcombe Solar Park 33kV S Stn","AshcombeSolarPark33kVSStn",348132,6.6000000000000003E-2,null,500,"Y",3,"Y"]
["East Midlands","Asher Lane STOR 33kV S Stn","AsherLaneSTOR33kVSStn",898663,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Ashgrove 33/11kV S Stn","Ashgrove33/11kVSStn",510064,0.7,"Y",500,"Y",3,"Y"]
["South West","Ashlawn Farm Solar Park 33kV S Stn","AshlawnFarmSolarPark33kVSStn",188123,8.5000000000000006E-2,null,500,"Y",3,"Y"]
["South West","Ashwater 33/11kV S Stn","Ashwater33/11kVSStn",350022,2.8330000000000002,null,3043,"",3,"Y"]
["South West","Ashwater Solar Park 33kV S Stn","AshwaterSolarPark33kVSStn",358160,0.5,null,500,"Y",3,"Y"]
["West Midlands","Astley Solar Farm 33kv S Stn","AstleySolarFarm33kvSStn",779071,0.47,null,351,"",3,"Y"]
["East Midlands","Aston House Solar Farm 33kV S Stn","AstonHouseSolarFarm33kVSStn",874987,0.23499999999999999,null,291,"",3,"Y"]
["East Midlands","Astrazeneca 33/11kV S Stn","Astrazeneca33/11kVSStn",920066,9.2999999999999999E-2,null,180,"",3,"Y"]
["South West","Astrazeneca 33/11kV S Stn","Astrazeneca33/11kVSStn",114258,0.47,null,348,"",3,"Y"]
["South West","Athelstan Road 33/11kV S Stn","AthelstanRoad33/11kVSStn",310020,0.2,null,261,"",3,"Y"]
["East Midlands","Atherstone 33/11kV S Stn","Atherstone33/11kVSStn",930076,5.1999999999999998E-2,null,90,"",3,"Y"]
["East Midlands","Atherstone Solar Farm 33kV S Stn","AtherstoneSolarFarm33kVSStn",939140,0.215,null,381,"",3,"Y"]
["East Midlands","Averill Solar Farm 33kV S Stn","AverillSolarFarm33kVSStn",898444,0.13,null,150,"",3,"Y"]
["South West","Avonmouth 33/11kV S Stn","Avonmouth33/11kVSStn",113368,7.0000000000000007E-2,null,109,"",3,"Y"]
["South West","Avonmouth Biogas 33kV S Stn","AvonmouthBiogas33kVSStn",114652,0.183,null,500,"Y",3,"Y"]
["South West","Avonmouth BSP 132/33kV S Stn","AvonmouthBSP132/33kVSStn",113367,1.4999999999999999E-2,null,92,"",3,"Y"]
["South West","Avonmouth Docks 33/6.6kV S Stn","AvonmouthDocks33/6.6kVSStn",113277,0.08,null,119,"",3,"Y"]
["South West","Avonmouth Wind Farm 33kV S Stn","AvonmouthWindFarm33kVSStn",118093,8.5000000000000006E-2,null,500,"Y",3,"Y"]
["South West","Axbridge 33/11kV S Stn","Axbridge33/11kVSStn",180017,0.19,null,281,"",3,"Y"]
["South West","Axe View Solar Farm 33kV S Stn","AxeViewSolarFarm33kVSStn",258174,3.1E-2,null,500,"Y",3,"Y"]
["South West","Axminster 33/11kV S Stn","Axminster33/11kVSStn",250280,0.11600000000000001,null,196,"",3,"Y"]
["South West","Axminster GSP 400/132kV S Stn","AxminsterGSP400/132kVSStn",206006,0.2,"Y",2096,"",1,"Y"]
["South West","Ayshford Court Farm Solar Park 33kV S Stn","AyshfordCourtFarmSolarPark33kVSStn",318035,0.17499999999999999,null,500,"Y",3,"Y"]
["East Midlands","Babelake St Packington 33kv S Stn","BabelakeStPackington33kvSStn",939146,0.2,null,248,"",3,"Y"]
["East Midlands","Baddesley Energy Park 33kV S Stn","BaddesleyEnergyPark33kVSStn",939417,0.30599999999999999,null,727,"",3,"Y"]
["South Wales","Baglan Bay PV Generation 33kV S Stn","BaglanBayPVGeneration33kVSStn",560336,0.44,null,500,"Y",3,"Y"]
["East Midlands","Bakewell 33/11kV S Stn","Bakewell33/11kVSStn",890065,0.3,null,268,"",3,"Y"]
["South West","Balls Wood Solar Park 33kV S Stn","BallsWoodSolarPark33kVSStn",338120,0.28899999999999998,null,500,"Y",3,"Y"]
["East Midlands","Bambers Farm Wind Generation 33kV S Stn","BambersFarmWindGeneration33kVSStn",900008,0.2,null,272,"",3,"Y"]
["West Midlands","Banbury 132/11kV S Stn","Banbury132/11kVSStn",670045,6.6000000000000003E-2,null,211,"",1,"Y"]
["East Midlands","Banbury Lane 33/11kV S Stn","BanburyLane33/11kVSStn",940058,0.56999999999999995,null,96,"",3,"Y"]
["East Midlands","Banbury Road 33/11kV S Stn","BanburyRoad33/11kVSStn",930051,0.123,null,224,"",3,"Y"]
["East Midlands","Bardon 33/11kV S Stn","Bardon33/11kVSStn",930091,0.25700000000000001,null,540,"",3,"Y"]
["South Wales","Bargoed Solar Park 33kV S Stn","BargoedSolarPark33kVSStn",550416,0.44,null,500,"Y",3,"Y"]
["West Midlands","Barlaston 132kV S Stn","Barlaston132kVSStn",680027,0.2,"Y",1000,"Y",1,"Y"]
["South West","Barnstaple 132/33/11kV S Stn","Barnstaple132/33/11kVSStn",260467,6.2E-2,null,93,"",3,"Y"]
["South West","Barnstaple Quay 33/11kV S Stn","BarnstapleQuay33/11kVSStn",260250,0.1,null,115,"",3,"Y"]
["South Wales","Barry Dock Biomass 33kV S Stn","BarryDockBiomass33kVSStn",510429,0.10299999999999999,null,500,"Y",3,"Y"]
["West Midlands","Bartley Green 132/11kV S Stn","BartleyGreen132/11kVSStn",670138,9.2999999999999999E-2,null,1038,"",1,"Y"]
["South West","Barton 33/11kV S Stn","Barton33/11kVSStn",340024,0.58099999999999996,null,109,"",3,"Y"]
["West Midlands","Barton Abrasives 33/11kV S Stn","BartonAbrasives33/11kVSStn",670148,0.151,null,831,"",3,"Y"]
["South West","Barton Hill STOR Generator 33kV S Stn","BartonHillSTORGenerator33kVSStn",348178,0.41,null,500,"Y",3,"Y"]
["East Midlands","Barton Under Needwood 33/11kV S Stn","BartonUnderNeedwood33/11kVSStn",870013,0.16500000000000001,null,185,"",3,"Y"]
["East Midlands","Barwell 33/11kV S Stn","Barwell33/11kVSStn",930099,0.27100000000000002,null,473,"",3,"Y"]
["South West","Bath Dolemeads 132/33/6.6kV S Stn","BathDolemeads132/33/6.6kVSStn",164087,7.1999999999999995E-2,null,68,"",3,"Y"]
["South West","Batheaston 33/6.6kV S Stn","Batheaston33/6.6kVSStn",160389,4.3999999999999997E-2,null,59,"",3,"Y"]
["South West","Bath Road 33/11kV S Stn","BathRoad33/11kVSStn",210160,0.06,null,90,"",3,"Y"]
["South West","Batsworthy Cross Wind Farm 33kV S Stn","BatsworthyCrossWindFarm33kVSStn",318152,0.49,null,500,"Y",3,"Y"]
["West Midlands","Battlefield Generation 33kV S Stn","BattlefieldGeneration33kVSStn",840698,0.14000000000000001,null,98,"",3,"Y"]
["West Midlands","Bayston Hill 33/11kV S Stn","BaystonHill33/11kVSStn",840013,0.26,null,494,"",3,"Y"]
["East Midlands","Beachampton Solar Farm 33kV S Stn","BeachamptonSolarFarm33kVSStn",945510,7.0000000000000007E-2,null,105,"",3,"Y"]
["South West","Beaford Solar Farm 33kV S Stn","BeafordSolarFarm33kVSStn",268005,0.375,null,500,"Y",3,"Y"]
["South West","Beaminster 33/11kV S Stn","Beaminster33/11kVSStn",250620,0.439,null,358,"",3,"Y"]
["South West","Bears Down Wind Farm 33kV S Stn","BearsDownWindFarm33kVSStn",437150,0.55000000000000004,null,282,"",3,"Y"]
["West Midlands","Bearstone 33/11kV S Stn","Bearstone33/11kVSStn",850002,0.42699999999999999,null,427,"",3,"Y"]
["South Wales","Beaufort Power Stor 33/11kV S Stn","BeaufortPowerStor33/11kVSStn",550441,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Beaumont Leys 33/11kV S Stn","BeaumontLeys33/11kVSStn",920026,0.13,null,275,"",3,"Y"]
["South West","Bedminster 33/11kV S Stn","Bedminster33/11kVSStn",110641,0.12,null,348,"",3,"Y"]
["South West","Beechgrove Farm Solar Park 33kV S Stn","BeechgroveFarmSolarPark33kVSStn",258019,0.16700000000000001,null,274,"",3,"Y"]
["East Midlands","Beeston 33/11kV S Stn","Beeston33/11kVSStn",880012,0.1,null,216,"",3,"Y"]
["East Midlands","Beevor Street 33/11kV S Stn","BeevorStreet33/11kVSStn",900009,0.15,null,300,"",3,"Y"]
["East Midlands","Belper 33/11kV S Stn","Belper33/11kVSStn",890076,8.3000000000000004E-2,null,120,"",3,"Y"]
["East Midlands","Bentinck Generating Station 33kV S Stn","BentinckGeneratingStation33kVSStn",898163,1.3,null,2275,"",3,"Y"]
["West Midlands","Bentley 132/11kV S Stn","Bentley132/11kVSStn",670046,8.8999999999999996E-2,null,694,"",1,"Y"]
["West Midlands","Berkeley 33/11kV S Stn","Berkeley33/11kVSStn",790015,0.33800000000000002,null,423,"",3,"Y"]
["East Midlands","Berkswell 275/132kV S Stn","Berkswell275/132kVSStn",690001,0.2,"Y",350,"",1,"Y"]
["West Midlands","Berrington 33/11kV S Stn","Berrington33/11kVSStn",840018,0.36,null,710,"",3,"Y"]
["South Wales","Berthllwyd Solar Park Generation 33kV S Stn","BerthllwydSolarParkGeneration33kVSStn",540426,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Betws Wind Farm Grid 132kV S Stn","BetwsWindFarmGrid132kVSStn",520341,0.2,"Y",1000,"Y",1,"Y"]
["East Midlands","Bevercotes 33/11kV S Stn","Bevercotes33/11kVSStn",890055,0.17100000000000001,null,171,"",3,"Y"]
["West Midlands","Bevington 66/11kV S Stn","Bevington66/11kVSStn",670098,0.154,null,248,"",3,"Y"]
["East Midlands","Bicker Fen 400/132kV S Stn","BickerFen400/132kVSStn",690003,0.04,null,710,"",1,"Y"]
["East Midlands","Bicker Fen Wind Generation 33kV S Stn","BickerFenWindGeneration33kVSStn",910019,0.7,"Y",500,"Y",3,"Y"]
["South West","Bideford Main 33/11kV S Stn","BidefordMain33/11kVSStn",350018,0.104,null,115,"",3,"Y"]
["South West","Bidwell Solar Park 33kV S Stn","BidwellSolarPark33kVSStn",348103,0.29799999999999999,null,500,"Y",3,"Y"]
["East Midlands","Bilborough 33/11kV S Stn","Bilborough33/11kVSStn",880013,0.13100000000000001,null,277,"",3,"Y"]
["East Midlands","Billingborough 33/11kV S Stn","Billingborough33/11kVSStn",910035,0.32300000000000001,null,633,"",3,"Y"]
["West Midlands","Bilson 33/11kV S Stn","Bilson33/11kVSStn",790026,0.104,null,260,"",3,"Y"]
["East Midlands","Bilsthorpe 33/11kV S Stn","Bilsthorpe33/11kVSStn",890054,0.2,null,396,"",3,"Y"]
["East Midlands","Bilsthorpe P V Generation 33kV S Stn","BilsthorpePVGeneration33kVSStn",898555,0.24,null,496,"",3,"Y"]
["East Midlands","Bilsthorpe Solar 33kV S Stn","BilsthorpeSolar33kVSStn",898326,0.27,null,208,"",3,"Y"]
["East Midlands","Bingham 33/11kV S Stn","Bingham33/11kVSStn",880039,6.0999999999999999E-2,null,73,"",3,"Y"]
["East Midlands","Birch Coppice 33/11kv S Stn","BirchCoppice33/11kvSStn",939800,0.13300000000000001,null,189,"",3,"Y"]
["West Midlands","Birchfield Lane 132/11kV S Stn","BirchfieldLane132/11kVSStn",670047,5.0999999999999997E-2,null,418,"",1,"Y"]
["South Wales","Birchgrove 33/11kV S Stn","Birchgrove33/11kVSStn",510069,6.7000000000000004E-2,null,500,"Y",3,"Y"]
["East Midlands","Birstall 33/11kV S Stn","Birstall33/11kVSStn",920029,7.6999999999999999E-2,null,182,"",3,"Y"]
["West Midlands","Bishops Castle 33/11kV S Stn","BishopsCastle33/11kVSStn",840007,0.19,null,134,"",3,"Y"]
["West Midlands","Bishops Cleeve 66/11kV S Stn","BishopsCleeve66/11kVSStn",670086,0.115,null,163,"",3,"Y"]
["South Wales","Bishopston 33/11kV S Stn","Bishopston33/11kVSStn",520070,0.434,null,500,"Y",3,"Y"]
["West Midlands","Bishops Wood 275/132kV S Stn","BishopsWood275/132kVSStn",670002,0.17,null,3145,"",1,"Y"]
["South West","Bishopsworth 33/11kV S Stn","Bishopsworth33/11kVSStn",113193,0.12,null,198,"",3,"Y"]
["East Midlands","Biwaters 33/11kV S Stn","Biwaters33/11kVSStn",890095,0.26200000000000001,null,349,"",3,"Y"]
["West Midlands","Bixhead 33/11kV S Stn","Bixhead33/11kVSStn",790018,0.38500000000000001,null,454,"",3,"Y"]
["South West","Blackawton 33/11kV S Stn","Blackawton33/11kVSStn",340022,1.3859999999999999,null,1249,"",3,"Y"]
["South West","Blackditch 33kV S Stn","Blackditch33kVSStn",210600,0.123,null,369,"",3,"Y"]
["West Midlands","Black Lake 132/11kV S Stn","BlackLake132/11kVSStn",670048,7.1999999999999995E-2,null,532,"",1,"Y"]
["South West","Blackpool 33/11kV S Stn","Blackpool33/11kVSStn",437350,0.53300000000000003,null,534,"",3,"Y"]
["East Midlands","Blackwell 33/11kV S Stn","Blackwell33/11kVSStn",890026,0.114,null,201,"",3,"Y"]
["South Wales","Blaenavon 66/11kV S Stn","Blaenavon66/11kVSStn",530071,0.11,null,146,"",3,"Y"]
["South Wales","Blaen Bowi Wind Farm 33kV S Stn","BlaenBowiWindFarm33kVSStn",580315,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Blaengwen Wind Farm 132kV S Stn","BlaengwenWindFarm132kVSStn",580328,0.2,"Y",1000,"Y",1,"Y"]
["South Wales","Blaenlleidi Wind Farm 33kV S Stn","BlaenlleidiWindFarm33kVSStn",520388,2.2000000000000002,null,500,"Y",3,"Y"]
["South Wales","Blaenporth 33/11kV S Stn","Blaenporth33/11kVSStn",580072,1.18,null,500,"Y",3,"Y"]
["South West","Blagdon 33/11kV S Stn","Blagdon33/11kVSStn",180173,0.11799999999999999,null,160,"",3,"Y"]
["East Midlands","Bletchley 132/33kV S Stn","Bletchley132/33kVSStn",690046,2.7E-2,null,166,"",3,"Y"]
["East Midlands","Bletchley 33/11kV S Stn","Bletchley33/11kVSStn",940042,2.7E-2,null,166,"",3,"Y"]
["East Midlands","Bletchley 33kV S Stn","Bletchley33kVSStn",940013,2.7E-2,null,166,"",3,"Y"]
["East Midlands","Bletchley Landfill 33kV S Stn","BletchleyLandfill33kVSStn",940020,0.192,null,416,"",3,"Y"]
["East Midlands","Blidworth 33/11kV S Stn","Blidworth33/11kVSStn",890041,0.64400000000000002,null,1173,"",3,"Y"]
["West Midlands","Bloxham 66/11kV S Stn","Bloxham66/11kVSStn",670087,0.31,null,504,"",3,"Y"]
["West Midlands","Bloxwich Ess 33kV S Stn","BloxwichEss33kVSStn",726003,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Boc Margam Grid 132kV S Stn","BocMargamGrid132kVSStn",560290,0.115,null,1000,"Y",1,"Y"]
["West Midlands","Bodenham 66/11kV S Stn","Bodenham66/11kVSStn",670112,0.46,null,1334,"",3,"Y"]
["South West","Bodiniel Solar Park 33kV S Stn","BodinielSolarPark33kVSStn",438020,0.9,null,500,"Y",3,"Y"]
["South West","Bodmin 33/11kV S Stn","Bodmin33/11kVSStn",437230,0.189,null,242,"",3,"Y"]
["South West","Bodwen Solar Farm 33kV S Stn","BodwenSolarFarm33kVSStn",438171,1.46,null,500,"Y",3,"Y"]
["East Midlands","Bolsover 33/11kV S Stn","Bolsover33/11kVSStn",890093,0.15,null,225,"",3,"Y"]
["East Midlands","Bolsover Moor Quarry PV Solar Farm 33kV S Stn","BolsoverMoorQuarryPVSolarFarm33kVSStn",898563,0.35,null,487,"",3,"Y"]
["East Midlands","Bombardier 33kV S Stn","Bombardier33kVSStn",870016,5.3999999999999999E-2,null,127,"",3,"Y"]
["South West","Bommerton Farm Solar Park 33kV S Stn","BommertonFarmSolarPark33kVSStn",268081,0.7,"Y",500,"Y",3,"Y"]
["South West","Bommertown Solar Park 33kV S Stn","BommertownSolarPark33kVSStn",268136,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Boothen 132/33/11kV S Stn","Boothen132/33/11kVSStn",680052,7.3999999999999996E-2,null,681,"",3,"Y"]
["East Midlands","Boothville 33/11kV S Stn","Boothville33/11kVSStn",940065,0.06,null,138,"",3,"Y"]
["East Midlands","Boots 33/11kV S Stn","Boots33/11kVSStn",880016,0.153,null,384,"",3,"Y"]
["West Midlands","Bordesley 132/11kV S Stn","Bordesley132/11kVSStn",670041,9.7000000000000003E-2,null,286,"",1,"Y"]
["East Midlands","Boston 132/33kV S Stn","Boston132/33kVSStn",690043,3.9E-2,null,257,"",3,"Y"]
["East Midlands","Boston 33kV S Stn","Boston33kVSStn",900004,3.9E-2,null,257,"",3,"Y"]
["East Midlands","Boston Biomass Generation 33kV S Stn","BostonBiomassGeneration33kVSStn",907058,9.6000000000000002E-2,null,261,"",3,"Y"]
["East Midlands","Bottesford 33/11kV S Stn","Bottesford33/11kVSStn",910038,0.217,null,260,"",3,"Y"]
["West Midlands","Boughton Rd 132/11kV S Stn","BoughtonRd132/11kVSStn",670137,4.3999999999999997E-2,null,498,"",1,"Y"]
["East Midlands","Bourne 132/33kV S Stn","Bourne132/33kVSStn",690044,0.09,null,844,"",3,"Y"]
["East Midlands","Bourne 33/11kV S Stn","Bourne33/11kVSStn",910032,0.09,null,844,"",3,"Y"]
["East Midlands","Bourne 33kV S Stn","Bourne33kVSStn",910005,0.09,null,844,"",3,"Y"]
["East Midlands","Bourne West 132/25kV S Stn","BourneWest132/25kVSStn",690039,0.17399999999999999,null,1366,"",1,"Y"]
["West Midlands","Bournville 132/11kV S Stn","Bournville132/11kVSStn",670050,6.8000000000000005E-2,null,474,"",1,"Y"]
["South West","Bournville 33/11kV S Stn","Bournville33/11kVSStn",180471,7.9000000000000001E-2,null,141,"",3,"Y"]
["South Wales","Boverton 33/11kV S Stn","Boverton33/11kVSStn",560075,0.32200000000000001,null,500,"Y",3,"Y"]
["South West","Bovey Tracey 33/11kV S Stn","BoveyTracey33/11kVSStn",340039,0.19700000000000001,null,215,"",3,"Y"]
["East Midlands","Bowbridge STOR Generation 33kV S Stn","BowbridgeSTORGeneration33kVSStn",690070,0.7,"Y",500,"Y",3,"Y"]
["South West","Bower Ashton 33/11kV S Stn","BowerAshton33/11kVSStn",113371,0.12,null,186,"",3,"Y"]
["South West","Bowhays Cross 132/33kV S Stn","BowhaysCross132/33kVSStn",210210,0.192,null,396,"",3,"Y"]
["South West","Bowhays Cross 33/11kV S Stn","BowhaysCross33/11kVSStn",210210,0.192,null,396,"",3,"Y"]
["East Midlands","Brackley 132/33kV S Stn","Brackley132/33kVSStn",690047,0.1,null,637,"",3,"Y"]
["East Midlands","Brackley 33/11kV S Stn","Brackley33/11kVSStn",947000,0.1,null,637,"",3,"Y"]
["East Midlands","Brackley 33kV S Stn","Brackley33kVSStn",946100,0.1,null,637,"",3,"Y"]
["East Midlands","Brackley Town 33/11kV S Stn","BrackleyTown33/11kVSStn",940028,4.1000000000000002E-2,null,80,"",3,"Y"]
["East Midlands","Brackmills 33/11kV S Stn","Brackmills33/11kVSStn",940072,0.06,null,160,"",3,"Y"]
["South West","Bradford Manor Solar Farm 33kV S Stn","BradfordManorSolarFarm33kVSStn",358057,0.34,null,500,"Y",3,"Y"]
["South West","Bradley Lane 33/11kV S Stn","BradleyLane33/11kVSStn",340020,8.3000000000000004E-2,null,78,"",3,"Y"]
["South West","Bradley Stoke 132/33kV S Stn","BradleyStoke132/33kVSStn",113572,0.21,null,1024,"",3,"Y"]
["South West","Bradley Stoke 33/11kV S Stn","BradleyStoke33/11kVSStn",113760,0.21,null,500,"Y",3,"Y"]
["South West","Bradon Fm Generator 33kV S Stn","BradonFmGenerator33kVSStn",210260,7.6999999999999999E-2,null,54,"",3,"Y"]
["East Midlands","Bradwell Abbey 132/33kV S Stn","BradwellAbbey132/33kVSStn",690006,9.4E-2,null,486,"",3,"Y"]
["East Midlands","Bradwell Abbey 33kV S Stn","BradwellAbbey33kVSStn",940006,9.4E-2,null,486,"",3,"Y"]
["East Midlands","Brafield On The Green PV 33kv S Stn","BrafieldOnTheGreenPV33kvSStn",946276,0.16300000000000001,null,263,"",3,"Y"]
["East Midlands","Branston South Solar Farm 33kV S Stn","BranstonSouthSolarFarm33kVSStn",907556,0.22,null,418,"",3,"Y"]
["South West","Bratton Fleming 33/11kV S Stn","BrattonFleming33/11kVSStn",260550,3.82,null,2475,"",3,"Y"]
["South West","Bratton Fleming Solar Park 33kV S Stn","BrattonFlemingSolarPark33kVSStn",268000,0.81,null,500,"Y",3,"Y"]
["East Midlands","Braunstone 33/11kV S Stn","Braunstone33/11kVSStn",920031,9.2999999999999999E-2,null,55,"",3,"Y"]
["East Midlands","Braunston Road 33/11kV S Stn","BraunstonRoad33/11kVSStn",940047,9.8000000000000004E-2,null,245,"",3,"Y"]
["South West","Braunton 33/11kV S Stn","Braunton33/11kVSStn",260220,0.372,null,463,"",3,"Y"]
["South Wales","Brawdy 33/11kV S Stn","Brawdy33/11kVSStn",600076,2.0630000000000002,null,500,"Y",3,"Y"]
["East Midlands","Breach Farm 33kv S Stn","BreachFarm33kvSStn",875157,0.747,null,1141,"",3,"Y"]
["South Wales","Brechfa Forest West Wind Farm 132kV S Stn","BrechfaForestWestWindFarm132kVSStn",520435,1.45,null,1000,"Y",1,"Y"]
["South Wales","Brecon 66/11kV S Stn","Brecon66/11kVSStn",610077,0.13700000000000001,null,210,null,3,"Y"]
["South Wales","Brecon Power Stor 33kV S Stn","BreconPowerStor33kVSStn",550442,0.434,null,240,"",3,"Y"]
["South West","Brent Knoll 33kV S Stn","BrentKnoll33kVSStn",182332,0.191,null,154,"",3,"Y"]
["East Midlands","Bretby 33/11kV S Stn","Bretby33/11kVSStn",870034,8.8999999999999996E-2,null,130,"",3,"Y"]
["South Wales","Bridell 33/11kV S Stn","Bridell33/11kVSStn",580078,0.24299999999999999,null,500,"Y",3,"Y"]
["South West","Bridge Mills 33/11kV S Stn","BridgeMills33/11kVSStn",310018,0.21,null,201,"",3,"Y"]
["South Wales","Bridgend Grid 132/33kV S Stn","BridgendGrid132/33kVSStn",560004,0.127,null,1000,"Y",3,"Y"]
["South Wales","Bridgend Trading Estate 33/11kV S Stn","BridgendTradingEstate33/11kVSStn",560079,0.7,"Y",500,"Y",3,"Y"]
["South West","Bridgwater Grid 132/33kV S Stn","BridgwaterGrid132/33kVSStn",210444,6.0999999999999999E-2,null,431,"",3,"Y"]
["South West","Bridgwater GSP 275/132kV S Stn","BridgwaterGSP275/132kVSStn",206008,5.6000000000000001E-2,null,820,"",1,"Y"]
["South West","Bridgwater Local 33/11kV S Stn","BridgwaterLocal33/11kVSStn",210060,9.0999999999999998E-2,null,358,"",3,"Y"]
["South West","Bridport 33/11kV S Stn","Bridport33/11kVSStn",250340,5.8000000000000003E-2,null,56,"",3,"Y"]
["South West","Bristol International Airport 33/11kV S Stn","BristolInternationalAirport33/11kVSStn",182736,0.28299999999999997,null,406,"",3,"Y"]
["West Midlands","Bristol Road 33kV S Stn","BristolRoad33kVSStn",795721,0.04,null,84,"",3,"Y"]
["South Wales","British Energy Newport South 33kV S Stn","BritishEnergyNewportSouth33kVSStn",530316,0.7,"Y",500,"Y",3,"Y"]
["South West","British Gas Hallen 33/11kV S Stn","BritishGasHallen33/11kVSStn",113429,7.0999999999999994E-2,null,110,"",3,"Y"]
["East Midlands","British Gypsum 33/11kV S Stn","BritishGypsum33/11kVSStn",920018,0.113,null,219,"",3,"Y"]
["West Midlands","British Industrial Sand 33kV S Stn","BritishIndustrialSand33kVSStn",850027,0.51200000000000001,null,701,"",3,"Y"]
["South Wales","Briton Ferry 132/33kV S Stn","BritonFerry132/33kVSStn",560005,5.8999999999999997E-2,null,1000,"Y",3,"Y"]
["South Wales","Briton Ferry STOR Generation 33kV S Stn","BritonFerrySTORGeneration33kVSStn",560347,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Broadfield 33/11kV S Stn","Broadfield33/11kVSStn",600085,0.23799999999999999,null,500,"Y",3,"Y"]
["South Wales","Broad St. Barry 33/11kV S Stn","BroadSt.Barry33/11kVSStn",510086,0.26300000000000001,null,500,"Y",3,"Y"]
["South Wales","Broad Street Swg Site 33kV S Stn","BroadStreetSwgSite33kVSStn",510439,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Broadway 66/11kV S Stn","Broadway66/11kVSStn",670089,0.37,null,701,"",3,"Y"]
["South West","Broadweir 33/11kV S Stn","Broadweir33/11kVSStn",114260,0.06,null,13.5,"",3,"Y"]
["West Midlands","Brockworth 33/11kV S Stn","Brockworth33/11kVSStn",790005,2.1000000000000001E-2,null,48,"",3,"Y"]
["West Midlands","Bromyard 66/11kV S Stn","Bromyard66/11kVSStn",670108,0.223,null,386,"",3,"Y"]
["West Midlands","Broseley 33/11kV S Stn","Broseley33/11kVSStn",840023,0.13,null,258,"",3,"Y"]
["West Midlands","Brotheridge Green 66/11kV S Stn","BrotheridgeGreen66/11kVSStn",670102,0.41,null,614,"",3,"Y"]
["East Midlands","Brownsover 33/11kV S Stn","Brownsover33/11kVSStn",930066,0.151,null,411,"",3,"Y"]
["East Midlands","Bruntingthorpe 33/11kV S Stn","Bruntingthorpe33/11kVSStn",930105,0.21,null,276,"",3,"Y"]
["East Midlands","Brush 33/11kV S Stn","Brush33/11kVSStn",920021,0.09,null,176,"",3,"Y"]
["South Wales","Bryn Blaen Wind Farm 66kV S Stn","BrynBlaenWindFarm66kVSStn",610443,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Bryncyrnau Isaf Solar Park 33kV S Stn","BryncyrnauIsafSolarPark33kVSStn",580432,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Brynhenllys Solar Park 33kV S Stn","BrynhenllysSolarPark33kVSStn",520446,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Brynhill Barry Grid 132/33/11kV S Stn","BrynhillBarryGrid132/33/11kVSStn",510088,0.08,null,1000,"Y",3,"Y"]
["South Wales","Brynmawr 33/11kV S Stn","Brynmawr33/11kVSStn",550090,0.10100000000000001,null,500,"Y",3,"Y"]
["South Wales","Brynteg Solar Farm 33kV S Stn","BryntegSolarFarm33kVSStn",520374,0.34,null,500,"Y",3,"Y"]
["South Wales","Bryn Titli Wind Farm 66kV S Stn","BrynTitliWindFarm66kVSStn",610297,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Brynwhilach Solar Park 33kV S Stn","BrynwhilachSolarPark33kVSStn",520396,0.13200000000000001,null,500,"Y",3,"Y"]
["South West","Buckfastleigh 33/11kV S Stn","Buckfastleigh33/11kVSStn",340014,0.55700000000000005,null,495,"",3,"Y"]
["East Midlands","Buckingham 33/11kV S Stn","Buckingham33/11kVSStn",940029,6.7000000000000004E-2,null,99,"",3,"Y"]
["South West","Buckwell Street 33/11kV S Stn","BuckwellStreet33/11kVSStn",330022,0.57999999999999996,null,229,"",3,"Y"]
["East Midlands","Budby 33/11kV S Stn","Budby33/11kVSStn",890045,0.51200000000000001,null,737,"",3,"Y"]
["South West","Budleigh Salterton 33/11kV S Stn","BudleighSalterton33/11kVSStn",310039,9.9000000000000005E-2,null,118,"",3,"Y"]
["East Midlands","Bugbrooke 33/11kV S Stn","Bugbrooke33/11kVSStn",940052,0.104,null,151,"",3,"Y"]
["South West","Bugle 33/11kV S Stn","Bugle33/11kVSStn",437360,0.43,null,476,"",3,"Y"]
["South Wales","Builth Wells 66/11kV S Stn","BuilthWells66/11kVSStn",610092,1.39,null,1215,null,3,"Y"]
["East Midlands","Bulwell 33/11kV S Stn","Bulwell33/11kVSStn",880019,7.5999999999999998E-2,null,176,"",3,"Y"]
["South West","Burlescombe 33/11kV S Stn","Burlescombe33/11kVSStn",310033,0.52300000000000002,null,1029,"",3,"Y"]
["East Midlands","Burnaston 132/11kV S Stn","Burnaston132/11kVSStn",680034,9.0999999999999998E-2,null,1237,"",1,"Y"]
["South West","Burnham 33/11kV S Stn","Burnham33/11kVSStn",210470,4.2999999999999997E-2,null,54,"",3,"Y"]
["West Midlands","Burntwood 132/11kV S Stn","Burntwood132/11kVSStn",680053,0.115,null,602,"",1,"Y"]
["South West","Burrowton Farm Solar Park 33kV S Stn","BurrowtonFarmSolarPark33kVSStn",318026,0.16,null,500,"Y",3,"Y"]
["West Midlands","Burslem 132/33/11kV S Stn","Burslem132/33/11kVSStn",680054,8.5000000000000006E-2,null,280,"",3,"Y"]
["West Midlands","Burslem 33/11/6.6kV S Stn","Burslem33/11/6.6kVSStn",680065,8.5000000000000006E-2,null,280,"",3,"Y"]
["South West","Burthy Solar Park 33kV S Stn","BurthySolarPark33kVSStn",418141,0.46,null,500,"Y",3,"Y"]
["East Midlands","Burton 132/11kV S Stn","Burton132/11kVSStn",874558,1.9E-2,null,141,"",1,"Y"]
["East Midlands","Burton 132/33/11kV S Stn","Burton132/33/11kVSStn",680033,1.9E-2,null,141,"",3,"Y"]
["East Midlands","Burton 33kV S Stn","Burton33kVSStn",875000,1.9E-2,null,141,"",3,"Y"]
["East Midlands","Burton Latimer 33/11kV S Stn","BurtonLatimer33/11kVSStn",920054,6.2E-2,null,106,"",3,"Y"]
["East Midlands","Burton Pedwardine Solar Park 1 33kV S Stn","BurtonPedwardineSolarPark133kVSStn",905663,0.17799999999999999,null,267,"",3,"Y"]
["East Midlands","Burton South 132/33kV S Stn","BurtonSouth132/33kVSStn",680009,0.1,null,2006,"",3,"Y"]
["East Midlands","Burton South 33kV S Stn","BurtonSouth33kVSStn",870004,0.1,null,843,"",3,"Y"]
["East Midlands","Burton Wold North 33kV S Stn","BurtonWoldNorth33kVSStn",925737,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Burton Wold Wind Farm Generation 33kV S Stn","BurtonWoldWindFarmGeneration33kVSStn",920012,0.13600000000000001,null,256,"",3,"Y"]
["East Midlands","Burton Wold Wind Farm South 33kV S Stn","BurtonWoldWindFarmSouth33kVSStn",923189,0.16600000000000001,null,187,"",3,"Y"]
["West Midlands","Bushbury A 132kV S Stn","BushburyA132kVSStn",670017,8.8999999999999996E-2,null,1664,"",1,"Y"]
["West Midlands","Bushbury B-C 132/33/11kV S Stn","BushburyB-C132/33/11kVSStn",670037,0.12,null,2077,"",3,"Y"]
["West Midlands","Bushbury D 132kV S Stn","BushburyD132kVSStn",680066,8.8999999999999996E-2,null,1664,"",1,"Y"]
["West Midlands","Bustleholm 132/11kV S Stn","Bustleholm132/11kVSStn",670139,0.1,null,990,"",1,"Y"]
["West Midlands","Bustleholm 275/132/11kV S Stn","Bustleholm275/132/11kVSStn",670004,0.1,null,990,"",1,"Y"]
["East Midlands","Buxton 33kV S Stn","Buxton33kVSStn",680028,0.7,"Y",500,"Y",3,"Y"]
["South West","Bystock Farm Solar Park 33kV S Stn","BystockFarmSolarPark33kVSStn",318137,0.185,null,500,"Y",3,"Y"]
["South Wales","Caerau Road 66/11kV S Stn","CaerauRoad66/11kVSStn",560093,0.34,null,500,"Y",3,"Y"]
["South Wales","Caerphilly Primary 33/11kV S Stn","CaerphillyPrimary33/11kVSStn",540094,0.13300000000000001,null,500,"Y",3,"Y"]
["South West","Cairns Road 33/11kV S Stn","CairnsRoad33/11kVSStn",110803,0.09,null,207,"",3,"Y"]
["South Wales","Caldicot 33/11kV S Stn","Caldicot33/11kVSStn",530095,0.11600000000000001,null,102,null,3,"Y"]
["South West","Callington 33/11kV S Stn","Callington33/11kVSStn",457260,0.13800000000000001,null,180,"",3,"Y"]
["South West","Callywith 33/11kV S Stn","Callywith33/11kVSStn",437830,0.46800000000000003,null,394,"",3,"Y"]
["East Midlands","Calvert 33/11kV S Stn","Calvert33/11kVSStn",940030,0.111,null,173,"",3,"Y"]
["East Midlands","Calverton 33/11kV S Stn","Calverton33/11kVSStn",880031,0.27700000000000002,null,300,"",3,"Y"]
["South West","Camborne 132/33kV S Stn","Camborne132/33kVSStn",407020,0.23200000000000001,null,512,"",3,"Y"]
["South West","Camborne Carn Brea 33/11kV S Stn","CamborneCarnBrea33/11kVSStn",417020,0.216,null,177,"",3,"Y"]
["South West","Camborne Holmans 33/11kV S Stn","CamborneHolmans33/11kVSStn",417540,0.23699999999999999,null,390,"",3,"Y"]
["South West","Camborne Treswithian 33/11kV S Stn","CamborneTreswithian33/11kVSStn",417010,2.2789999999999999,null,3519,"",3,"Y"]
["West Midlands","Cambridge Arms 132kV S Stn","CambridgeArms132kVSStn",675348,7.1999999999999995E-2,null,614,"",1,"Y"]
["West Midlands","Cambridge Solar Power 33kv S Stn","CambridgeSolarPower33kvSStn",795644,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Camp 33/11kV S Stn","Camp33/11kVSStn",790013,1.357,null,1154,"",3,"Y"]
["East Midlands","Campbell Park 33/11kV S Stn","CampbellPark33/11kVSStn",940067,0.05,null,75,"",3,"Y"]
["East Midlands","Campbell Street 33/11kV S Stn","CampbellStreet33/11kVSStn",940059,0.152,null,391,"",3,"Y"]
["East Midlands","Campion Hills 33/11kV S Stn","CampionHills33/11kVSStn",930053,0.11700000000000001,null,220,"",3,"Y"]
["West Midlands","Cannock 132/11kV S Stn","Cannock132/11kVSStn",680055,4.2000000000000003E-2,null,240,"",1,"Y"]
["East Midlands","Cannon Street 33/11kV S Stn","CannonStreet33/11kVSStn",920058,4.8000000000000001E-2,null,123,"",3,"Y"]
["East Midlands","Canopus Solar Farm 33kV S Stn","CanopusSolarFarm33kVSStn",906775,5.8000000000000003E-2,null,119,"",3,"Y"]
["South Wales","Canton 33/11kV S Stn","Canton33/11kVSStn",510096,0.19700000000000001,null,500,"Y",3,"Y"]
["South West","Capelands Farm Solar Park 33kV S Stn","CapelandsFarmSolarPark33kVSStn",268113,0.86,null,500,"Y",3,"Y"]
["South Wales","Cardiff Central Grid 132/33kV S Stn","CardiffCentralGrid132/33kVSStn",510006,0.2,"Y",1000,"Y",3,"Y"]
["South Wales","Cardiff East Grid 275/132/33/11kV S Stn","CardiffEastGrid275/132/33/11kVSStn",510007,0.2,"Y",1480,"",3,"Y"]
["South Wales","Cardiff North Grid 132/33kV S Stn","CardiffNorthGrid132/33kVSStn",510008,8.1000000000000003E-2,null,1000,"Y",3,"Y"]
["South Wales","Cardiff South Grid 132/11kV S Stn","CardiffSouthGrid132/11kVSStn",510905,0.2,"Y",1000,"Y",1,"Y"]
["South Wales","Cardiff West Grid 132/33kV S Stn","CardiffWestGrid132/33kVSStn",510009,0.2,"Y",1000,"Y",3,"Y"]
["South Wales","Cardigan 33/11kV S Stn","Cardigan33/11kVSStn",580272,0.7,"Y",500,"Y",3,"Y"]
["South West","Carditch Drove Solar Park 33kV S Stn","CarditchDroveSolarPark33kVSStn",188112,0.1,null,500,"Y",3,"Y"]
["South West","Carland Cross Wind Farm 33kV S Stn","CarlandCrossWindFarm33kVSStn",417800,0.52,null,1435,"",3,"Y"]
["South West","Carloggas Farm Solar Park 33kV S Stn","CarloggasFarmSolarPark33kVSStn",438087,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Carlton On Trent 33/11kV S Stn","CarltonOnTrent33/11kVSStn",890061,0.67500000000000004,null,989,"",3,"Y"]
["West Midlands","Carlton Park 132/11kV S Stn","CarltonPark132/11kVSStn",690072,0.2,"Y",1000,"Y",1,"Y"]
["South Wales","Carmarthen 132/33kV S Stn","Carmarthen132/33kVSStn",580010,0.2,"Y",1000,"Y",3,"Y"]
["South West","Carnemough Farm Solar Park 33kV S Stn","CarnemoughFarmSolarPark33kVSStn",418158,0.56100000000000005,null,500,"Y",3,"Y"]
["South West","Carnworthy Solar Park 132kV S Stn","CarnworthySolarPark132kVSStn",357304,1.254,null,1400,"Y",1,"Y"]
["West Midlands","Castle Bromwich 132/11kV S Stn","CastleBromwich132/11kVSStn",670032,8.6999999999999994E-2,null,383,"",1,"Y"]
["East Midlands","Castle Donington 33/11kV S Stn","CastleDonington33/11kVSStn",870047,0.13600000000000001,null,171,"",3,"Y"]
["West Midlands","Castle Meads 132/33kV S Stn","CastleMeads132/33kVSStn",670012,7.3999999999999996E-2,null,1037,"",3,"Y"]
["East Midlands","Castle Road 33/11kV S Stn","CastleRoad33/11kVSStn",880025,7.2999999999999995E-2,null,194,"",3,"Y"]
["East Midlands","Caterpillar Desford 33/11kV S Stn","CaterpillarDesford33/11kVSStn",930094,0.109,null,124,"",3,"Y"]
["South West","Cattledown STOR Generator 33kV S Stn","CattledownSTORGenerator33kVSStn",338177,0.124,null,500,"Y",3,"Y"]
["West Midlands","Cauldon 33/11kV S Stn","Cauldon33/11kVSStn",850026,0.34,null,454,"",3,"Y"]
["West Midlands","Cauldon Cement 33kV S Stn","CauldonCement33kVSStn",850021,0.251,null,277,"",3,"Y"]
["South West","Causilgey Solar Farm 33kV S Stn","CausilgeySolarFarm33kVSStn",418046,1.1100000000000001,null,500,"Y",3,"Y"]
["East Midlands","Caythorpe 33/11kV S Stn","Caythorpe33/11kVSStn",880037,0.30499999999999999,null,573,"",3,"Y"]
["South Wales","Cefn Betingau Solar PV 33kV S Stn","CefnBetingauSolarPV33kVSStn",520339,0.34100000000000003,null,500,"Y",3,"Y"]
["South Wales","Cefn Gwrgan 66kV S Stn","CefnGwrgan66kVSStn",560025,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Cellarhead 400/132kV S Stn","Cellarhead400/132kVSStn",680067,0.105,null,2405,"",1,"Y"]
["South Wales","Cenin Energy Park 33kV S Stn","CeninEnergyPark33kVSStn",560382,1.5740000000000001,null,500,"Y",3,"Y"]
["South West","Central Intake 33kV S Stn","CentralIntake33kVSStn",330041,0.3,null,421,"",3,"Y"]
["East Midlands","Chaddesden 33/11kV S Stn","Chaddesden33/11kVSStn",870044,8.7999999999999995E-2,null,205,"",3,"Y"]
["West Midlands","Chad Valley 132/11kV S Stn","ChadValley132/11kVSStn",670051,0.08,null,336,"",1,"Y"]
["South West","Chalhanger Farm Solar Park 33kV S Stn","ChalhangerFarmSolarPark33kVSStn",358085,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Chapel Brampton 33/11kV S Stn","ChapelBrampton33/11kVSStn",940056,8.3000000000000004E-2,null,128,"",3,"Y"]
["East Midlands","Chapel St Leonards 33/11kV S Stn","ChapelStLeonards33/11kVSStn",900015,0.219,null,438,"",3,"Y"]
["South West","Chard 33/11kV S Stn","Chard33/11kVSStn",250360,2.9000000000000001E-2,null,39,"",3,"Y"]
["West Midlands","Cheadle 33/11kV S Stn","Cheadle33/11kVSStn",850024,0.13700000000000001,null,229,"",3,"Y"]
["West Midlands","Cheapside 132/11kV S Stn","Cheapside132/11kVSStn",670052,7.3999999999999996E-2,null,610,"",1,"Y"]
["East Midlands","Checkerhouse 132/33kV S Stn","Checkerhouse132/33kVSStn",680013,0.21,null,685,"",3,"Y"]
["East Midlands","Checkerhouse 33/11kV S Stn","Checkerhouse33/11kVSStn",890010,0.21,null,685,"",3,"Y"]
["East Midlands","Checkerhouse 33kV S Stn","Checkerhouse33kVSStn",890050,0.21,null,685,"",3,"Y"]
["South West","Cheddar 33/11kV S Stn","Cheddar33/11kVSStn",181345,8.2000000000000003E-2,null,128,"",3,"Y"]
["West Midlands","Cheddleton 33/11kV S Stn","Cheddleton33/11kVSStn",850020,0.23100000000000001,null,416,"",3,"Y"]
["West Midlands","Chelmsley Wood 132/11kV S Stn","ChelmsleyWood132/11kVSStn",670140,2.9000000000000001E-2,null,609,"",1,"Y"]
["West Midlands","Chelmsley Wood 33/11kV S Stn","ChelmsleyWood33/11kVSStn",670131,3.6999999999999998E-2,null,37,"",3,"Y"]
["South West","Chelson Generator 33kV S Stn","ChelsonGenerator33kVSStn",330046,0.24,null,326,"",3,"Y"]
["West Midlands","Cheltenham 132/66/11kV S Stn","Cheltenham132/66/11kVSStn",670053,5.1999999999999998E-2,null,201,"",3,"Y"]
["East Midlands","Chelveston Energy Park 33kV S Stn","ChelvestonEnergyPark33kVSStn",927000,0.12,null,211,"",3,"Y"]
["East Midlands","Chelveston Solar Park 33kV S Stn","ChelvestonSolarPark33kVSStn",926237,0.7,"Y",500,"Y",3,"Y"]
["South West","Chelwood Solar Park 33kV S Stn","ChelwoodSolarPark33kVSStn",118154,0.125,null,500,"Y",3,"Y"]
["South Wales","Chepstow 33/11kV S Stn","Chepstow33/11kVSStn",530099,0.36499999999999999,null,341,null,3,"Y"]
["West Midlands","Cherington 33/11kV S Stn","Cherington33/11kVSStn",790010,2.95,null,2183,"",3,"Y"]
["East Midlands","Chesterfield 275/132/33kV S Stn","Chesterfield275/132/33kVSStn",680007,5.6000000000000001E-2,null,1070,"",3,"Y"]
["East Midlands","Chesterfield 33kV S Stn","Chesterfield33kVSStn",680032,5.6000000000000001E-2,null,1070,"",3,"Y"]
["West Midlands","Chester Street 132/11kV S Stn","ChesterStreet132/11kVSStn",670054,0.38400000000000001,null,614,"",1,"Y"]
["South West","Chew Stoke 33/11kV S Stn","ChewStoke33/11kVSStn",181230,0.40200000000000002,null,339,"",3,"Y"]
["South West","Chewton Mendip 33/11kV S Stn","ChewtonMendip33/11kVSStn",160415,2,null,2670,"",3,"Y"]
["East Midlands","Childs Way 33/11kV S Stn","ChildsWay33/11kVSStn",940039,0.05,null,125,"",3,"Y"]
["East Midlands","Chilwell 33/11kV S Stn","Chilwell33/11kVSStn",880010,0.106,null,190,"",3,"Y"]
["West Midlands","Chipping Sodbury 132/33/11kV S Stn","ChippingSodbury132/33/11kVSStn",670042,0.28000000000000003,null,974,"",3,"Y"]
["South West","Chudleigh Knighton 33/11kV S Stn","ChudleighKnighton33/11kVSStn",340011,0.24199999999999999,null,222,"",3,"Y"]
["South West","Churchill 132/33kV S Stn","Churchill132/33kVSStn",182373,0.18,null,271,"",3,"Y"]
["South West","Churchill Gate 33/11kV S Stn","ChurchillGate33/11kVSStn",182570,0.55000000000000004,null,853,"",3,"Y"]
["East Midlands","Churchover 33/11kV S Stn","Churchover33/11kVSStn",930086,0.19,null,190,"",3,"Y"]
["East Midlands","Church Street 33/11kV S Stn","ChurchStreet33/11kVSStn",870027,1.4999999999999999E-2,null,206,"",3,"Y"]
["South West","Churchtown Farm Solar Park 33kV S Stn","ChurchtownFarmSolarPark33kVSStn",418008,0.37,null,262,"",3,"Y"]
["South West","Churston 33/11kV S Stn","Churston33/11kVSStn",340029,0.621,null,384,"",3,"Y"]
["South West","Chynoweth Solar Park 33kV S Stn","ChynowethSolarPark33kVSStn",418009,0.38,null,821,null,3,"Y"]
["East Midlands","Cinderhill 33/11kV S Stn","Cinderhill33/11kVSStn",880015,0.09,null,136,"",3,"Y"]
["South Wales","Clase 33/11kV S Stn","Clase33/11kVSStn",520100,0.20399999999999999,null,500,"Y",3,"Y"]
["East Midlands","Claverdon 33/11kV S Stn","Claverdon33/11kVSStn",930048,0.129,null,187,"",3,"Y"]
["South Wales","Clawdd Ddu Solar Farm 33kV S Stn","ClawddDduSolarFarm33kVSStn",520340,0.34,null,500,"Y",3,"Y"]
["East Midlands","Clay Lake Generation 33kV S Stn","ClayLakeGeneration33kVSStn",690069,0.7,"Y",500,"Y",3,"Y"]
["South West","Cleave Farm Solar Park 33kV S Stn","CleaveFarmSolarPark33kVSStn",268091,0.29199999999999998,null,500,"Y",3,"Y"]
["West Midlands","Cleobury Mortimer 33/11kV S Stn","CleoburyMortimer33/11kVSStn",750004,0.17199999999999999,null,241,"",3,"Y"]
["South West","Clevedon 33/11kV S Stn","Clevedon33/11kVSStn",180198,0.26200000000000001,null,275,"",3,"Y"]
["East Midlands","Clifton 33/11kV S Stn","Clifton33/11kVSStn",880024,9.7000000000000003E-2,null,363,"",3,"Y"]
["South West","Clifton 33/11kV S Stn","Clifton33/11kVSStn",111158,0.12,null,251,"",3,"Y"]
["East Midlands","Clipstone 132/33kV S Stn","Clipstone132/33kVSStn",680012,0.18,null,477,"",3,"Y"]
["East Midlands","Clipstone 33/11kV S Stn","Clipstone33/11kVSStn",890040,0.18,null,477,"",3,"Y"]
["East Midlands","Clipstone 33kV S Stn","Clipstone33kVSStn",890006,0.18,null,477,"",3,"Y"]
["South West","Clovelly 33/11kV S Stn","Clovelly33/11kVSStn",350011,2.1,null,1338,"",3,"Y"]
["East Midlands","Clowne 33/11kV S Stn","Clowne33/11kVSStn",890085,0.5,null,884,"",3,"Y"]
["South West","Clyst Honiton 33/11kV S Stn","ClystHoniton33/11kVSStn",310034,0.5,null,565,"",3,"Y"]
["West Midlands","Coaley 33kV S Stn","Coaley33kVSStn",790024,0.23499999999999999,null,411,"",3,"Y"]
["East Midlands","Coalville 132/33kV S Stn","Coalville132/33kVSStn",690024,0.109,null,382,"",3,"Y"]
["East Midlands","Coalville 33/11kV S Stn","Coalville33/11kVSStn",930092,0.109,null,382,"",3,"Y"]
["East Midlands","Coalville 33kV S Stn","Coalville33kVSStn",930020,0.109,null,382,"",3,"Y"]
["East Midlands","Cobb Farm Solar Generation 33kV S Stn","CobbFarmSolarGeneration33kVSStn",898371,0.19600000000000001,null,175,"",3,"Y"]
["South West","Cobbs Cross Solar Farm 33kV S Stn","CobbsCrossSolarFarm33kVSStn",218061,0.157,null,500,"Y",3,"Y"]
["South Wales","Cockett Valley Solar Park 33kV S Stn","CockettValleySolarPark33kVSStn",520423,0.41199999999999998,null,500,"Y",3,"Y"]
["South West","Coker 33/11kV S Stn","Coker33/11kVSStn",250530,1.1120000000000001,null,1672,"",3,"Y"]
["South West","Cold Northcott Wind Farm 33kV S Stn","ColdNorthcottWindFarm33kVSStn",457810,0.12,null,69,"",3,"Y"]
["South West","Colley End 33/11kV S Stn","ColleyEnd33/11kVSStn",340034,0.18,null,214,"",3,"Y"]
["South West","Colley Lane 33/11kV S Stn","ColleyLane33/11kVSStn",210120,8.2000000000000003E-2,null,295,"",3,"Y"]
["East Midlands","Colwick 33/11kV S Stn","Colwick33/11kVSStn",880035,2.1999999999999999E-2,null,175,"",3,"Y"]
["South West","Colyford 33/11kV S Stn","Colyford33/11kVSStn",250310,0.60899999999999999,null,605,"",3,"Y"]
["South West","Combe Park 33/6.6kV S Stn","CombePark33/6.6kVSStn",164016,7.5999999999999998E-2,null,96,"",3,"Y"]
["West Midlands","Commercial Road 33/11kV S Stn","CommercialRoad33/11kVSStn",790007,8.5000000000000006E-2,null,125,"",3,"Y"]
["South Wales","Commercial St. Neath 33/11kV S Stn","CommercialSt.Neath33/11kVSStn",560103,0.22500000000000001,null,500,"Y",3,"Y"]
["South West","Compton Martin 33/11kV S Stn","ComptonMartin33/11kVSStn",181346,0.46899999999999997,null,935,"",3,"Y"]
["West Midlands","Condover Solar Farm 33kV S Stn","CondoverSolarFarm33kVSStn",841546,0.26,null,284,"",3,"Y"]
["West Midlands","Congleton 33/11kV S Stn","Congleton33/11kVSStn",850022,7.5999999999999998E-2,null,115,"",3,"Y"]
["South West","Congresbury 33/11kV S Stn","Congresbury33/11kVSStn",180006,0.153,null,325,"",3,"Y"]
["South West","Connon Bridge Landfill 33kV S Stn","ConnonBridgeLandfill33kVSStn",437340,1.7,null,1513,"",3,"Y"]
["South West","Constantine 33/11kV S Stn","Constantine33/11kVSStn",417320,3.8519999999999999,null,4898,"",3,"Y"]
["South West","Coombe Farm Solar Park 33kV S Stn","CoombeFarmSolarPark33kVSStn",318146,0.25,null,500,"Y",3,"Y"]
["South West","Coombeshead Farm Solar Park 33kV S Stn","CoombesheadFarmSolarPark33kVSStn",348131,0.56000000000000005,null,500,"Y",3,"Y"]
["East Midlands","Copley Farm Solar Generation 33kV S Stn","CopleyFarmSolarGeneration33kVSStn",917592,0.15,null,290,"",3,"Y"]
["East Midlands","Copsewood 33/11kV S Stn","Copsewood33/11kVSStn",930044,0.104,null,253,"",3,"Y"]
["West Midlands","Copt Heath 132/11kV S Stn","CoptHeath132/11kVSStn",670055,0.115,null,566,"",1,"Y"]
["East Midlands","Corby 132/33kV S Stn","Corby132/33kVSStn",690008,0.2,"Y",1000,"Y",3,"Y"]
["East Midlands","Corby Central 33/11kV S Stn","CorbyCentral33/11kVSStn",920049,0.151,null,313,"",3,"Y"]
["East Midlands","Corby No2 33/11kV S Stn","CorbyNo233/11kVSStn",920053,7.3999999999999996E-2,null,1221,"",3,"Y"]
["East Midlands","Corby No2 33kV S Stn","CorbyNo233kVSStn",920007,7.3999999999999996E-2,null,1221,"",3,"Y"]
["East Midlands","Corby North 132kV S Stn","CorbyNorth132kVSStn",690048,6.5000000000000002E-2,null,1049,"",1,"Y"]
["East Midlands","Corby North 33kV S Stn","CorbyNorth33kVSStn",920063,6.5000000000000002E-2,null,1049,"",3,"Y"]
["South West","Core Hill 33/11kV S Stn","CoreHill33/11kVSStn",310044,0.17799999999999999,null,160,"",3,"Y"]
["South West","Cornwall Energy Recovery Centre 132kV S Stn","CornwallEnergyRecoveryCentre132kVSStn",438149,0.78,null,1400,"Y",1,"Y"]
["West Midlands","Coseley 132/11kV S Stn","Coseley132/11kVSStn",670056,0.10100000000000001,null,760,"",1,"Y"]
["West Midlands","Cotes Heath 33/11kV S Stn","CotesHeath33/11kVSStn",850005,0.17,null,425,"",3,"Y"]
["East Midlands","Cotgrave 33/11kV S Stn","Cotgrave33/11kVSStn",880036,0.126,null,177,"",3,"Y"]
["South West","Cotham 33/11kV S Stn","Cotham33/11kVSStn",114389,0.16500000000000001,null,81,"",3,"Y"]
["East Midlands","Coton Road 33/6.6kV S Stn","CotonRoad33/6.6kVSStn",930069,0.109,null,222,"",3,"Y"]
["South West","Countess Wear 33/11kV S Stn","CountessWear33/11kVSStn",310048,0.124,null,35,"",3,"Y"]
["West Midlands","Courtaulds 33/6.6kV S Stn","Courtaulds33/6.6kVSStn",930026,0.13900000000000001,null,209,"",3,"Y"]
["South Wales","Court Coleman PV Generation 33/11kV S Stn","CourtColemanPVGeneration33/11kVSStn",560379,0.28000000000000003,null,500,"Y",3,"Y"]
["East Midlands","Courthouse Green 33/11kV S Stn","CourthouseGreen33/11kVSStn",930033,0.127,null,70,"",3,"Y"]
["East Midlands","Courthouse Green 33/6.6kV S Stn","CourthouseGreen33/6.6kVSStn",930035,0.127,null,70,"",3,"Y"]
["South Wales","Court Rd. Barry 33/11kV S Stn","CourtRd.Barry33/11kVSStn",510104,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Coventry 275/132kV S Stn","Coventry275/132kVSStn",690002,0.2,"Y",2800,"Y",1,"Y"]
["East Midlands","Coventry Arena 33/11kV S Stn","CoventryArena33/11kVSStn",930083,0.23,null,202,"",3,"Y"]
["East Midlands","Coventry Central 132/33kV S Stn","CoventryCentral132/33kVSStn",690013,9.2999999999999999E-2,null,331,"",3,"Y"]
["East Midlands","Coventry Central 33kV S Stn","CoventryCentral33kVSStn",930013,9.2999999999999999E-2,null,331,"",3,"Y"]
["East Midlands","Coventry Colliery 33/11kV S Stn","CoventryColliery33/11kVSStn",930036,0.13300000000000001,null,262,"",3,"Y"]
["East Midlands","Coventry North 132/33kV S Stn","CoventryNorth132/33kVSStn",690012,7.2999999999999995E-2,null,752,"",3,"Y"]
["East Midlands","Coventry North 33/11kV S Stn","CoventryNorth33/11kVSStn",930046,7.2999999999999995E-2,null,752,"",3,"Y"]
["East Midlands","Coventry North 33kV S Stn","CoventryNorth33kVSStn",930009,7.2999999999999995E-2,null,752,"",3,"Y"]
["East Midlands","Coventry South 132/33kV S Stn","CoventrySouth132/33kVSStn",690014,5.7000000000000002E-2,null,553,"",3,"Y"]
["East Midlands","Coventry South 33/11kV S Stn","CoventrySouth33/11kVSStn",930032,5.7000000000000002E-2,null,553,"",3,"Y"]
["East Midlands","Coventry South 33kV S Stn","CoventrySouth33kVSStn",930012,5.7000000000000002E-2,null,553,"",3,"Y"]
["East Midlands","Coventry Waste Reduction 33kV S Stn","CoventryWasteReduction33kVSStn",930082,8.6999999999999994E-2,null,232,"",3,"Y"]
["East Midlands","Coventry West 132/33kV S Stn","CoventryWest132/33kVSStn",690015,0.12,null,1161,"",3,"Y"]
["East Midlands","Coventry West 33/6.6kV S Stn","CoventryWest33/6.6kVSStn",930025,0.12,null,1161,"",3,"Y"]
["East Midlands","Coventry West 33kV S Stn","CoventryWest33kVSStn",930014,0.12,null,1161,"",3,"Y"]
["South Wales","Cowbridge 33/11kV S Stn","Cowbridge33/11kVSStn",560105,0.21,null,500,"Y",3,"Y"]
["West Midlands","Cowhorn 33/11kV S Stn","Cowhorn33/11kVSStn",790011,8.7999999999999995E-2,null,120,"",3,"Y"]
["South West","Cowley Road 33/11kV S Stn","CowleyRoad33/11kVSStn",310014,6.4000000000000001E-2,null,77,"",3,"Y"]
["East Midlands","Cox Street 33/6.6 Kv S Stn","CoxStreet33/6.6KvSStn",930031,9.0999999999999998E-2,null,224,"",3,"Y"]
["East Midlands","Craggs Lane 33/11kV S Stn","CraggsLane33/11kVSStn",890032,0.156,null,293,"",3,"Y"]
["East Midlands","Cranwell 33/11kV S Stn","Cranwell33/11kVSStn",910031,0.11,null,220,"",3,"Y"]
["West Midlands","Craven Arms 33/11kV S Stn","CravenArms33/11kVSStn",750003,0.15,null,196,"",3,"Y"]
["South West","Crediton 33/11kV S Stn","Crediton33/11kVSStn",310015,0.11700000000000001,null,120,"",3,"Y"]
["South West","Creech St Michael 33/11kV S Stn","CreechStMichael33/11kVSStn",210030,0.30399999999999999,null,333,"",3,"Y"]
["South Wales","Creigiau 33/11kV S Stn","Creigiau33/11kVSStn",540106,0.78400000000000003,null,500,"Y",3,"Y"]
["South West","Crewkerne 33/11kV S Stn","Crewkerne33/11kVSStn",250370,8.8999999999999996E-2,null,307,"",3,"Y"]
["South West","Crewkerne Solar Park 33kV S Stn","CrewkerneSolarPark33kVSStn",258153,0.13800000000000001,null,500,"Y",3,"Y"]
["South West","Cribbs Causeway 33/11kV S Stn","CribbsCauseway33/11kVSStn",113983,7.6999999999999999E-2,null,32,"",3,"Y"]
["East Midlands","Crick 33/11kV S Stn","Crick33/11kVSStn",940068,8.2000000000000003E-2,null,158,"",3,"Y"]
["South West","Cricket St Thomas Solar Park 33kV S Stn","CricketStThomasSolarPark33kVSStn",258063,0.13600000000000001,null,500,"Y",3,"Y"]
["South Wales","Crickhowell 66/11kV S Stn","Crickhowell66/11kVSStn",610107,0.497,null,561,null,3,"Y"]
["South West","Crinacott Farm Solar Park 33kV S Stn","CrinacottFarmSolarPark33kVSStn",358068,0.14000000000000001,null,500,"Y",3,"Y"]
["East Midlands","Croft End Solar Farm 33kV S Stn","CroftEndSolarFarm33kVSStn",905191,7.0000000000000007E-2,null,165,"",3,"Y"]
["East Midlands","Cromford 33/11kV S Stn","Cromford33/11kVSStn",890073,0.21,null,422,"",3,"Y"]
["South Wales","Cross Hands 33/11kV S Stn","CrossHands33/11kVSStn",520307,0.248,null,500,"Y",3,"Y"]
["East Midlands","Crowland 33/11kV S Stn","Crowland33/11kVSStn",910029,0.13800000000000001,null,215,"",3,"Y"]
["East Midlands","Crown Farm 33/11kV S Stn","CrownFarm33/11kVSStn",890037,2.5999999999999999E-2,null,487,"",3,"Y"]
["South Wales","Crugmore Solar Park 33kV S Stn","CrugmoreSolarPark33kVSStn",580383,0.23,null,500,"Y",3,"Y"]
["South Wales","Crumlin 132/11kV S Stn","Crumlin132/11kVSStn",550011,0.219,null,1000,"Y",1,"Y"]
["South Wales","Crumlin STOR 33kV S Stn","CrumlinSTOR33kVSStn",550436,0.84399999999999997,null,710,"",3,"Y"]
["South Wales","Crwys Rd. 33/11kV S Stn","CrwysRd.33/11kVSStn",510108,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Crymlyn Burrows 33kV S Stn","CrymlynBurrows33kVSStn",520312,0.3,null,500,"Y",3,"Y"]
["South West","Cullompton 33/11kV S Stn","Cullompton33/11kVSStn",310024,0.27100000000000002,null,298,"",3,"Y"]
["South West","Cullompton Solar Park 33kV S Stn","CullomptonSolarPark33kVSStn",318098,0.2,null,500,"Y",3,"Y"]
["South West","Culmhead 33/11kV S Stn","Culmhead33/11kVSStn",210390,0.79300000000000004,null,948,"",3,"Y"]
["South West","Culmhead Solar Park 33kV S Stn","CulmheadSolarPark33kVSStn",218009,0.13700000000000001,null,500,"Y",3,"Y"]
["South West","Curry Mallet 33/11kV S Stn","CurryMallet33/11kVSStn",210450,0.78800000000000003,null,871,"",3,"Y"]
["South Wales","Cwmbargoed Coal Washery (Load) 33kV S Stn","CwmbargoedCoalWashery(Load)33kVSStn",550389,0.30199999999999999,null,500,"Y",3,"Y"]
["South Wales","Cwmbran Primary 132/11kV S Stn","CwmbranPrimary132/11kVSStn",530110,6.3E-2,null,287,null,1,"Y"]
["South Wales","Cwm Cae Singrug Solar Park 33kV S Stn","CwmCaeSingrugSolarPark33kVSStn",550377,0.5,null,500,"Y",3,"Y"]
["South Wales","Cwmfelinfach 33/11kV S Stn","Cwmfelinfach33/11kVSStn",550111,0.34399999999999997,null,500,"Y",3,"Y"]
["South Wales","Cwmffrwd 33/11kV S Stn","Cwmffrwd33/11kVSStn",580296,0.65,null,500,"Y",3,"Y"]
["South Wales","Cyncoed 33/11kV S Stn","Cyncoed33/11kVSStn",510115,0.23,null,500,"Y",3,"Y"]
["South West","Dairy Crest Davidstow 33/11kV S Stn","DairyCrestDavidstow33/11kVSStn",437470,1.1499999999999999,null,771,"",3,"Y"]
["East Midlands","Daneshill Generation 33kV S Stn","DaneshillGeneration33kVSStn",890017,0.28999999999999998,null,335,"",3,"Y"]
["East Midlands","Danesmoor 33/11kV S Stn","Danesmoor33/11kVSStn",890094,0.26300000000000001,null,108,"",3,"Y"]
["East Midlands","Darley Abbey 33/11kV S Stn","DarleyAbbey33/11kVSStn",870039,0.09,null,132,"",3,"Y"]
["South West","Darracott Moor Windfarm 33kV S Stn","DarracottMoorWindfarm33kVSStn",260180,0.82,null,792,"",3,"Y"]
["South West","Dartmouth 33/11kV S Stn","Dartmouth33/11kVSStn",340030,0.39300000000000002,null,381,"",3,"Y"]
["East Midlands","Daventry 132/33kV S Stn","Daventry132/33kVSStn",690052,4.4999999999999998E-2,null,147,"",3,"Y"]
["East Midlands","Daventry 33/11kV S Stn","Daventry33/11kVSStn",940049,4.4999999999999998E-2,null,147,"",3,"Y"]
["East Midlands","Daventry 33kV S Stn","Daventry33kVSStn",940008,4.4999999999999998E-2,null,147,"",3,"Y"]
["South West","Davidstow 33/11kV S Stn","Davidstow33/11kVSStn",437410,4.3,null,3677,"",3,"Y"]
["South West","Dawlish 33/11kV S Stn","Dawlish33/11kVSStn",340023,0.14299999999999999,null,125,"",3,"Y"]
["East Midlands","Dayfields Farm PV 33kV S Stn","DayfieldsFarmPV33kVSStn",875119,0.24,null,278,"",3,"Y"]
["East Midlands","Decoy Farm Generation 33kV S Stn","DecoyFarmGeneration33kVSStn",917572,0.251,null,314,"",3,"Y"]
["East Midlands","Deepdale Solar Farm 33kV S Stn","DeepdaleSolarFarm33kVSStn",917435,0.12,null,123,"",3,"Y"]
["East Midlands","Deeping St Nicholas Wind Generation 33kV S Stn","DeepingStNicholasWindGeneration33kVSStn",910015,0.7,"Y",500,"Y",3,"Y"]
["South West","Delabole 33/11kV S Stn","Delabole33/11kVSStn",437420,1.278,null,1388,"",3,"Y"]
["South West","Denbrook Wind Farm 33kV S Stn","DenbrookWindFarm33kVSStn",358159,0.16600000000000001,null,500,"Y",3,"Y"]
["East Midlands","Denby 33/11kV S Stn","Denby33/11kVSStn",890082,0.11799999999999999,null,250,"",3,"Y"]
["East Midlands","Denton 33/11kV S Stn","Denton33/11kVSStn",940066,0.28000000000000003,null,425,"",3,"Y"]
["South West","Denzell Downs Wind Farm 33kV S Stn","DenzellDownsWindFarm33kVSStn",438148,0.15640000000000001,null,500,"Y",3,"Y"]
["East Midlands","Derby 132/11kV S Stn","Derby132/11kVSStn",870036,8.4000000000000005E-2,null,375,"",1,"Y"]
["East Midlands","Derby 132/33/11kV S Stn","Derby132/33/11kVSStn",680041,8.4000000000000005E-2,null,375,"",3,"Y"]
["East Midlands","Derby 33kV S Stn","Derby33kVSStn",870012,8.4000000000000005E-2,null,375,"",3,"Y"]
["East Midlands","Derby South 132/33kV S Stn","DerbySouth132/33kVSStn",680029,0.05,null,481,"",3,"Y"]
["East Midlands","Derby South 33kV S Stn","DerbySouth33kVSStn",870005,0.05,null,134,"",3,"Y"]
["East Midlands","Derby Waste Sinfin Lane 33kV S Stn","DerbyWasteSinfinLane33kVSStn",875073,0.125,null,334,"",3,"Y"]
["South West","Derriton Fields Solar Park 33kV S Stn","DerritonFieldsSolarPark33kVSStn",358080,0.28499999999999998,null,500,"Y",3,"Y"]
["South Wales","Derwyn Solar Farm 33kV S Stn","DerwynSolarFarm33kVSStn",510407,0.14000000000000001,null,500,"Y",3,"Y"]
["East Midlands","Desborough 33/11kV S Stn","Desborough33/11kVSStn",920048,6.4000000000000001E-2,null,100,"",3,"Y"]
["East Midlands","Desford 33/11kV S Stn","Desford33/11kVSStn",930093,0.111,null,216,"",3,"Y"]
["South West","Devoran 33/11kV S Stn","Devoran33/11kVSStn",417310,2.1150000000000002,null,2563,"",3,"Y"]
["East Midlands","Dillotford Avenue 33/11kV S Stn","DillotfordAvenue33/11kVSStn",930042,6.7000000000000004E-2,null,162,"",3,"Y"]
["South West","Dinder 33/11kV S Stn","Dinder33/11kVSStn",160811,4.2699999999999996,null,4582,"",3,"Y"]
["South West","Dinder Farm Solar Park 33kV S Stn","DinderFarmSolarPark33kVSStn",168106,0.65600000000000003,null,500,"Y",3,"Y"]
["East Midlands","Doddington Park 33/11kV S Stn","DoddingtonPark33/11kVSStn",900028,7.9000000000000001E-2,null,146,"",3,"Y"]
["East Midlands","Donington 33/11kV S Stn","Donington33/11kVSStn",910024,0.128,null,192,"",3,"Y"]
["West Midlands","Donnington 33/11kV S Stn","Donnington33/11kVSStn",840010,7.8E-2,null,161,"",3,"Y"]
["South West","Dorchester Street 33/6.6kV S Stn","DorchesterStreet33/6.6kVSStn",164170,7.1999999999999995E-2,null,105,"",3,"Y"]
["West Midlands","Dothill 33/11kV S Stn","Dothill33/11kVSStn",840019,0.20799999999999999,null,386,"",3,"Y"]
["South Wales","Dowlais Grid 132/33kV S Stn","DowlaisGrid132/33kVSStn",550012,0.2,"Y",1000,"Y",3,"Y"]
["South Wales","Dowlais Stor Generation East 33kV S Stn","DowlaisStorGenerationEast33kVSStn",550403,0.3347,null,500,"Y",3,"Y"]
["South Wales","Dowlais STOR Generation West 33kV S Stn","DowlaisSTORGenerationWest33kVSStn",550354,0.52,null,500,"Y",3,"Y"]
["South West","Dowlish Ford 33/11kV S Stn","DowlishFord33/11kVSStn",250350,0.16,null,202,"",3,"Y"]
["East Midlands","Dowsby Fen 33/11kV S Stn","DowsbyFen33/11kVSStn",910025,0.154,null,394,"",3,"Y"]
["East Midlands","Drakelow 275/132kV S Stn","Drakelow275/132kVSStn",680005,0.2,"Y",2800,"Y",1,"Y"]
["East Midlands","Drakelow Solar Farm 33kV S Stn","DrakelowSolarFarm33kVSStn",875067,0.18,null,119,"",3,"Y"]
["West Midlands","Drayton Farm North 66/11kv S Stn","DraytonFarmNorth66/11kvSStn",778960,9.1999999999999998E-2,null,209,"",3,"Y"]
["South West","Drinnick 33/11kV S Stn","Drinnick33/11kVSStn",437370,0.96699999999999997,null,1462,"",3,"Y"]
["West Midlands","Droitwich 66/11kV S Stn","Droitwich66/11kVSStn",670115,9.8000000000000004E-2,null,141,"",3,"Y"]
["West Midlands","Dudbridge 33/11kV S Stn","Dudbridge33/11kVSStn",790009,0.17299999999999999,null,237,"",3,"Y"]
["West Midlands","Dudley 132/11kV S Stn","Dudley132/11kVSStn",670057,5.3999999999999999E-2,null,437,"",1,"Y"]
["South Wales","Duffryn Brodyn 33kV S Stn","DuffrynBrodyn33kVSStn",590298,0.7,"Y",500,"Y",3,"Y"]
["South West","Dunkeswell 33/11kV S Stn","Dunkeswell33/11kVSStn",310057,0.29099999999999998,null,203,"",3,"Y"]
["West Midlands","Dunlop 132kV S Stn","Dunlop132kVSStn",670029,0.23799999999999999,null,2222,"",1,"Y"]
["East Midlands","Dunlop 33/6.6kV S Stn","Dunlop33/6.6kVSStn",930039,9.8000000000000004E-2,null,218,"",3,"Y"]
["South West","Dunsland Cross Wind Farm 33kV S Stn","DunslandCrossWindFarm33kVSStn",358167,0.29799999999999999,null,500,"Y",3,"Y"]
["West Midlands","Dursley 33/11kV S Stn","Dursley33/11kVSStn",790021,6.7000000000000004E-2,null,120,"",3,"Y"]
["West Midlands","Dymock 66/11kV S Stn","Dymock66/11kVSStn",670143,0.314,null,891,"",3,"Y"]
["East Midlands","Eagle Centre 33/11kV S Stn","EagleCentre33/11kVSStn",870015,0.1,null,95,"",3,"Y"]
["East Midlands","Eakley Lanes North PV 33kV S Stn","EakleyLanesNorthPV33kVSStn",946140,0.152,null,156,"",3,"Y"]
["East Midlands","Eakley Lanes South PV 33kV S Stn","EakleyLanesSouthPV33kVSStn",946141,7.0000000000000007E-2,null,72,"",3,"Y"]
["East Midlands","Eakring Solar Farm 33kV S Stn","EakringSolarFarm33kVSStn",898340,0.22,null,395,"",3,"Y"]
["East Midlands","Earls Barton 33/11kV S Stn","EarlsBarton33/11kVSStn",940053,0.15,null,267,"",3,"Y"]
["East Midlands","Earlstrees 33/11kV S Stn","Earlstrees33/11kVSStn",920052,6.3E-2,null,118,"",3,"Y"]
["South Wales","East Aberthaw 132/33kV S Stn","EastAberthaw132/33kVSStn",510059,0.16,null,1000,"Y",3,"Y"]
["South West","Eastacombe Solar Farm 33kV S Stn","EastacombeSolarFarm33kVSStn",358022,0.33500000000000002,null,500,"Y",3,"Y"]
["South West","East Brent 33/11kV S Stn","EastBrent33/11kVSStn",181425,0.158,null,144,"",3,"Y"]
["South West","East Budleigh 33/11kV S Stn","EastBudleigh33/11kVSStn",310040,2.5,null,2390,"",3,"Y"]
["South West","East Chinnock 33/11kV S Stn","EastChinnock33/11kVSStn",250290,0.29599999999999999,null,413,"",3,"Y"]
["East Midlands","East Claydon 132/33kV S Stn","EastClaydon132/33kVSStn",690075,3.9E-2,null,936,"",3,"Y"]
["East Midlands","East Claydon 400/132kV S Stn","EastClaydon400/132kVSStn",690061,3.9E-2,null,936,"",1,"Y"]
["South West","East Curry 33/11kV S Stn","EastCurry33/11kVSStn",350015,0.93100000000000005,null,865,"",3,"Y"]
["West Midlands","Eastern Avenue 132/11kV S Stn","EasternAvenue132/11kVSStn",670058,3.9E-2,null,416,"",1,"Y"]
["West Midlands","Easthope 33/11kV S Stn","Easthope33/11kVSStn",840008,0.6,null,586,"",3,"Y"]
["South West","East Langford Solar Park 33kV S Stn","EastLangfordSolarPark33kVSStn",358017,0.28999999999999998,null,402,"",3,"Y"]
["East Midlands","East Leake 33/11kV S Stn","EastLeake33/11kVSStn",880023,0.14399999999999999,null,215,"",3,"Y"]
["East Midlands","Easton 33/11kV S Stn","Easton33/11kVSStn",910041,0.113,null,90,"",3,"Y"]
["South West","Easton-In-Gordano 33/11kV S Stn","Easton-In-Gordano33/11kVSStn",181414,0.189,null,417,"",3,"Y"]
["South West","Eastville 33/11kV S Stn","Eastville33/11kVSStn",110644,0.10199999999999999,null,500,"Y",3,"Y"]
["South West","East Yelland 132/33kV S Stn","EastYelland132/33kVSStn",260465,0.22,null,263,"",3,"Y"]
["South West","East Youlstone Windfarm 33kV S Stn","EastYoulstoneWindfarm33kVSStn",358114,0.7,null,500,"Y",3,"Y"]
["South Wales","Ebbw Vale 132/11kV S Stn","EbbwVale132/11kVSStn",550013,0.159,null,1000,"Y",1,"Y"]
["West Midlands","Eccleshall 33/11kV S Stn","Eccleshall33/11kVSStn",850010,0.20100000000000001,null,228,"",3,"Y"]
["East Midlands","Eckington 33/11kV S Stn","Eckington33/11kVSStn",890083,0.122,null,262,"",3,"Y"]
["South West","Edgarley 33/11kV S Stn","Edgarley33/11kVSStn",210110,0.14799999999999999,null,194,"",3,"Y"]
["West Midlands","EFW Javelin Park 33kV S Stn","EFWJavelinPark33kVSStn",795870,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","EFW Paving Way 33kV S Stn","EFWPavingWay33kVSStn",904540,7.3999999999999996E-2,null,164,"",3,"Y"]
["South West","Eggbuckland 33/11kV S Stn","Eggbuckland33/11kVSStn",330025,7.1999999999999995E-2,null,24,"",3,"Y"]
["East Midlands","Eldergate 33/11kV S Stn","Eldergate33/11kVSStn",940071,0.05,null,75,"",3,"Y"]
["South West","Elim Terrace 33/11kV S Stn","ElimTerrace33/11kVSStn",330019,0.16,null,281,"",3,"Y"]
["East Midlands","Ellesmere Avenue 33/11kV S Stn","EllesmereAvenue33/11kVSStn",940055,0.121,null,227,"",3,"Y"]
["West Midlands","Elmdon 132/11kV S Stn","Elmdon132/11kVSStn",670059,0.06,null,424,"",1,"Y"]
["East Midlands","Elms Farm Southam Solar Farm 33kV S Stn","ElmsFarmSouthamSolarFarm33kVSStn",939156,0.2,null,290,"",3,"Y"]
["West Midlands","Elton 33/11kV S Stn","Elton33/11kVSStn",790016,0.33800000000000002,null,403,"",3,"Y"]
["South Wales","Ely 33/11kV S Stn","Ely33/11kVSStn",510119,7.3999999999999996E-2,null,500,"Y",3,"Y"]
["East Midlands","Emberton Pv 33kv S Stn","EmbertonPv33kvSStn",946213,9.6000000000000002E-2,null,108,"",3,"Y"]
["South West","Emersons Green 33/11kV S Stn","EmersonsGreen33/11kVSStn",114391,0.33,null,144,"",3,"Y"]
["East Midlands","Empingham 33/11kV S Stn","Empingham33/11kVSStn",910056,0.10100000000000001,null,148,"",3,"Y"]
["East Midlands","Enderby 400/132kV S Stn","Enderby400/132kVSStn",690004,6.5000000000000002E-2,null,849,"",1,"Y"]
["West Midlands","Endon 33/11kV S Stn","Endon33/11kVSStn",850016,0.41299999999999998,null,909,"",3,"Y"]
["South Wales","Energlyn BSP 132/11kV S Stn","EnerglynBSP132/11kVSStn",540910,0.13800000000000001,null,1000,"Y",1,"Y"]
["South Wales","Energlyn Primary 33/11kV S Stn","EnerglynPrimary33/11kVSStn",540120,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","English Electric 33/11kV S Stn","EnglishElectric33/11kVSStn",930063,6.4000000000000001E-2,null,170,"",3,"Y"]
["South West","Entry Hill 33/6.6kV S Stn","EntryHill33/6.6kVSStn",160355,6.5000000000000002E-2,null,88,"",3,"Y"]
["West Midlands","Epwell 66/11kV S Stn","Epwell66/11kVSStn",670090,0.34,null,308,"",3,"Y"]
["East Midlands","Equitix ESI CHP Notts 33kV S Stn","EquitixESICHPNotts33kVSStn",917673,0.13,null,323,"",3,"Y"]
["West Midlands","Erdington 132/11kV S Stn","Erdington132/11kVSStn",670136,0.2,"Y",1000,"Y",1,"Y"]
["West Midlands","Erdington 132kV S Stn","Erdington132kVSStn",670034,0.121,null,581,"",1,"Y"]
["East Midlands","Erin Road 33/11kV S Stn","ErinRoad33/11kVSStn",898500,0.25,null,397,"",3,"Y"]
["East Midlands","Ermine Farm Solar Farm 33kV S Stn","ErmineFarmSolarFarm33kVSStn",916813,0.16,null,500,"Y",3,"Y"]
["South West","Ernesettle 132/33kV S Stn","Ernesettle132/33kVSStn",330001,0.153,null,1232,"",3,"Y"]
["South West","Ernesettle B & S 33/11kV S Stn","ErnesettleB&S33/11kVSStn",330038,0.153,null,216,"",3,"Y"]
["South West","Ernesettle Lane STOR Generator 33kV S Stn","ErnesettleLaneSTORGenerator33kVSStn",333743,0.156,null,1171,"",3,"Y"]
["South West","Evercreech 33/11kV S Stn","Evercreech33/11kVSStn",161823,0.129,null,103,"",3,"Y"]
["West Midlands","Evesham 66/11kV S Stn","Evesham66/11kVSStn",670097,0.14499999999999999,null,399,"",3,"Y"]
["South West","Exebridge 33/11kV S Stn","Exebridge33/11kVSStn",210140,1.25,null,689,"",3,"Y"]
["South West","Exeter City 132/33kV S Stn","ExeterCity132/33kVSStn",310001,0.1,null,467,"",3,"Y"]
["South West","Exeter Main 33kV S Stn","ExeterMain33kVSStn",310003,0.15,null,1648,"",3,"Y"]
["South West","Exeter Main 400/132kV S Stn","ExeterMain400/132kVSStn",306005,0.115,null,1648,"",1,"Y"]
["South West","Exeter Science Park 33/11kV S Stn","ExeterSciencePark33/11kVSStn",310060,0.32,null,500,"Y",3,"Y"]
["South West","Exminster 33/11kV S Stn","Exminster33/11kVSStn",310030,0.16400000000000001,null,187,"",3,"Y"]
["South West","Exmouth 132/33kV S Stn","Exmouth132/33kVSStn",310004,7.5999999999999998E-2,null,323,"",3,"Y"]
["South West","Exmouth Works 33/11kV S Stn","ExmouthWorks33/11kVSStn",310038,0.11,null,151,"",3,"Y"]
["East Midlands","Exton 33/11kV S Stn","Exton33/11kVSStn",910052,0.52800000000000002,null,737,"",3,"Y"]
["East Midlands","Eyam 33/11kV S Stn","Eyam33/11kVSStn",890066,0.5,null,685,"",3,"Y"]
["South Wales","Fairwater 33/11kV S Stn","Fairwater33/11kVSStn",510121,0.7,"Y",500,"Y",3,"Y"]
["South West","Falmouth Bickland Hill 33/11kV S Stn","FalmouthBicklandHill33/11kVSStn",417160,0.186,null,275,"",3,"Y"]
["South West","Falmouth Docks 33/11kV S Stn","FalmouthDocks33/11kVSStn",417180,0.13400000000000001,null,182,"",3,"Y"]
["South West","Faraday Road STOR Generator 33kV S Stn","FaradayRoadSTORGenerator33kVSStn",333718,0.124,null,500,"Y",3,"Y"]
["East Midlands","Farndon Road 33/11kV S Stn","FarndonRoad33/11kVSStn",920046,5.6000000000000001E-2,null,134,"",3,"Y"]
["East Midlands","Farnsfield 33/11kV S Stn","Farnsfield33/11kVSStn",890056,0.38700000000000001,null,766,"",3,"Y"]
["West Midlands","Feckenham 275/66/11kV S Stn","Feckenham275/66/11kVSStn",670003,7.2999999999999995E-2,null,1030,"",3,"Y"]
["South West","Feeder Road 132/33kV S Stn","FeederRoad132/33kVSStn",113449,0.05,null,251,"",3,"Y"]
["South West","Feeder Road 33kV S Stn","FeederRoad33kVSStn",113372,0.05,null,79,"",3,"Y"]
["South West","Feeder Road A 33/11kV S Stn","FeederRoadA33/11kVSStn",113373,0.05,null,140,"",3,"Y"]
["South West","Feeder Road B 33/11kV S Stn","FeederRoadB33/11kVSStn",113374,0.05,null,140,"",3,"Y"]
["South Wales","Felindre Pumping Station 33kV S Stn","FelindrePumpingStation33kVSStn",520326,0.26900000000000002,null,500,"Y",3,"Y"]
["East Midlands","Fen Farm 33/11kV S Stn","FenFarm33/11kVSStn",940023,9.0999999999999998E-2,null,194,"",3,"Y"]
["South Wales","Fenton Farm PV Generation 33kV S Stn","FentonFarmPVGeneration33kVSStn",600367,0.16,null,500,"Y",3,"Y"]
["South Wales","Ferndale Wind Farm 33kV S Stn","FerndaleWindFarm33kVSStn",540332,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Fernwood 33/11kV S Stn","Fernwood33/11kVSStn",900011,0.13200000000000001,null,318,"",3,"Y"]
["South Wales","Ffos Las PV Generation 33kV S Stn","FfosLasPVGeneration33kVSStn",520345,0.32400000000000001,null,500,"Y",3,"Y"]
["South Wales","Ffynnon Oer Wind Farm 66kV S Stn","FfynnonOerWindFarm66kVSStn",560320,2.2170000000000001,null,500,"Y",3,"Y"]
["East Midlands","Fields Farm Southam Solar Farm 33kV S Stn","FieldsFarmSouthamSolarFarm33kVSStn",939242,0.1,null,138,"",3,"Y"]
["East Midlands","Field Street 33/11kV S Stn","FieldStreet33/11kVSStn",920045,4.9000000000000002E-2,null,124,"",3,"Y"]
["South West","Filton Dc 33/11kV S Stn","FiltonDc33/11kVSStn",113369,0.13,null,201,"",3,"Y"]
["South Wales","Fishguard 33/11kV S Stn","Fishguard33/11kVSStn",600124,1.895,null,500,"Y",3,"Y"]
["East Midlands","Fiskerton 33/11kV S Stn","Fiskerton33/11kVSStn",900035,0.19,null,392,"",3,"Y"]
["East Midlands","Fiskerton Solar Farm 33kV S Stn","FiskertonSolarFarm33kVSStn",906387,8.4000000000000005E-2,null,229,"",3,"Y"]
["East Midlands","Flagg 33/11kV S Stn","Flagg33/11kVSStn",890064,2.2000000000000002,null,2640,"",3,"Y"]
["South West","Folly Bridge 33/11kV S Stn","FollyBridge33/11kVSStn",310016,0.621,null,631,"",3,"Y"]
["South West","Ford Farm Solar Farm 33kV S Stn","FordFarmSolarFarm33kVSStn",458047,1.1499999999999999,null,500,"Y",3,"Y"]
["South Wales","Fords Bridgend 132kV S Stn","FordsBridgend132kVSStn",560050,0.2,"Y",1000,"Y",1,"Y"]
["South West","Forestmoor 33/11kV S Stn","Forestmoor33/11kVSStn",350025,0.72,null,715,"",3,"Y"]
["West Midlands","Forsbrook 132/33kV S Stn","Forsbrook132/33kVSStn",680048,0.82,null,6239,"",3,"Y"]
["East Midlands","Fosse Way Radford Semele Solar Farm 33kV S Stn","FosseWayRadfordSemeleSolarFarm33kVSStn",939301,0.08,null,100,"",3,"Y"]
["West Midlands","Four Ashes 33/11kV S Stn","FourAshes33/11kVSStn",670124,0.189,null,230,"",3,"Y"]
["West Midlands","Four Ashes E F W 33kV S Stn","FourAshesEFW33kVSStn",670141,0.7,"Y",500,"Y",3,"Y"]
["South West","Four Burrows Blackdown Solar Park 33kV S Stn","FourBurrowsBlackdownSolarPark33kVSStn",418108,0.878,null,500,"Y",3,"Y"]
["South West","Fourburrows Pendown 33kV S Stn","FourburrowsPendown33kVSStn",418041,0.48,null,500,"Y",3,"Y"]
["South West","Four Burrows Windfarm 33kV S Stn","FourBurrowsWindfarm33kVSStn",417820,0.38200000000000001,null,845,"",3,"Y"]
["South West","Fowey 33/11kV S Stn","Fowey33/11kVSStn",437570,1.448,null,1725,"",3,"Y"]
["South West","Foxcombe Solar Park 33kV S Stn","FoxcombeSolarPark33kVSStn",358076,0.7,"Y",500,"Y",3,"Y"]
["South West","Foxhills 33/11kV S Stn","Foxhills33/11kVSStn",162344,0.16200000000000001,null,226,"",3,"Y"]
["East Midlands","Fox Milne 33/11kV S Stn","FoxMilne33/11kVSStn",940043,4.1000000000000002E-2,null,47,"",3,"Y"]
["South West","Fraddon 132/33kV S Stn","Fraddon132/33kVSStn",407380,0.27400000000000002,null,2392,"",3,"Y"]
["South West","Fraddon 33/11kV S Stn","Fraddon33/11kVSStn",437380,0.27400000000000002,null,2121,"",3,"Y"]
["South West","Francis Court Farm Solar Park 33kV S Stn","FrancisCourtFarmSolarPark33kVSStn",318118,0.41499999999999998,null,500,"Y",3,"Y"]
["South West","Freathy Farm Solar Park 33kV S Stn","FreathyFarmSolarPark33kVSStn",458089,0.7,"Y",500,"Y",3,"Y"]
["South West","Fremington 33/11kV S Stn","Fremington33/11kVSStn",260480,1.7090000000000001,null,2616,"",3,"Y"]
["East Midlands","French Farm Wind Farm 33kV S Stn","FrenchFarmWindFarm33kVSStn",917670,0.105,null,234,"",3,"Y"]
["West Midlands","Froghall 33/11kV S Stn","Froghall33/11kVSStn",850017,0.19400000000000001,null,238,"",3,"Y"]
["South West","Frys Hill Radio 33kV/LV S Stn","FrysHillRadio33kV/LVSStn",182000,0.7,"Y",500,"Y",3,"Y"]
["South West","Fulford Solar Park 33kV S Stn","FulfordSolarPark33kVSStn",318031,0.7,"Y",500,"Y",3,"Y"]
["South West","Fullabrook Windfarm 132kV S Stn","FullabrookWindfarm132kVSStn",260006,0.4,null,580,"",1,"Y"]
["South West","Galsworthy Wind Farm 132kV S Stn","GalsworthyWindFarm132kVSStn",357295,0.54,null,1400,"Y",1,"Y"]
["South West","Garlenick Wind Farm 33kV S Stn","GarlenickWindFarm33kVSStn",438084,1.306,null,500,"Y",3,"Y"]
["South Wales","Garn Farm Solar Park 33kV S Stn","GarnFarmSolarPark33kVSStn",560359,0.34,null,500,"Y",3,"Y"]
["South Wales","Garngoch 33/11kV S Stn","Garngoch33/11kVSStn",520127,0.29199999999999998,null,743,"",3,"Y"]
["East Midlands","Garnham Close STOR 33kV S Stn","GarnhamCloseSTOR33kVSStn",898530,0.2,null,102,"",3,"Y"]
["West Midlands","Garreg Lwyd Wind Farm 66kV S Stn","GarregLwydWindFarm66kVSStn",670153,2.2200000000000002,null,2743,"",3,"Y"]
["South West","Garvinack Farm Solar Park 33kV S Stn","GarvinackFarmSolarPark33kVSStn",418126,0.7,null,500,"Y",3,"Y"]
["South West","Gas Lane 33/11kV S Stn","GasLane33/11kVSStn",180003,3.7999999999999999E-2,null,36,"",3,"Y"]
["South Wales","Gas Yard 33/11kV S Stn","GasYard33/11kVSStn",540128,0.24199999999999999,null,500,"Y",3,"Y"]
["East Midlands","Gawcott Fields Solar Park 33kV S Stn","GawcottFieldsSolarPark33kVSStn",946154,7.4999999999999997E-2,null,69,"",3,"Y"]
["East Midlands","Gaydon 33/11kV S Stn","Gaydon33/11kVSStn",930057,0.28999999999999998,null,286,"",3,"Y"]
["East Midlands","Gec Test Bed Whetstone 33kV S Stn","GecTestBedWhetstone33kVSStn",930090,0.33,null,521,"",3,"Y"]
["East Midlands","Gedling 33/11kV S Stn","Gedling33/11kVSStn",880034,8.7999999999999995E-2,null,215,"",3,"Y"]
["South West","Geevor 33/11kV S Stn","Geevor33/11kVSStn",417040,3.4,null,2309,"",3,"Y"]
["South Wales","Gelliwern Isaf Pv Gen 33kV S Stn","GelliwernIsafPvGen33kVSStn",520392,0.42,null,500,"Y",3,"Y"]
["South West","Georgeham 33/11kV S Stn","Georgeham33/11kVSStn",260570,3.23,null,2061,"",3,"Y"]
["South Wales","Gethin Street Swansea 33/11kV S Stn","GethinStreetSwansea33/11kVSStn",520129,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Gipsy Lane 33/11kV S Stn","GipsyLane33/11kVSStn",930080,6.8000000000000005E-2,null,122,"",3,"Y"]
["South Wales","GKN Rod Mill 33kV S Stn","GKNRodMill33kVSStn",510928,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Glasbury 66/11kV S Stn","Glasbury66/11kVSStn",610133,1.099,null,1044,null,3,"Y"]
["South West","Glebe Farm 2 Solar Farm 33kV S Stn","GlebeFarm2SolarFarm33kVSStn",218044,0.69,null,578,null,3,"Y"]
["East Midlands","Glebe Farm Solar Park 33kV S Stn","GlebeFarmSolarPark33kVSStn",926242,0.08,null,52,"",3,"Y"]
["West Midlands","Gnosall 33/11kV S Stn","Gnosall33/11kVSStn",850009,0.16300000000000001,null,152,"",3,"Y"]
["East Midlands","Goitside 132/33kV S Stn","Goitside132/33kVSStn",680038,9.1999999999999998E-2,null,88,"",3,"Y"]
["East Midlands","Goitside 33/6.6kV S Stn","Goitside33/6.6kVSStn",890075,9.1999999999999998E-2,null,88,"",3,"Y"]
["East Midlands","Goitside 33kV S Stn","Goitside33kVSStn",890016,9.1999999999999998E-2,null,88,"",3,"Y"]
["South Wales","Golden Hill 132/33kV S Stn","GoldenHill132/33kVSStn",600014,0.24299999999999999,null,1000,"Y",3,"Y"]
["West Midlands","Goldenhill Bank 33/11kV S Stn","GoldenhillBank33/11kVSStn",850012,0.108,null,169,"",3,"Y"]
["South West","Goonhilly Solar Park 33kV S Stn","GoonhillySolarPark33kVSStn",418102,0.36,null,500,"Y",3,"Y"]
["South West","Goonhilly Wind Farm 33kV S Stn","GoonhillyWindFarm33kVSStn",415927,0.52,null,388,"",3,"Y"]
["South West","Gover Park Solar Park 33kV S Stn","GoverParkSolarPark33kVSStn",418096,0.54900000000000004,null,500,"Y",3,"Y"]
["South Wales","Gowerton East Grid 132/33kV S Stn","GowertonEastGrid132/33kVSStn",520045,0.156,null,1000,"Y",3,"Y"]
["South Wales","Gowerton STOR 33kV S Stn","GowertonSTOR33kVSStn",520427,0.27300000000000002,null,479,"",3,"Y"]
["South Wales","Grange 66kV S Stn","Grange66kVSStn",560015,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Grange Farm Solar Kirkby On Bain 33kV S Stn","GrangeFarmSolarKirkbyOnBain33kVSStn",906537,5.1999999999999998E-2,null,46,"",3,"Y"]
["South West","Grange Farm Solar Park 33kV S Stn","GrangeFarmSolarPark33kVSStn",218004,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Grangetown Grid Primary 132/11kV S Stn","GrangetownGridPrimary132/11kVSStn",510908,0.2,"Y",1000,"Y",1,"Y"]
["East Midlands","Grantham 132/33kV S Stn","Grantham132/33kVSStn",690041,0.3,null,1096,"",3,"Y"]
["East Midlands","Grantham 33kV S Stn","Grantham33kVSStn",910003,0.3,null,1096,"",3,"Y"]
["East Midlands","Grantham North 132/11kV S Stn","GranthamNorth132/11kVSStn",910018,0.104,null,376,"",1,"Y"]
["East Midlands","Grantham North 132/25/11kV S Stn","GranthamNorth132/25/11kVSStn",690031,0.104,null,376,"",1,"Y"]
["East Midlands","Grantham South 132/11kV S Stn","GranthamSouth132/11kVSStn",910036,0.2,null,700,"",1,"Y"]
["East Midlands","Grantham South 132kV S Stn","GranthamSouth132kVSStn",690032,0.2,null,700,"",1,"Y"]
["East Midlands","Grassmoor 33/11kV S Stn","Grassmoor33/11kVSStn",890084,0.08,null,182,"",3,"Y"]
["West Midlands","Great Alne 66/11kV S Stn","GreatAlne66/11kVSStn",670105,0.159,null,348,"",3,"Y"]
["East Midlands","Great Hale 33/11kV S Stn","GreatHale33/11kVSStn",900023,0.19600000000000001,null,226,"",3,"Y"]
["South West","Great Houndbeare Farm Solar Park 33kV S Stn","GreatHoundbeareFarmSolarPark33kVSStn",318164,0.22900000000000001,null,500,"Y",3,"Y"]
["East Midlands","Greatmoor Efw Calvert 33kv S Stn","GreatmoorEfwCalvert33kvSStn",946240,0.05,null,154,"",3,"Y"]
["South West","Great Torrington 33/11kV S Stn","GreatTorrington33/11kVSStn",260270,0.28999999999999998,null,234,"",3,"Y"]
["East Midlands","Green Lane Marchinton PV 33kV S Stn","GreenLaneMarchintonPV33kVSStn",875036,0.24,null,411,"",3,"Y"]
["East Midlands","Grendon 400/132kV S Stn","Grendon400/132kVSStn",690007,0.2,"Y",2800,"Y",1,"Y"]
["East Midlands","Gresley 132/33kV S Stn","Gresley132/33kVSStn",680035,0.11700000000000001,null,671,"",3,"Y"]
["East Midlands","Gresley 33/11kV S Stn","Gresley33/11kVSStn",870053,0.11700000000000001,null,671,"",3,"Y"]
["East Midlands","Gresley 33kV S Stn","Gresley33kVSStn",870010,0.11700000000000001,null,671,"",3,"Y"]
["East Midlands","Groby Road 33/11kV S Stn","GrobyRoad33/11kVSStn",920027,8.4000000000000005E-2,null,164,"",3,"Y"]
["East Midlands","Gulson Road 33/6.6kV S Stn","GulsonRoad33/6.6kVSStn",930043,9.8000000000000004E-2,null,206,"",3,"Y"]
["South West","Gunnislake 33/11kV S Stn","Gunnislake33/11kVSStn",457270,8.6,null,4954,"",3,"Y"]
["South Wales","Gwaun Cae Gurwen 33/11kV S Stn","GwaunCaeGurwen33/11kVSStn",520137,1.82,null,500,"Y",3,"Y"]
["East Midlands","Gypsum Solar Farm 33kV S Stn","GypsumSolarFarm33kVSStn",926431,0.08,null,112,"",3,"Y"]
["South Wales","Hafod Y Dafal Solar Park 33kV S Stn","HafodYDafalSolarPark33kVSStn",550402,0.59799999999999998,null,500,"Y",3,"Y"]
["West Midlands","Halesfield 33/11kV S Stn","Halesfield33/11kVSStn",840002,7.3999999999999996E-2,null,198,"",3,"Y"]
["West Midlands","Halesowen 132/11kV S Stn","Halesowen132/11kVSStn",670060,8.5000000000000006E-2,null,909,"",1,"Y"]
["East Midlands","Halfway 33/11kV S Stn","Halfway33/11kVSStn",890089,0.11799999999999999,null,184,"",3,"Y"]
["East Midlands","Hallcroft Road 33/11kV S Stn","HallcroftRoad33/11kVSStn",890052,0.20599999999999999,null,225,"",3,"Y"]
["East Midlands","Hall Farm Newbold Verdon 33kV S Stn","HallFarmNewboldVerdon33kVSStn",939122,0.22500000000000001,null,338,"",3,"Y"]
["West Midlands","Hall Farm Pv Awre 33kv S Stn","HallFarmPvAwre33kvSStn",795669,0.15,null,117,"",3,"Y"]
["West Midlands","Hall Green 132/11kV S Stn","HallGreen132/11kVSStn",670028,7.5999999999999998E-2,null,516,"",1,"Y"]
["South West","Halse Solar Farm 33kV S Stn","HalseSolarFarm33kVSStn",218043,0.09,null,112,null,3,"Y"]
["East Midlands","Hamilton 33/11kV S Stn","Hamilton33/11kVSStn",920044,7.8E-2,null,204,"",3,"Y"]
["West Midlands","Hammerley Down 33/11kV S Stn","HammerleyDown33/11kVSStn",790025,0.50600000000000001,null,582,"",3,"Y"]
["West Midlands","Hams Hall 132/33kV S Stn","HamsHall132/33kVSStn",670033,0.105,null,1775,"",3,"Y"]
["West Midlands","Hams Hall South 132/11kV S Stn","HamsHallSouth132/11kVSStn",670043,0.08,null,1115,"",1,"Y"]
["East Midlands","Handley Park Solar Park 33kv S Stn","HandleyParkSolarPark33kvSStn",946180,0.11,null,109,"",3,"Y"]
["East Midlands","Hanslope Park 33/11kV S Stn","HanslopePark33/11kVSStn",940022,0.13100000000000001,null,192,"",3,"Y"]
["East Midlands","Harbury 132/33kV S Stn","Harbury132/33kVSStn",690010,0.06,null,281,"",3,"Y"]
["East Midlands","Harbury 33/11kV S Stn","Harbury33/11kVSStn",930058,0.06,null,281,"",3,"Y"]
["East Midlands","Harbury 33kV S Stn","Harbury33kVSStn",930011,0.06,null,281,"",3,"Y"]
["West Midlands","Harlescott 33/11kV S Stn","Harlescott33/11kVSStn",840021,6.3E-2,null,214,"",3,"Y"]
["East Midlands","Harrold 33/11kV S Stn","Harrold33/11kVSStn",920061,0.156,null,232,"",3,"Y"]
["West Midlands","Hartlebury 66/11kV S Stn","Hartlebury66/11kVSStn",765589,0.28100000000000003,null,281,"",3,"Y"]
["West Midlands","Hartlebury EFW 66kV S Stn","HartleburyEFW66kVSStn",778880,0.28100000000000003,null,281,"",3,"Y"]
["East Midlands","Hartwell Road 33kV S Stn","HartwellRoad33kVSStn",946139,6.9000000000000006E-2,null,142,"",3,"Y"]
["South West","Hatchlands Farm Solar Park 33kV S Stn","HatchlandsFarmSolarPark33kVSStn",348045,0.4,null,500,"Y",3,"Y"]
["South West","Hatherleigh 33/11kV S Stn","Hatherleigh33/11kVSStn",350019,0.155,null,177,"",3,"Y"]
["East Midlands","Hatton 33/11kV S Stn","Hatton33/11kVSStn",870031,4.3999999999999997E-2,null,88,"",3,"Y"]
["East Midlands","Hatton Gas Compressor 132kV S Stn","HattonGasCompressor132kVSStn",690064,0.15,null,480,"",1,"Y"]
["South West","Haven Road 33/11kV S Stn","HavenRoad33/11kVSStn",310049,0.19,null,253,"",3,"Y"]
["South Wales","Haverfordwest 33/11kV S Stn","Haverfordwest33/11kVSStn",600017,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Haverfordwest Grid 132/33kV S Stn","HaverfordwestGrid132/33kVSStn",600016,0.45900000000000002,null,1000,"Y",3,"Y"]
["South Wales","Haverfordwest Solar Park 33kV S Stn","HaverfordwestSolarPark33kVSStn",600387,0.28000000000000003,null,83,"",3,"Y"]
["South West","Hawkers Farm Solar Park 33kV S Stn","HawkersFarmSolarPark33kVSStn",188124,0.109,null,500,"Y",3,"Y"]
["East Midlands","Hawkesmill Lane 33/6.6kV S Stn","HawkesmillLane33/6.6kVSStn",930028,0.152,null,269,"",3,"Y"]
["East Midlands","Hawton 132/33kV S Stn","Hawton132/33kVSStn",690042,7.0000000000000007E-2,null,469,"",3,"Y"]
["East Midlands","Hawton 33/11kV S Stn","Hawton33/11kVSStn",900026,7.0000000000000007E-2,null,469,"",3,"Y"]
["East Midlands","Hawton 33kV S Stn","Hawton33kVSStn",900003,7.0000000000000007E-2,null,469,"",3,"Y"]
["East Midlands","Hawton Wind Farm 33kV S Stn","HawtonWindFarm33kVSStn",906972,0.27,null,684,"",3,"Y"]
["South West","Haye Lane Solar Park 33kV S Stn","HayeLaneSolarPark33kVSStn",458030,0.112,null,500,"Y",3,"Y"]
["West Midlands","Hayford Solar Farm 33kV S Stn","HayfordSolarFarm33kVSStn",840844,0.14000000000000001,null,202,"",3,"Y"]
["South West","Hayle 132/33kV S Stn","Hayle132/33kVSStn",407150,9.5000000000000001E-2,null,112,"",3,"Y"]
["South West","Hayle 33/11kV S Stn","Hayle33/11kVSStn",417150,9.5000000000000001E-2,null,131,"",3,"Y"]
["South West","Hazard Farm Solar Park 33kV S Stn","HazardFarmSolarPark33kVSStn",348077,0.496,null,500,"Y",3,"Y"]
["East Midlands","Hazelwood 33/11kV S Stn","Hazelwood33/11kVSStn",920050,0.13,null,2117,"",3,"Y"]
["East Midlands","Heanor 132/33kV S Stn","Heanor132/33kVSStn",680036,9.5000000000000001E-2,null,522,"",3,"Y"]
["East Midlands","Heanor 33/11kV S Stn","Heanor33/11kVSStn",870022,9.5000000000000001E-2,null,522,"",3,"Y"]
["East Midlands","Heanor 33kV S Stn","Heanor33kVSStn",870007,9.5000000000000001E-2,null,522,"",3,"Y"]
["South Wales","Heath 33/11kV S Stn","Heath33/11kVSStn",510141,0.7,"Y",500,"Y",3,"Y"]
["South West","Heathfield Landfill 33kV S Stn","HeathfieldLandfill33kVSStn",340043,0.28999999999999998,null,341,"",3,"Y"]
["South Wales","Heath Hospital Primary 33/11kV S Stn","HeathHospitalPrimary33/11kVSStn",510327,0.7,"Y",500,"Y",3,"Y"]
["South West","Heavitree 33/11kV S Stn","Heavitree33/11kVSStn",310029,0.26,null,323,"",3,"Y"]
["South West","Heddon Cross 33/11kV S Stn","HeddonCross33/11kVSStn",260430,1.68,null,1054,"",3,"Y"]
["South West","Hele Manor STOR 33kV S Stn","HeleManorSTOR33kVSStn",218045,0.26500000000000001,null,133,"",3,"Y"]
["South West","Helston 33/11kV S Stn","Helston33/11kVSStn",417050,0.25900000000000001,null,336,"",3,"Y"]
["South West","Hemerdon Mine 33/11kV S Stn","HemerdonMine33/11kVSStn",333760,0.53,null,500,"Y",3,"Y"]
["South West","Hemyock 33/11kV S Stn","Hemyock33/11kVSStn",310056,0.60699999999999998,null,715,"",3,"Y"]
["South Wales","Hendai Solar Farm 33kV S Stn","HendaiSolarFarm33kVSStn",550378,0.39,null,500,"Y",3,"Y"]
["South Wales","Hendre Fawr Solar Farm 33/11kV S Stn","HendreFawrSolarFarm33/11kVSStn",550375,0.16,null,500,"Y",3,"Y"]
["South Wales","Hendy 33/11kV S Stn","Hendy33/11kVSStn",520142,0.29299999999999998,null,500,"Y",3,"Y"]
["West Midlands","Henley Solar Farm 33kV S Stn","HenleySolarFarm33kVSStn",745465,0.126,null,252,"",3,"Y"]
["West Midlands","Hereford 132/66kV S Stn","Hereford132/66kVSStn",670013,0.129,null,647,"",3,"Y"]
["West Midlands","Hereford Central 66/11kv S Stn","HerefordCentral66/11kvSStn",670151,0.156,null,279,"",3,"Y"]
["West Midlands","Hereford North 66/11kV S Stn","HerefordNorth66/11kVSStn",670096,9.6000000000000002E-2,null,141,"",3,"Y"]
["West Midlands","Hereford South 66/11kV S Stn","HerefordSouth66/11kVSStn",670103,0.16600000000000001,null,266,"",3,"Y"]
["East Midlands","Hermitage Lane Generation 33kV S Stn","HermitageLaneGeneration33kVSStn",898541,0.61,null,325,"",3,"Y"]
["South West","Hewas Solar Farm 33kV S Stn","HewasSolarFarm33kVSStn",438066,0.32,null,500,"Y",3,"Y"]
["South West","Hewlett Packard 33/11kV S Stn","HewlettPackard33/11kVSStn",113720,6.3E-2,null,28,"",3,"Y"]
["South West","Hewlett Packard 33kV S Stn","HewlettPackard33kVSStn",114632,6.3E-2,null,500,"Y",3,"Y"]
["South West","Hexworthy Barton Solar Park 33kV S Stn","HexworthyBartonSolarPark33kVSStn",458086,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Heywood Grange PV Farm 33kV S Stn","HeywoodGrangePVFarm33kVSStn",863413,0.21,null,556,"",3,"Y"]
["East Midlands","Higham Ferrers Switching Station 33kV S Stn","HighamFerrersSwitchingStation33kVSStn",926264,0.27,null,331,"",3,"Y"]
["South West","Higher Berechapel Farm Solar Park 33kV S Stn","HigherBerechapelFarmSolarPark33kVSStn",258083,0.7,"Y",500,"Y",3,"Y"]
["South West","Higher Bye Farm Solar Park 33kV S Stn","HigherByeFarmSolarPark33kVSStn",218021,6.5000000000000002E-2,null,500,"Y",3,"Y"]
["South West","Higher North Beer Farm Solar Park 33kV S Stn","HigherNorthBeerFarmSolarPark33kVSStn",358056,0.20699999999999999,null,500,"Y",3,"Y"]
["South West","Higher Tregarne Solar Farm 33kV S Stn","HigherTregarneSolarFarm33kVSStn",418049,1.04,null,500,"Y",3,"Y"]
["South West","Higher Trenhayle Farm Solar Park 33kV S Stn","HigherTrenhayleFarmSolarPark33kVSStn",418034,0.93300000000000005,null,500,"Y",3,"Y"]
["South West","Higher Trevartha Solar Farm 33kV S Stn","HigherTrevarthaSolarFarm33kVSStn",458048,1.46,null,500,"Y",3,"Y"]
["South West","Higher Woodway 33/11kV S Stn","HigherWoodway33/11kVSStn",340018,0.16800000000000001,null,198,"",3,"Y"]
["East Midlands","Highfields 33/11kV S Stn","Highfields33/11kVSStn",920036,9.8000000000000004E-2,null,318,"",3,"Y"]
["South West","High Littleton 33/11kV S Stn","HighLittleton33/11kVSStn",161532,0.24,null,401,"",3,"Y"]
["South Wales","Highmead 33/11kV S Stn","Highmead33/11kVSStn",510144,4.5999999999999999E-2,null,96,"",3,"Y"]
["West Midlands","High Offley 33/11kV S Stn","HighOffley33/11kVSStn",850004,0.5,null,526,"",3,"Y"]
["West Midlands","High Point Solar Pv 33kv S Stn","HighPointSolarPv33kvSStn",745501,9.8000000000000004E-2,null,128,"",3,"Y"]
["West Midlands","Highters Heath 132/11kV S Stn","HightersHeath132/11kVSStn",670061,6.5000000000000002E-2,null,469,"",1,"Y"]
["South West","Hill Barton Primary 33/11kV S Stn","HillBartonPrimary33/11kVSStn",310061,0.16900000000000001,null,500,"Y",3,"Y"]
["West Midlands","Hill Chorlton 33/11kV S Stn","HillChorlton33/11kVSStn",850003,0.67700000000000005,null,193,"",3,"Y"]
["East Midlands","Hill Farm Battery Generation 33kV S Stn","HillFarmBatteryGeneration33kVSStn",939476,0.38700000000000001,null,617,"",3,"Y"]
["East Midlands","Hillmorton 33/11kV S Stn","Hillmorton33/11kVSStn",930067,7.0000000000000007E-2,null,182,"",3,"Y"]
["South Wales","Hill Solar Farm 33kV S Stn","HillSolarFarm33kVSStn",550390,0.95,null,500,"Y",3,"Y"]
["East Midlands","Hinckley 132/11kV S Stn","Hinckley132/11kVSStn",930103,0.159,null,872,"",1,"Y"]
["East Midlands","Hinckley 132/33/11kV S Stn","Hinckley132/33/11kVSStn",690029,0.159,null,872,"",3,"Y"]
["East Midlands","Hinckley 33kV S Stn","Hinckley33kVSStn",930019,0.159,null,872,"",3,"Y"]
["East Midlands","Hindlow 33/11kV S Stn","Hindlow33/11kVSStn",890063,1.3,null,2200,"",3,"Y"]
["West Midlands","Hinksford 132/33/11kV S Stn","Hinksford132/33/11kVSStn",670062,0.12,null,1079,"",3,"Y"]
["West Midlands","Hinksford Farm Generation 33kV S Stn","HinksfordFarmGeneration33kVSStn",736183,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Hinstock 33/11kV S Stn","Hinstock33/11kVSStn",850007,0.56999999999999995,null,689,"",3,"Y"]
["South Wales","Hirwaun 132/33kV S Stn","Hirwaun132/33kVSStn",550018,0.21299999999999999,null,1000,"Y",3,"Y"]
["South Wales","Hirwaun STOR Generation 33kV S Stn","HirwaunSTORGeneration33kVSStn",550343,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Hockley 132/11kv S Stn","Hockley132/11kvSStn",670200,0.08,null,240,"",1,"Y"]
["East Midlands","Hockley Farm Road 33/11kV S Stn","HockleyFarmRoad33/11kVSStn",926144,0.1,null,331,"",3,"Y"]
["East Midlands","Holbeach 33/11kV S Stn","Holbeach33/11kVSStn",910026,7.5999999999999998E-2,null,111,"",3,"Y"]
["East Midlands","Holbrook Lane 33/6.6kV S Stn","HolbrookLane33/6.6kVSStn",930038,0.04,null,73,"",3,"Y"]
["South West","Holford 33/11kV S Stn","Holford33/11kVSStn",210560,1.7,null,430,"",3,"Y"]
["South West","Hollicombe 33/11kV S Stn","Hollicombe33/11kVSStn",340033,0.08,null,23,"",3,"Y"]
["East Midlands","Holme Carr 33/11kV S Stn","HolmeCarr33/11kVSStn",890042,0.314,null,566,"",3,"Y"]
["South West","Holsworthy 33/11kV S Stn","Holsworthy33/11kVSStn",350014,0.251,null,402,"",3,"Y"]
["East Midlands","Holtwood Farm Solar Park 33kV S Stn","HoltwoodFarmSolarPark33kVSStn",875065,0.22,null,274,"",3,"Y"]
["East Midlands","Holwell 33/11kV S Stn","Holwell33/11kVSStn",910044,7.6999999999999999E-2,null,106,"",3,"Y"]
["East Midlands","Holyhead Road 33/11kV S Stn","HolyheadRoad33/11kVSStn",930037,5.1999999999999998E-2,null,90,"",3,"Y"]
["East Midlands","Homestead Solar Park 33kV S Stn","HomesteadSolarPark33kVSStn",946176,0.27100000000000002,null,306,"",3,"Y"]
["South West","Honiton Heathfield 33/11kV S Stn","HonitonHeathfield33/11kVSStn",310042,0.21099999999999999,null,180,"",3,"Y"]
["West Midlands","Hookgate 33/11kV S Stn","Hookgate33/11kVSStn",850006,0.54,null,1030,"",3,"Y"]
["South West","Hope Solar Park 33kV S Stn","HopeSolarPark33kVSStn",418029,0.432,null,500,"Y",3,"Y"]
["South Wales","Hoplass Solar Farm PV Generation 33kV S Stn","HoplassSolarFarmPVGeneration33kVSStn",600355,0.32,null,500,"Y",3,"Y"]
["East Midlands","Hopton 33/11kV S Stn","Hopton33/11kVSStn",890071,1.1970000000000001,null,1831,"",3,"Y"]
["East Midlands","Horncastle 33/11kV S Stn","Horncastle33/11kVSStn",900013,0.127,null,251,"",3,"Y"]
["South West","Horsacott Solar Farm 33kV S Stn","HorsacottSolarFarm33kVSStn",268004,0.17,null,500,"Y",3,"Y"]
["East Midlands","Horsemoor Drove Solar 33kV S Stn","HorsemoorDroveSolar33kVSStn",917574,0.06,null,121,"",3,"Y"]
["West Midlands","Hortonwood 132/11kV S Stn","Hortonwood132/11kVSStn",680060,0.111,null,876,"",1,"Y"]
["West Midlands","Howard Road STOR 66kV S Stn","HowardRoadSTOR66kVSStn",779441,0.7,"Y",500,"Y",3,"Y"]
["South West","Howton Farm Solar Park 33kV S Stn","HowtonFarmSolarPark33kVSStn",458013,0.57999999999999996,null,1148,"",3,"Y"]
["East Midlands","Hucknall 33/11kV S Stn","Hucknall33/11kVSStn",880011,0.191,null,285,"",3,"Y"]
["South West","Huntworth Generator 33kV S Stn","HuntworthGenerator33kVSStn",210270,0.219,null,494.9,"",3,"Y"]
["South West","Hurcott 33kV S Stn","Hurcott33kVSStn",258130,0.55000000000000004,null,500,"Y",3,"Y"]
["South West","Hurcott Solar Park 33kV S Stn","HurcottSolarPark33kVSStn",258127,8.4000000000000005E-2,null,500,"Y",3,"Y"]
["East Midlands","Huthwaite 33/11kV S Stn","Huthwaite33/11kVSStn",890027,7.9000000000000001E-2,null,132,"",3,"Y"]
["West Midlands","I54 33/11kv S Stn","I5433/11kvSStn",735832,0.7,"Y",500,"Y",3,"Y"]
["South West","Ilfracombe 33/11kV S Stn","Ilfracombe33/11kVSStn",260230,0.36899999999999999,null,349,"",3,"Y"]
["East Midlands","Ilkeston 33/11kV S Stn","Ilkeston33/11kVSStn",870048,0.17,null,276,"",3,"Y"]
["South Wales","Inco Europe South 33kV S Stn","IncoEuropeSouth33kVSStn",520147,0.21,null,500,"Y",3,"Y"]
["South West","Indian Queens 400/132kV S Stn","IndianQueens400/132kVSStn",406002,0.2,"Y",3070,"",1,"Y"]
["East Midlands","Infinity Park 33/11kv S Stn","InfinityPark33/11kvSStn",875136,0.14799999999999999,null,410,"",3,"Y"]
["East Midlands","Ingoldmells 33/11kV S Stn","Ingoldmells33/11kVSStn",900017,0.105,null,210,"",3,"Y"]
["East Midlands","Interlink Park 33/11 Kv S Stn","InterlinkPark33/11KvSStn",930084,0.17100000000000001,null,380,"",3,"Y"]
["West Midlands","Ipsley 66/11kV S Stn","Ipsley66/11kVSStn",670120,6.8000000000000005E-2,null,146,"",3,"Y"]
["East Midlands","Irchester Road Switching Station 33kV S Stn","IrchesterRoadSwitchingStation33kVSStn",926349,0.309,null,200,"",3,"Y"]
["South West","Iron Acton 275/132kV S Stn","IronActon275/132kVSStn",106009,0.2,"Y",1486,"",1,"Y"]
["West Midlands","Iron Acton 275/132kV S Stn","IronActon275/132kVSStn",670001,0.09,null,1503,"",1,"Y"]
["West Midlands","Ironbridge 132/33kV S Stn","Ironbridge132/33kVSStn",680025,0.04,null,91,"",3,"Y"]
["South Wales","Ironbridge 33/11kV S Stn","Ironbridge33/11kVSStn",510148,7.3999999999999996E-2,null,163,"",3,"Y"]
["West Midlands","Ironbridge 400/132kV S Stn","Ironbridge400/132kVSStn",680000,0.06,null,1245,"",1,"Y"]
["East Midlands","Irthlingborough 132/33kV S Stn","Irthlingborough132/33kVSStn",690049,6.5000000000000002E-2,null,131,"",3,"Y"]
["East Midlands","Irthlingborough 33/11kV S Stn","Irthlingborough33/11kVSStn",921092,6.5000000000000002E-2,null,131,"",3,"Y"]
["East Midlands","Irthlingborough 33kV S Stn","Irthlingborough33kVSStn",928000,6.5000000000000002E-2,null,131,"",3,"Y"]
["South West","Isles Of Scilly 33/11kV S Stn","IslesOfScilly33/11kVSStn",417760,0.52400000000000002,null,214,"",3,"Y"]
["South West","Ivybridge 33/11kV S Stn","Ivybridge33/11kVSStn",330030,0.20200000000000001,null,245,"",3,"Y"]
["South West","Iwood Lane Solar Park 33kV S Stn","IwoodLaneSolarPark33kVSStn",188122,8.5000000000000006E-2,null,500,"Y",3,"Y"]
["East Midlands","Jaguar Browns Lane 33/11kv S Stn","JaguarBrownsLane33/11kvSStn",930029,9.2999999999999999E-2,null,160,"",3,"Y"]
["East Midlands","Jaguar Land Rover 33/11kV S Stn","JaguarLandRover33/11kVSStn",939305,0.28999999999999998,null,286,"",3,"Y"]
["South Wales","Jersey Marine 33/11kV S Stn","JerseyMarine33/11kVSStn",520284,9.2999999999999999E-2,null,500,"Y",3,"Y"]
["South Wales","Jesus College P V Generation 33kV S Stn","JesusCollegePVGeneration33kVSStn",510398,0.16200000000000001,null,500,"Y",3,"Y"]
["East Midlands","JLR Whitley 33/11kV S Stn","JLRWhitley33/11kVSStn",939482,0.7,null,340,"",3,"Y"]
["South Wales","Jordanston Farm PV Generation 33kV S Stn","JordanstonFarmPVGeneration33kVSStn",600350,0.5,null,500,"Y",3,"Y"]
["East Midlands","Jupiter 33/11kV S Stn","Jupiter33/11kVSStn",920028,7.4999999999999997E-2,null,153,"",3,"Y"]
["East Midlands","Kelmarsh Wind Farm 33kV S Stn","KelmarshWindFarm33kVSStn",926263,0.15,null,329,"",3,"Y"]
["East Midlands","Kenilworth 33/11kV S Stn","Kenilworth33/11kVSStn",930050,0.08,null,142,"",3,"Y"]
["West Midlands","Kenswick 66/11kV S Stn","Kenswick66/11kVSStn",670116,0.48699999999999999,null,360,"",3,"Y"]
["South West","Kerriers Solar Park 33kV S Stn","KerriersSolarPark33kVSStn",438099,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Ketley 132/33/11kV S Stn","Ketley132/33/11kVSStn",680024,0.09,null,720,"",3,"Y"]
["East Midlands","Kettering 132/33kV S Stn","Kettering132/33kVSStn",690050,0.02,null,168,"",3,"Y"]
["East Midlands","Kettering 33kV S Stn","Kettering33kVSStn",920008,0.02,null,168,"",3,"Y"]
["East Midlands","Kettering North 33/11kV S Stn","KetteringNorth33/11kVSStn",920013,5.8999999999999997E-2,null,142,"",3,"Y"]
["East Midlands","Ketton Cement 33/11kV S Stn","KettonCement33/11kVSStn",910051,0.17299999999999999,null,284,"",3,"Y"]
["South West","Keynsham East 33/11kV S Stn","KeynshamEast33/11kVSStn",111481,0.108,null,130,"",3,"Y"]
["South West","Keynsham West 33/11kV S Stn","KeynshamWest33/11kVSStn",113180,0.108,null,170,"",3,"Y"]
["East Midlands","Keyworth 33/11kV S Stn","Keyworth33/11kVSStn",880033,0.105,null,211,"",3,"Y"]
["East Midlands","Kibworth 132/33kV S Stn","Kibworth132/33kVSStn",690028,9.5000000000000001E-2,null,319,"",3,"Y"]
["East Midlands","Kibworth 33/11kV S Stn","Kibworth33/11kVSStn",920043,9.5000000000000001E-2,null,319,"",3,"Y"]
["East Midlands","Kibworth 33kV S Stn","Kibworth33kVSStn",920001,9.5000000000000001E-2,null,319,"",3,"Y"]
["West Midlands","Kidderminster 132/33/11kV S Stn","Kidderminster132/33/11kVSStn",670063,0.24,null,1546,"",3,"Y"]
["West Midlands","Kidsgrove 132/25kV S Stn","Kidsgrove132/25kVSStn",680044,9.5000000000000001E-2,null,826,"",1,"Y"]
["South Wales","Kidwelly 33/11kV S Stn","Kidwelly33/11kVSStn",520286,0.748,null,500,"Y",3,"Y"]
["East Midlands","Kiln Farm 33/11kV S Stn","KilnFarm33/11kVSStn",940034,3.5000000000000003E-2,null,93,"",3,"Y"]
["East Midlands","Kilton Road 33/11kV S Stn","KiltonRoad33/11kVSStn",890043,0.23799999999999999,null,395,"",3,"Y"]
["South West","Kingsbridge 33/11kV S Stn","Kingsbridge33/11kVSStn",340016,0.18,null,118,"",3,"Y"]
["South West","Kingsland Barton Solar Park 33kV S Stn","KingslandBartonSolarPark33kVSStn",268007,0.29199999999999998,null,500,"Y",3,"Y"]
["West Midlands","Kingsley Holt 33/11kV S Stn","KingsleyHolt33/11kVSStn",850018,0.221,null,351,"",3,"Y"]
["West Midlands","Kingstanding 132/11kV S Stn","Kingstanding132/11kVSStn",670128,0.23,null,265,"",1,"Y"]
["East Midlands","Kingsthorpe 33/11kV S Stn","Kingsthorpe33/11kVSStn",940060,0.11899999999999999,null,223,"",3,"Y"]
["East Midlands","Kingston 33/11kV S Stn","Kingston33/11kVSStn",940070,0.06,null,136,"",3,"Y"]
["South West","Kingsweston 33/11kV S Stn","Kingsweston33/11kVSStn",113339,0.11,null,206,"",3,"Y"]
["West Midlands","Kington 66/11kV S Stn","Kington66/11kVSStn",670114,0.38500000000000001,null,454,"",3,"Y"]
["West Midlands","Kinver 33/11kV S Stn","Kinver33/11kVSStn",770005,1.2130000000000001,null,1237,"",3,"Y"]
["East Midlands","Kirton 33/11kV S Stn","Kirton33/11kVSStn",910022,9.6000000000000002E-2,null,192,"",3,"Y"]
["West Midlands","Kitts Green 132/11kV S Stn","KittsGreen132/11kVSStn",670030,0.125,null,635,"",1,"Y"]
["West Midlands","Kitwell 275/132kV S Stn","Kitwell275/132kVSStn",670011,0.126,null,2528,"",1,"Y"]
["West Midlands","Knighton 66/11kV S Stn","Knighton66/11kVSStn",670121,0.97299999999999998,null,973,"",3,"Y"]
["South West","Knockworthy Farm Solar Park 33kV S Stn","KnockworthyFarmSolarPark33kVSStn",268001,0.57999999999999996,null,500,"Y",3,"Y"]
["West Midlands","Knypersley 33/11kV S Stn","Knypersley33/11kVSStn",850015,0.15,null,418,"",3,"Y"]
["South Wales","Lady Windsor 33/11kV S Stn","LadyWindsor33/11kVSStn",550149,0.53700000000000003,null,500,"Y",3,"Y"]
["West Midlands","Ladywood 132/11kV S Stn","Ladywood132/11kVSStn",670040,0.17299999999999999,null,1358,"",1,"Y"]
["South Wales","Lampeter Primary 132/33kV S Stn","LampeterPrimary132/33kVSStn",590020,0.2,"Y",1000,"Y",3,"Y"]
["South West","Landulph 132/33kV S Stn","Landulph132/33kVSStn",457710,0.32,null,3050,"",3,"Y"]
["South West","Landulph GSP 400/132kV S Stn","LandulphGSP400/132kVSStn",406003,0.43,null,3182,"",1,"Y"]
["South West","Laneast 33/11kV S Stn","Laneast33/11kVSStn",457620,5.55,null,2270,"",3,"Y"]
["South West","Langage 33/11kV S Stn","Langage33/11kVSStn",330042,0.121,null,157,"",3,"Y"]
["South West","Langage Energy Centre 33kV S Stn","LangageEnergyCentre33kVSStn",330047,0.61699999999999999,null,5577,"",3,"Y"]
["East Midlands","Langar Solar Switch Room 33kV S Stn","LangarSolarSwitchRoom33kVSStn",883446,0.16400000000000001,null,198,"",3,"Y"]
["East Midlands","Langdale Drive 33/11kV S Stn","LangdaleDrive33/11kVSStn",930081,0.112,null,202,"",3,"Y"]
["East Midlands","Langrick 33/11kV S Stn","Langrick33/11kVSStn",900021,0.22900000000000001,null,307,"",3,"Y"]
["South West","Langunnett Farm Solar Farm 33kV S Stn","LangunnettFarmSolarFarm33kVSStn",438059,0.38,null,500,"Y",3,"Y"]
["South West","Lanner 33/11kV S Stn","Lanner33/11kVSStn",417030,8.4740000000000002,null,4813,"",3,"Y"]
["South West","Lanreath 33/11kV S Stn","Lanreath33/11kVSStn",437460,1.4710000000000001,null,1352,"",3,"Y"]
["South West","Lapford 33/11kV S Stn","Lapford33/11kVSStn",310013,0.73099999999999998,null,681,"",3,"Y"]
["West Midlands","Larport Farm 66kV S Stn","LarportFarm66kVSStn",756542,0.7,"Y",500,"Y",3,"Y"]
["South West","Launceston 33/11kV S Stn","Launceston33/11kVSStn",457250,0.13,null,296,"",3,"Y"]
["South West","Lawes Bridge 33/11kV S Stn","LawesBridge33/11kVSStn",340025,0.26,null,384,"",3,"Y"]
["East Midlands","Lawford 33/11kV S Stn","Lawford33/11kVSStn",930055,5.1999999999999998E-2,null,134,"",3,"Y"]
["South West","Lawrence Weston Solar Park 33kV S Stn","LawrenceWestonSolarPark33kVSStn",118166,0.186,null,278.8,"",3,"Y"]
["South West","Laywell 33/11kV S Stn","Laywell33/11kVSStn",341542,0.7,"Y",500,"Y",3,"Y"]
["South West","Laywell Brixham 33/11kV S Stn","LaywellBrixham33/11kVSStn",340035,0.39500000000000002,null,499,"",3,"Y"]
["East Midlands","Leadenham 33/11kV S Stn","Leadenham33/11kVSStn",910058,8.5999999999999993E-2,null,248,"",3,"Y"]
["East Midlands","Lea Marston 400/132kV S Stn","LeaMarston400/132kVSStn",720004,0.2,"Y",2800,"Y",1,"Y"]
["West Midlands","Lea Marston 400/132kV S Stn","LeaMarston400/132kVSStn",720004,0.2,"Y",2800,"Y",1,"Y"]
["West Midlands","Leaton 33/11kV S Stn","Leaton33/11kVSStn",840016,0.41099999999999998,null,652,"",3,"Y"]
["West Midlands","Ledbury 66/11kV S Stn","Ledbury66/11kVSStn",670129,9.6000000000000002E-2,null,294,"",3,"Y"]
["West Midlands","Leebotwood 33/11kV S Stn","Leebotwood33/11kVSStn",840006,0.48399999999999999,null,523,"",3,"Y"]
["West Midlands","Leek 33/11kV S Stn","Leek33/11kVSStn",850028,0.216,null,307,"",3,"Y"]
["East Midlands","Leicester 132/33kV S Stn","Leicester132/33kVSStn",690026,4.2999999999999997E-2,null,524,"",1,"Y"]
["East Midlands","Leicester 33/11kV S Stn","Leicester33/11kVSStn",920033,4.2999999999999997E-2,null,524,"",1,"Y"]
["East Midlands","Leicester 33kV S Stn","Leicester33kVSStn",920006,4.2999999999999997E-2,null,524,"",1,"Y"]
["East Midlands","Leicester East 132/33kV S Stn","LeicesterEast132/33kVSStn",690025,3.6999999999999998E-2,null,68,"",3,"Y"]
["East Midlands","Leicester East 33/6.6kV S Stn","LeicesterEast33/6.6kVSStn",920040,3.6999999999999998E-2,null,35,"",3,"Y"]
["East Midlands","Leicester East 33kV S Stn","LeicesterEast33kVSStn",920004,3.6999999999999998E-2,null,35,"",3,"Y"]
["East Midlands","Leicester North 132/33kV S Stn","LeicesterNorth132/33kVSStn",690023,0.1,null,113,"",3,"Y"]
["East Midlands","Leicester North 33/11kV S Stn","LeicesterNorth33/11kVSStn",920030,0.1,null,113,"",3,"Y"]
["East Midlands","Leicester North 33kV S Stn","LeicesterNorth33kVSStn",920003,0.1,null,113,"",3,"Y"]
["East Midlands","Lenton 33/11kV S Stn","Lenton33/11kVSStn",880014,0.17599999999999999,null,412,"",3,"Y"]
["West Midlands","Leominster 66/11kV S Stn","Leominster66/11kVSStn",670100,0.253,null,441,"",3,"Y"]
["East Midlands","Lero 33/6.6kV S Stn","Lero33/6.6kVSStn",920023,0.09,null,166,"",3,"Y"]
["East Midlands","Leverton Battery Storage 33kV S Stn","LevertonBatteryStorage33kVSStn",907046,0.91200000000000003,null,218,"",3,"Y"]
["East Midlands","Leverton Solar Park 33kV S Stn","LevertonSolarPark33kVSStn",906126,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Lichfield 132/11kV S Stn","Lichfield132/11kVSStn",680056,9.8000000000000004E-2,null,470,"",1,"Y"]
["South Wales","Liddlestone Ridge PV Generation 33kV S Stn","LiddlestoneRidgePVGeneration33kVSStn",600357,0.7,"Y",500,"Y",3,"Y"]
["South West","Lifton 33/11kV S Stn","Lifton33/11kVSStn",330040,0.09,null,58,"",3,"Y"]
["East Midlands","Lilbourne Wind Farm 33kV S Stn","LilbourneWindFarm33kVSStn",946165,0.18,null,257,"",3,"Y"]
["South Wales","Lime Street Gorseinon 33/11kV S Stn","LimeStreetGorseinon33/11kVSStn",520217,0.28000000000000003,null,500,"Y",3,"Y"]
["East Midlands","Lime Tree Place 33/11kV S Stn","LimeTreePlace33/11kVSStn",890039,0.154,null,233,"",3,"Y"]
["East Midlands","Lincoln Farm Solar 33kV S Stn","LincolnFarmSolar33kVSStn",906936,0.14799999999999999,null,359,"",3,"Y"]
["East Midlands","Lincoln Local 132kV S Stn","LincolnLocal132kVSStn",690058,7.0000000000000007E-2,null,261,"",1,"Y"]
["East Midlands","Lincoln Local No 2 132/11kV S Stn","LincolnLocalNo2132/11kVSStn",900034,7.0000000000000007E-2,null,260,"",1,"Y"]
["East Midlands","Lincoln Local No 4 132/11kV S Stn","LincolnLocalNo4132/11kVSStn",907000,7.0000000000000007E-2,null,261,"",1,"Y"]
["East Midlands","Lincoln Main 132/33/11kV S Stn","LincolnMain132/33/11kVSStn",690057,0.04,null,236,"",3,"Y"]
["East Midlands","Lincoln No 1 33kV S Stn","LincolnNo133kVSStn",900002,0.04,null,236,"",3,"Y"]
["East Midlands","Lincoln No 2 33kV S Stn","LincolnNo233kVSStn",690073,0.04,null,236,"",3,"Y"]
["East Midlands","Lincoln No 5 132/11kV S Stn","LincolnNo5132/11kVSStn",900040,0.04,null,236,"",1,"Y"]
["East Midlands","Lindhurst Wind Farm 33kV S Stn","LindhurstWindFarm33kVSStn",890022,0.40400000000000003,null,553,"",3,"Y"]
["East Midlands","Lindridge Farm Solar Park 33kV S Stn","LindridgeFarmSolarPark33kVSStn",939263,0.13700000000000001,null,278,"",3,"Y"]
["South West","Linketty Lane 33/11kV S Stn","LinkettyLane33/11kVSStn",330029,0.161,null,162,"",3,"Y"]
["South West","Liskeard 33/11kV S Stn","Liskeard33/11kVSStn",457290,0.432,null,638,"",3,"Y"]
["South Wales","Litchard 33/11kV S Stn","Litchard33/11kVSStn",560150,0.151,null,500,"Y",3,"Y"]
["East Midlands","Little Hallam 33/11kV S Stn","LittleHallam33/11kVSStn",870049,0.17499999999999999,null,315,"",3,"Y"]
["East Midlands","Little Irchester 33/11kV S Stn","LittleIrchester33/11kVSStn",920060,0.14000000000000001,null,420,"",3,"Y"]
["East Midlands","Little Morton Solar Farm 33kV S Stn","LittleMortonSolarFarm33kVSStn",898284,8.5000000000000006E-2,null,134,"",3,"Y"]
["South Wales","Little Neath Solar Farm 33kV S Stn","LittleNeathSolarFarm33kVSStn",600353,0.59,null,500,"Y",3,"Y"]
["South Wales","Little Neath Solar Farm 33kV S Stn","LittleNeathSolarFarm33kVSStn",600391,0.44,null,500,"Y",3,"Y"]
["South West","Little Trevease Farm Solar Farm 33kV S Stn","LittleTreveaseFarmSolarFarm33kVSStn",418060,1.79,null,500,"Y",3,"Y"]
["East Midlands","Littlewood Farm PV 33kV S Stn","LittlewoodFarmPV33kVSStn",898475,0.28999999999999998,null,442,"",3,"Y"]
["East Midlands","Littlewood Farm Solar 33kV S Stn","LittlewoodFarmSolar33kVSStn",946198,0.28000000000000003,null,101,"",3,"Y"]
["South West","Liverton Farm Solar Park 33kV S Stn","LivertonFarmSolarPark33kVSStn",318110,0.245,null,500,"Y",3,"Y"]
["South Wales","Llanarth Primary 132/33kV S Stn","LlanarthPrimary132/33kVSStn",590021,1.1419999999999999,null,1000,"Y",3,"Y"]
["South Wales","Llancadle Solar Farm 33kV S Stn","LlancadleSolarFarm33kVSStn",510401,0.16,null,500,"Y",3,"Y"]
["South Wales","Llandarcy 33/11kV S Stn","Llandarcy33/11kVSStn",560322,0.28100000000000003,null,500,"Y",3,"Y"]
["South Wales","Llandarcy STOR Generation 33kV S Stn","LlandarcySTORGeneration33kVSStn",560358,0.63,null,500,"Y",3,"Y"]
["South Wales","Llandeilo 33/11kV S Stn","Llandeilo33/11kVSStn",590151,0.85799999999999998,null,500,"Y",3,"Y"]
["South Wales","Llandough 33/11kV S Stn","Llandough33/11kVSStn",510152,7.0000000000000007E-2,null,500,"Y",3,"Y"]
["South Wales","Llandovery 33/11kV S Stn","Llandovery33/11kVSStn",590153,0.32300000000000001,null,500,"Y",3,"Y"]
["South Wales","Llandrindod Wells 66/11kV S Stn","LlandrindodWells66/11kVSStn",610154,0.191,null,144,null,3,"Y"]
["South Wales","Llanelli Grid 132/11kV S Stn","LlanelliGrid132/11kVSStn",520022,8.5000000000000006E-2,null,1000,"Y",1,"Y"]
["South Wales","Llanfihangel Ystrad 33/11kV S Stn","LlanfihangelYstrad33/11kVSStn",590156,1.0109999999999999,null,500,"Y",3,"Y"]
["South Wales","Llanfyrnach 33/11kV S Stn","Llanfyrnach33/11kVSStn",580308,3.843,null,500,"Y",3,"Y"]
["South Wales","Llangadog 33/11kV S Stn","Llangadog33/11kVSStn",590157,0.74,null,500,"Y",3,"Y"]
["South Wales","Llangewydd 33/11kV S Stn","Llangewydd33/11kVSStn",560158,0.22600000000000001,null,500,"Y",3,"Y"]
["South Wales","Llanishen 33/11kV S Stn","Llanishen33/11kVSStn",510160,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Llanllwni 33/11kV S Stn","Llanllwni33/11kVSStn",590161,3.76,null,500,"Y",3,"Y"]
["South Wales","Llanrhidian 33/11kV S Stn","Llanrhidian33/11kVSStn",520162,1.4319999999999999,null,500,"Y",3,"Y"]
["South Wales","Llantarnam 132/66kV S Stn","Llantarnam132/66kVSStn",530023,0.10299999999999999,null,460,null,1,"Y"]
["South Wales","Llwyndu Solar Farm 33kV S Stn","LlwynduSolarFarm33kVSStn",580380,0.54,null,500,"Y",3,"Y"]
["South Wales","Llyn Brianne 33kV S Stn","LlynBrianne33kVSStn",590304,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Llynfi 66/11kV S Stn","Llynfi66/11kVSStn",560024,0.26500000000000001,null,500,"Y",3,"Y"]
["South Wales","Llynfi Afan Wind Farm 66kV S Stn","LlynfiAfanWindFarm66kVSStn",560420,0.78,null,325,"",3,"Y"]
["East Midlands","Lockheed 33/11kV S Stn","Lockheed33/11kVSStn",930056,0.11700000000000001,null,22,"",3,"Y"]
["South West","Lockleaze 132/33/11kV S Stn","Lockleaze132/33/11kVSStn",113370,5.7000000000000002E-2,null,184,"",3,"Y"]
["South West","Lockleaze 33/11kV S Stn","Lockleaze33/11kVSStn",110772,5.7000000000000002E-2,null,21,"",3,"Y"]
["South West","Lockleaze Battery Storage 33kV S Stn","LockleazeBatteryStorage33kVSStn",118179,0.69,null,500,"Y",3,"Y"]
["East Midlands","Lodge Farm Solar 33kV S Stn","LodgeFarmSolar33kVSStn",898432,0.09,null,132,"",3,"Y"]
["East Midlands","Lodge Farm Solar Park 33kV S Stn","LodgeFarmSolarPark33kVSStn",883349,0.09,null,132,"",3,"Y"]
["East Midlands","London Road 33/6.6kV S Stn","LondonRoad33/6.6kVSStn",930027,8.4000000000000005E-2,null,82,"",3,"Y"]
["East Midlands","London Road Heat Station 33kV S Stn","LondonRoadHeatStation33kVSStn",880042,3.1E-2,null,47,"",3,"Y"]
["West Midlands","Longbridge 132/11kV S Stn","Longbridge132/11kVSStn",670049,0.04,null,449,"",1,"Y"]
["South West","Longbridge 33/11kV S Stn","Longbridge33/11kVSStn",330024,0.20899999999999999,null,341,"",3,"Y"]
["East Midlands","Longcliffe 33/11kV S Stn","Longcliffe33/11kVSStn",890067,0.65,null,1276,"",3,"Y"]
["East Midlands","Long Eaton 33/11kV S Stn","LongEaton33/11kVSStn",870050,6.4000000000000001E-2,null,115,"",3,"Y"]
["West Midlands","Long Marston 66/11kV S Stn","LongMarston66/11kVSStn",670094,0.10100000000000001,null,128,"",3,"Y"]
["East Midlands","Long Sutton 33/11kV S Stn","LongSutton33/11kVSStn",910027,0.13400000000000001,null,257,"",3,"Y"]
["West Midlands","Longton 132/33/11kV S Stn","Longton132/33/11kVSStn",850001,4.7E-2,null,420,"",3,"Y"]
["South West","Looe 33/11kV S Stn","Looe33/11kVSStn",457300,0.94099999999999995,null,1622,"",3,"Y"]
["East Midlands","Loscoe 132kV S Stn","Loscoe132kVSStn",680069,0.11,null,576,"",1,"Y"]
["South West","Lostwithiel 33/11kV S Stn","Lostwithiel33/11kVSStn",437390,1.377,null,1526,"",3,"Y"]
["East Midlands","Loughborough 132/11kV S Stn","Loughborough132/11kVSStn",920020,9.1999999999999998E-2,null,436,"",1,"Y"]
["East Midlands","Loughborough 132/33/11kV S Stn","Loughborough132/33/11kVSStn",690022,9.1999999999999998E-2,null,436,"",3,"Y"]
["East Midlands","Loughborough 33kV S Stn","Loughborough33kVSStn",920002,9.1999999999999998E-2,null,436,"",3,"Y"]
["South Wales","Loughor Solar Park 33kV S Stn","LoughorSolarPark33kVSStn",560363,0.14499999999999999,null,500,"Y",3,"Y"]
["West Midlands","Lower Chadnor 66/11kV S Stn","LowerChadnor66/11kVSStn",670117,0.35499999999999998,null,383,"",3,"Y"]
["South Wales","Lower House P V Generation 66kV S Stn","LowerHousePVGeneration66kVSStn",530406,0.23,null,500,"Y",3,"Y"]
["West Midlands","Lower Newton Solar Farm 33kV S Stn","LowerNewtonSolarFarm33kVSStn",856887,0.13,null,185,"",3,"Y"]
["South West","Lower Tinacre Solar Farm 33kV S Stn","LowerTinacreSolarFarm33kVSStn",358050,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Low Farm AD 33kV S Stn","LowFarmAD33kVSStn",897792,0.27300000000000002,null,355,"",3,"Y"]
["East Midlands","Low Spinney Wind Farm 33kV S Stn","LowSpinneyWindFarm33kVSStn",938992,0.1,null,140,"",3,"Y"]
["South West","Luckwell Bridge 33/11kV S Stn","LuckwellBridge33/11kVSStn",210490,4.79,null,2476,"",3,"Y"]
["West Midlands","Ludlow 132/66/33/11kV S Stn","Ludlow132/66/33/11kVSStn",670064,0.15,null,599,"",3,"Y"]
["South West","Luscott Barton Solar Farm 33kV S Stn","LuscottBartonSolarFarm33kVSStn",268078,0.46899999999999997,null,500,"Y",3,"Y"]
["East Midlands","Lutterworth 33/11kV S Stn","Lutterworth33/11kVSStn",930062,7.1999999999999995E-2,null,122,"",3,"Y"]
["South West","Luxulyan Solar Park 33kV S Stn","LuxulyanSolarPark33kVSStn",438025,1.89,null,500,"Y",3,"Y"]
["South West","Lydeard St Lawrence 33/11kV S Stn","LydeardStLawrence33/11kVSStn",210050,0.86799999999999999,null,1075,"",3,"Y"]
["West Midlands","Lydney 33/11kV S Stn","Lydney33/11kVSStn",790001,0.21,null,712,"",3,"Y"]
["West Midlands","Lydney Local 132kV S Stn","LydneyLocal132kVSStn",670031,0.21,null,712,"",1,"Y"]
["West Midlands","Lye 132/11kV S Stn","Lye132/11kVSStn",670065,4.2999999999999997E-2,null,430,"",1,"Y"]
["South West","Lynton 33/11kV S Stn","Lynton33/11kVSStn",260410,4.5,null,2133,"",3,"Y"]
["East Midlands","Lyon Road Generation 33kV S Stn","LyonRoadGeneration33kVSStn",946411,0.7,"Y",500,"Y",3,"Y"]
["South West","Lypstone Farm 33/11kV S Stn","LypstoneFarm33/11kVSStn",181216,6.2E-2,null,143,"",3,"Y"]
["East Midlands","Mackworth 33/11kV S Stn","Mackworth33/11kVSStn",870038,9.8000000000000004E-2,null,200,"",3,"Y"]
["West Midlands","Madeley 33/11kV S Stn","Madeley33/11kVSStn",840014,6.5000000000000002E-2,null,83,"",3,"Y"]
["West Midlands","Madley 66/11kV S Stn","Madley66/11kVSStn",670109,0.28999999999999998,null,592,"",3,"Y"]
["South Wales","Maerdy 33/11kV S Stn","Maerdy33/11kVSStn",540306,0.378,null,500,"Y",3,"Y"]
["South Wales","Maerdy Wind Farm 33kV S Stn","MaerdyWindFarm33kVSStn",540338,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Maes Ar Dafen 33/11kV S Stn","MaesArDafen33/11kVSStn",520299,0.16400000000000001,null,500,"Y",3,"Y"]
["South Wales","Maesgwyne Wind Farm 132kV S Stn","MaesgwyneWindFarm132kVSStn",560331,0.14299999999999999,null,1000,"Y",1,"Y"]
["South Wales","Maesgwyn Wind Farm 33kV S Stn","MaesgwynWindFarm33kVSStn",560411,0.47,null,500,"Y",3,"Y"]
["East Midlands","Magna Park 33/11kV S Stn","MagnaPark33/11kVSStn",930107,0.127,null,245,"",3,"Y"]
["South Wales","Magor BSP 132/11kV S Stn","MagorBSP132/11kVSStn",530941,0.105,null,484,null,1,"Y"]
["South West","Makro Exeter STOR Generator 33kV S Stn","MakroExeterSTORGenerator33kVSStn",318161,0.34499999999999997,null,500,"Y",3,"Y"]
["West Midlands","Malehurst 33/11kV S Stn","Malehurst33/11kVSStn",840017,0.23599999999999999,null,354,"",3,"Y"]
["West Midlands","Malvern 132/11kV S Stn","Malvern132/11kVSStn",670067,4.8000000000000001E-2,null,319,"",1,"Y"]
["South West","Mangotsfield 33/11kV S Stn","Mangotsfield33/11kVSStn",111800,9.2999999999999999E-2,null,23,"",3,"Y"]
["South Wales","Manmoel Solar Park 33kV S Stn","ManmoelSolarPark33kVSStn",550434,0.84,null,832,"",3,"Y"]
["South Wales","Manoravon Pumping Station 33kV S Stn","ManoravonPumpingStation33kVSStn",590170,0.72799999999999998,null,1421,"",3,"Y"]
["East Midlands","Manor Farm PV Horton 33kV S Stn","ManorFarmPVHorton33kVSStn",946270,0.11,null,165,"",3,"Y"]
["South West","Manor Farm Solar Park 33kV S Stn","ManorFarmSolarPark33kVSStn",438011,0.214,null,350,"",3,"Y"]
["South Wales","Manor Farm Solar Park 66kV S Stn","ManorFarmSolarPark66kVSStn",530415,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Mansfield 132/33kV S Stn","Mansfield132/33kVSStn",680018,0.1,null,383,"",3,"Y"]
["East Midlands","Mansfield 33/11kV S Stn","Mansfield33/11kVSStn",890036,0.1,null,383,"",3,"Y"]
["East Midlands","Mansfield 33kV S Stn","Mansfield33kVSStn",890008,0.1,null,383,"",3,"Y"]
["East Midlands","Mansfield Street 33/11kV S Stn","MansfieldStreet33/11kVSStn",920024,0.157,null,393,"",3,"Y"]
["East Midlands","Mantle Lane 33/11kV S Stn","MantleLane33/11kVSStn",930098,0.05,null,80,"",3,"Y"]
["East Midlands","Manton 33/11kV S Stn","Manton33/11kVSStn",890044,0.27,null,385,"",3,"Y"]
["East Midlands","Mapperley 33/11kV S Stn","Mapperley33/11kVSStn",880029,9.6000000000000002E-2,null,145,"",3,"Y"]
["South West","Marazion 33/11kV S Stn","Marazion33/11kVSStn",417070,1.347,null,1611,"",3,"Y"]
["East Midlands","Marchington 33/11kV S Stn","Marchington33/11kVSStn",870028,0.215,null,338,"",3,"Y"]
["South Wales","Margam Biomass Generation 132kV S Stn","MargamBiomassGeneration132kVSStn",560372,0.11700000000000001,null,822,"",1,"Y"]
["South Wales","Margam BOC Biomass 33kV S Stn","MargamBOCBiomass33kVSStn",560324,0.27,null,500,"Y",3,"Y"]
["South Wales","Margam Grid 132/66kV S Stn","MargamGrid132/66kVSStn",560047,0.2,"Y",1000,"Y",3,"Y"]
["East Midlands","Market Deeping 33/11kV S Stn","MarketDeeping33/11kVSStn",910045,0.19,null,258,"",3,"Y"]
["West Midlands","Market Drayton 33/11kV S Stn","MarketDrayton33/11kVSStn",850008,0.21,null,700,"",3,"Y"]
["East Midlands","Market Harborough 33/11kV S Stn","MarketHarborough33/11kVSStn",920047,0.17,null,262,"",3,"Y"]
["East Midlands","Market Overton 33/11kV S Stn","MarketOverton33/11kVSStn",910048,0.23200000000000001,null,282,"",3,"Y"]
["South West","Marksbury Solar Park 33kV S Stn","MarksburySolarPark33kVSStn",118117,9.6000000000000002E-2,null,500,"Y",3,"Y"]
["South West","Marlands Fields Creacombe Solar Park 33kV S Stn","MarlandsFieldsCreacombeSolarPark33kVSStn",338185,0.48399999999999999,null,483,"",3,"Y"]
["East Midlands","Marlborough Road 33/11kV S Stn","MarlboroughRoad33/11kVSStn",880026,0.161,null,243,"",3,"Y"]
["East Midlands","Marlborough Street 33/11kV S Stn","MarlboroughStreet33/11kVSStn",940037,8.1000000000000003E-2,null,230,"",3,"Y"]
["South West","Marldon 33/11kV S Stn","Marldon33/11kVSStn",340027,0.14899999999999999,null,119,"",3,"Y"]
["West Midlands","Marle Hill 132/66/11kV S Stn","MarleHill132/66/11kVSStn",670066,3.5000000000000003E-2,null,160,"",3,"Y"]
["South West","Marley Thatch Farm Solar Park 33kV S Stn","MarleyThatchFarmSolarPark33kVSStn",348027,0.76200000000000001,null,500,"Y",3,"Y"]
["South West","Marsh Barton 33/11kV S Stn","MarshBarton33/11kVSStn",310022,0.7,"Y",87,"",3,"Y"]
["South West","Marsh Barton Power Station 132kV S Stn","MarshBartonPowerStation132kVSStn",310006,0.10170999999999999,null,612.70000000000005,"",1,"Y"]
["South West","Marsh Green 33/11kV S Stn","MarshGreen33/11kVSStn",310036,0.82799999999999996,null,800,"",3,"Y"]
["East Midlands","Marsh Lane 33/11kV S Stn","MarshLane33/11kVSStn",900007,0.105,null,230,"",3,"Y"]
["South West","Martock 33/11kV S Stn","Martock33/11kVSStn",250300,0.33600000000000002,null,265,"",3,"Y"]
["East Midlands","Matlock 33/11kV S Stn","Matlock33/11kVSStn",890074,0.106,null,165,"",3,"Y"]
["East Midlands","Maxwell House Data Centre 33/11kV S Stn","MaxwellHouseDataCentre33/11kVSStn",945675,0.23,null,208,"",3,"Y"]
["West Midlands","Mead Lane 33/11kV S Stn","MeadLane33/11kVSStn",790023,0.08,null,113,"",3,"Y"]
["East Midlands","Meadow Farm Solar 33kV S Stn","MeadowFarmSolar33kVSStn",926406,0.18,null,217,"",3,"Y"]
["East Midlands","Meadow Lane 33/11kV S Stn","MeadowLane33/11kVSStn",890090,0.215,null,424,"",3,"Y"]
["West Midlands","Meaford C 132/33/11kV S Stn","MeafordC132/33/11kVSStn",680026,0.11,null,1013,"",3,"Y"]
["South Wales","Meinciau 33/11kV S Stn","Meinciau33/11kVSStn",520172,3.44,null,500,"Y",3,"Y"]
["East Midlands","Melbourne 33/11kV S Stn","Melbourne33/11kVSStn",870017,0.129,null,249,"",3,"Y"]
["South West","Melksham 400/275/132kV S Stn","Melksham400/275/132kVSStn",106010,0.2,"Y",2800,"Y",1,"Y"]
["East Midlands","Melton Mowbray 132/33kV S Stn","MeltonMowbray132/33kVSStn",690033,4.2999999999999997E-2,null,242,"",3,"Y"]
["East Midlands","Melton Mowbray 33/11kV S Stn","MeltonMowbray33/11kVSStn",910039,4.2999999999999997E-2,null,242,"",3,"Y"]
["East Midlands","Melton Mowbray 33kV S Stn","MeltonMowbray33kVSStn",910006,4.2999999999999997E-2,null,242,"",3,"Y"]
["South Wales","Merlins Bridge 33/11kV S Stn","MerlinsBridge33/11kVSStn",600173,0.2,null,500,"Y",3,"Y"]
["South West","Merrivale 33/11kV S Stn","Merrivale33/11kVSStn",330017,0.153,null,214,"",3,"Y"]
["South Wales","Merthyr East Primary 132/11kV S Stn","MerthyrEastPrimary132/11kVSStn",550901,0.23599999999999999,null,1000,"Y",1,"Y"]
["East Midlands","Metheringham 33/11kV S Stn","Metheringham33/11kVSStn",900037,0.13,null,250,"",3,"Y"]
["South West","Mevagissey 33/11kV S Stn","Mevagissey33/11kVSStn",437400,0.9,null,1128,"",3,"Y"]
["South West","Middle Barlington 33/11kV S Stn","MiddleBarlington33/11kVSStn",260420,2.4500000000000002,null,1581,"",3,"Y"]
["South Wales","Middle Fan 33/11kV S Stn","MiddleFan33/11kVSStn",540174,0.247,null,500,"Y",3,"Y"]
["East Midlands","Middlefield 33/11kV S Stn","Middlefield33/11kVSStn",930088,0.19700000000000001,null,388,"",3,"Y"]
["East Midlands","Middlemarsh 132kV S Stn","Middlemarsh132kVSStn",690021,0.2,"Y",1000,"Y",1,"Y"]
["South West","Middle Treworder Farm Solar Park 33kV S Stn","MiddleTreworderFarmSolarPark33kVSStn",438036,0.68100000000000005,null,500,"Y",3,"Y"]
["South West","Midsomer Norton 33/11kV S Stn","MidsomerNorton33/11kVSStn",160423,0.05,null,82,"",3,"Y"]
["South West","Milehouse 132/33kV S Stn","Milehouse132/33kVSStn",330002,0.11700000000000001,null,303,"",3,"Y"]
["South Wales","Milford Haven 33/11kV S Stn","MilfordHaven33/11kVSStn",600279,0.22,null,500,"Y",3,"Y"]
["South Wales","Milford Haven Grid 132/33kV S Stn","MilfordHavenGrid132/33kVSStn",600042,1.07,null,1000,"Y",3,"Y"]
["East Midlands","Millclose 33/11kV S Stn","Millclose33/11kVSStn",890068,0.16400000000000001,null,273,"",3,"Y"]
["East Midlands","Mill Farm Battery Storage 33kV S Stn","MillFarmBatteryStorage33kVSStn",917757,0.57499999999999996,null,642,"",3,"Y"]
["East Midlands","Mill Farm Solar Boothby Great Wood 33kV S Stn","MillFarmSolarBoothbyGreatWood33kVSStn",917647,0.21299999999999999,null,234,"",3,"Y"]
["South West","Millfield 33/11kV S Stn","Millfield33/11kVSStn",210100,0.189,null,275,"",3,"Y"]
["South Wales","Mill St. Tonyrefail 33/11kV S Stn","MillSt.Tonyrefail33/11kVSStn",540241,0.7,"Y",384,"",3,"Y"]
["East Midlands","Misson 33/11kV S Stn","Misson33/11kVSStn",890049,0.17799999999999999,null,343,"",3,"Y"]
["East Midlands","Misterton 33/11kV S Stn","Misterton33/11kVSStn",890060,0.30099999999999999,null,286,"",3,"Y"]
["West Midlands","Mitcheldean 33/11kV S Stn","Mitcheldean33/11kVSStn",790014,0.193,null,239,"",3,"Y"]
["East Midlands","Moat Farm Draycott-In-The-Clay Solar Site 33kV S Stn","MoatFarmDraycott-In-The-ClaySolarSite33kVSStn",875043,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Moat Farm Solar Farm 33kV S Stn","MoatFarmSolarFarm33kVSStn",898324,0.43,null,305,"",3,"Y"]
["South West","Modbury 33/11kV S Stn","Modbury33/11kVSStn",340040,0.21299999999999999,null,218,"",3,"Y"]
["East Midlands","Moira 33/11kV S Stn","Moira33/11kVSStn",930102,0.14599999999999999,null,283,"",3,"Y"]
["West Midlands","Moneystone Quarry PV Farm 33kV S Stn","MoneystoneQuarryPVFarm33kVSStn",863412,0.249,null,373,"",3,"Y"]
["South Wales","Monmouth 66/11kV S Stn","Monmouth66/11kVSStn",530177,7.3999999999999996E-2,null,85,null,3,"Y"]
["South West","Montacute 33/11kV S Stn","Montacute33/11kVSStn",250400,0.42799999999999999,null,537,"",3,"Y"]
["West Midlands","Montpellier 132/11kV S Stn","Montpellier132/11kVSStn",670068,4.3999999999999997E-2,null,216,"",1,"Y"]
["South West","Montys Farm Solar Park 33kV S Stn","MontysFarmSolarPark33kVSStn",218041,0.19700000000000001,null,500,"Y",3,"Y"]
["East Midlands","Moorgreen 33/11kV S Stn","Moorgreen33/11kVSStn",890025,0.114,null,251,"",3,"Y"]
["West Midlands","Moreton 66/11kV S Stn","Moreton66/11kVSStn",670085,0.114,null,191,"",3,"Y"]
["South Wales","Morlanga Farm 33/11kV S Stn","MorlangaFarm33/11kVSStn",510178,1.214,null,500,"Y",3,"Y"]
["East Midlands","Morley 33/11kV S Stn","Morley33/11kVSStn",870042,0.104,null,208,"",3,"Y"]
["South Wales","Morriston 132/11kV S Stn","Morriston132/11kVSStn",520291,0.127,null,1000,"Y",1,"Y"]
["South West","Mortonhampstead 33/11kV S Stn","Mortonhampstead33/11kVSStn",340012,0.20899999999999999,null,116,"",3,"Y"]
["South West","Morwenstow 33/11kV S Stn","Morwenstow33/11kVSStn",350024,2.09,null,2036,"",3,"Y"]
["South Wales","Mountain Ash 33/11kV S Stn","MountainAsh33/11kVSStn",550179,0.14099999999999999,null,500,"Y",3,"Y"]
["South Wales","Mountain Ash Grid 132/33kV S Stn","MountainAshGrid132/33kVSStn",550026,1.03,null,1000,"Y",3,"Y"]
["East Midlands","Mount Bridge 33/11kV S Stn","MountBridge33/11kVSStn",900022,0.08,null,151,"",3,"Y"]
["East Midlands","Mount Mill Solar Park 33kV S Stn","MountMillSolarPark33kVSStn",946174,0.09,null,203,"",3,"Y"]
["East Midlands","Mountsorrel 33/11kV S Stn","Mountsorrel33/11kVSStn",920025,0.192,null,369,"",3,"Y"]
["South West","Mousehole 33/11kV S Stn","Mousehole33/11kVSStn",417340,3.3639999999999999,null,2301,"",3,"Y"]
["South West","Mullion 33/11kV S Stn","Mullion33/11kVSStn",417780,0.443,null,338,"",3,"Y"]
["South Wales","Mynydd Brombil Windfarm 33kV S Stn","MynyddBrombilWindfarm33kVSStn",560417,1.5309999999999999,null,500,"Y",3,"Y"]
["South Wales","Mynydd Portref Wind Farm 33kV S Stn","MynyddPortrefWindFarm33kVSStn",540335,1.48,null,500,"Y",3,"Y"]
["South Wales","Mynydd Uchaf Wind Farm 33kV S Stn","MynyddUchafWindFarm33kVSStn",520445,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Mynydd Y Bwllfa Wind Farm 132kV S Stn","MynyddYBwllfaWindFarm132kVSStn",550376,1.05,null,1000,"Y",1,"Y"]
["South Wales","Mynydd Y Gwair Wind Farm 132kV S Stn","MynyddYGwairWindFarm132kVSStn",520438,0.61599999999999999,null,3000,"",1,"Y"]
["South Wales","Mynydd Y Gwrhyd Wind Generation 33kV S Stn","MynyddYGwrhydWindGeneration33kVSStn",520410,0.92,null,500,"Y",3,"Y"]
["South Wales","Mynydd Yr Aber Wind Farm 66kV S Stn","MynyddYrAberWindFarm66kVSStn",560421,0.86199999999999999,null,500,"Y",3,"Y"]
["South West","Nailsea 33/11kV S Stn","Nailsea33/11kVSStn",181000,0.23499999999999999,null,404,"",3,"Y"]
["East Midlands","Nailstone 33/11kV S Stn","Nailstone33/11kVSStn",930097,0.49399999999999999,null,935,"",3,"Y"]
["West Midlands","Naishcombe Hill 33/11kV S Stn","NaishcombeHill33/11kVSStn",790012,0.66,null,832,"",3,"Y"]
["South West","Nancrossa Solar Park 33kV S Stn","NancrossaSolarPark33kVSStn",418163,1.9279999999999999,null,500,"Y",3,"Y"]
["South West","Nanteague Solar Park 33kV S Stn","NanteagueSolarPark33kVSStn",418101,0.75,null,500,"Y",3,"Y"]
["South Wales","Nantgaredig 33/11kV S Stn","Nantgaredig33/11kVSStn",590180,4.0490000000000004,null,500,"Y",3,"Y"]
["South Wales","Nantgarw BSP 132/11kV S Stn","NantgarwBSP132/11kVSStn",540903,0.29299999999999998,null,1000,"Y",1,"Y"]
["South Wales","Nantwen 33/11kV S Stn","Nantwen33/11kVSStn",550182,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Nathenfoel Solar Park 33kV S Stn","NathenfoelSolarPark33kVSStn",590424,0.39500000000000002,null,500,"Y",3,"Y"]
["West Midlands","Nechells East 275/132kV S Stn","NechellsEast275/132kVSStn",670007,7.0000000000000007E-2,null,1540,"",1,"Y"]
["West Midlands","Nechells West 132/25/11kV S Stn","NechellsWest132/25/11kVSStn",670069,0.11,null,583,"",1,"Y"]
["South Wales","Nelson 33/11kV S Stn","Nelson33/11kVSStn",550183,0.5,null,500,"Y",3,"Y"]
["West Midlands","Netherhills 33/11kV S Stn","Netherhills33/11kVSStn",790022,0.27300000000000002,null,380,"",3,"Y"]
["South West","Nether Mill Farm Solar Park 33kV S Stn","NetherMillFarmSolarPark33kVSStn",318032,0.7,"Y",500,"Y",3,"Y"]
["South West","Nether Stowey 33/11kV S Stn","NetherStowey33/11kVSStn",210130,0.443,null,269,"",3,"Y"]
["South Wales","Nevern 33/11kV S Stn","Nevern33/11kVSStn",600184,2.6,null,500,"Y",3,"Y"]
["East Midlands","New Albion Wind Farm 33kV S Stn","NewAlbionWindFarm33kVSStn",926186,0.182,null,275,"",3,"Y"]
["East Midlands","Newark Junction 33/11kV S Stn","NewarkJunction33/11kVSStn",900024,0.161,null,240,"",3,"Y"]
["East Midlands","New Beacon Road 33/11kV S Stn","NewBeaconRoad33/11kVSStn",910034,0.08,null,102,"",3,"Y"]
["South West","Newbury 33/11kV S Stn","Newbury33/11kVSStn",161701,0.97099999999999997,null,1035,"",3,"Y"]
["West Midlands","Newcastle 132/11kV S Stn","Newcastle132/11kVSStn",680057,0.11,null,722,"",1,"Y"]
["West Midlands","Newcastle 33/11kV S Stn","Newcastle33/11kVSStn",680045,5.8000000000000003E-2,null,681,"",3,"Y"]
["South Wales","Newcastle Emlyn South 33/11kV S Stn","NewcastleEmlynSouth33/11kVSStn",580276,0.66900000000000004,null,500,"Y",3,"Y"]
["East Midlands","Newdigate 33/11kV S Stn","Newdigate33/11kVSStn",930079,0.23,null,390,"",3,"Y"]
["West Midlands","Newent 66/11kV S Stn","Newent66/11kVSStn",670133,0.3,null,851,"",3,"Y"]
["South Wales","Newhouse 33/11kV S Stn","Newhouse33/11kVSStn",530294,0.32,null,341,null,3,"Y"]
["South West","Newlands Farm Solar Park 33kV S Stn","NewlandsFarmSolarPark33kVSStn",258062,0.23,null,500,"Y",3,"Y"]
["South Wales","New Lodge 33/11kV S Stn","NewLodge33/11kVSStn",520187,0.18,null,500,"Y",3,"Y"]
["South West","Newlyn 33/11kV S Stn","Newlyn33/11kVSStn",417690,0.55100000000000005,null,1160,"",3,"Y"]
["South West","Newnham Farm Solar Park 33kV S Stn","NewnhamFarmSolarPark33kVSStn",338133,0.56000000000000005,null,500,"Y",3,"Y"]
["West Midlands","Newport 33/11kV S Stn","Newport33/11kVSStn",840009,0.25,null,407,"",3,"Y"]
["South Wales","Newport East 132/11kV S Stn","NewportEast132/11kVSStn",530027,0.2,"Y",1000,"Y",1,"Y"]
["East Midlands","Newport Pagnell 33/11kV S Stn","NewportPagnell33/11kVSStn",940041,0.13100000000000001,null,271,"",3,"Y"]
["South Wales","Newport South 132/33kV S Stn","NewportSouth132/33kVSStn",530028,1.7999999999999999E-2,null,148,null,1,"Y"]
["South West","Newport Street 33/11kV S Stn","NewportStreet33/11kVSStn",330015,0.55300000000000005,null,147,"",3,"Y"]
["South Wales","Newport West 132/11kV S Stn","NewportWest132/11kVSStn",530900,9.1999999999999998E-2,null,672,null,1,"Y"]
["South West","Newquay Trencreek Ln 33/11kV S Stn","NewquayTrencreekLn33/11kVSStn",437610,0.46899999999999997,null,463,"",3,"Y"]
["South West","Newquay Trevemper 33/11kV S Stn","NewquayTrevemper33/11kVSStn",437220,0.66600000000000004,null,1010,"",3,"Y"]
["South West","New Rendy Farm Solar Farm 33kV S Stn","NewRendyFarmSolarFarm33kVSStn",218000,0.11600000000000001,null,500,"Y",3,"Y"]
["South West","New Row Farm Solar Park 33kV S Stn","NewRowFarmSolarPark33kVSStn",168104,0.66600000000000004,null,500,"Y",3,"Y"]
["South West","Newton Abbot 132/33/11kV S Stn","NewtonAbbot132/33/11kVSStn",340001,0.11,null,405,"",3,"Y"]
["South West","Newton Abbot Main 33/11kV S Stn","NewtonAbbotMain33/11kVSStn",340019,8.5000000000000006E-2,null,23,"",3,"Y"]
["South West","Newton Barton Solar Park 33kV S Stn","NewtonBartonSolarPark33kVSStn",458128,0.32,null,500,"Y",3,"Y"]
["South West","Newton Downs Solar Park 33kV S Stn","NewtonDownsSolarPark33kVSStn",338190,0.46,null,457,"",3,"Y"]
["South Wales","Newton Down Wind Farm 33kV S Stn","NewtonDownWindFarm33kVSStn",560419,1.6759999999999999,null,1240,"",3,"Y"]
["South West","Newton Ferrers 33/11kV S Stn","NewtonFerrers33/11kVSStn",330032,0.46,null,457,"",3,"Y"]
["South West","Newton Poppleford 33/11kV S Stn","NewtonPoppleford33/11kVSStn",310045,0.34,null,284,"",3,"Y"]
["East Midlands","Newton Road 33/11kV S Stn","NewtonRoad33/11kVSStn",940040,0.109,null,167,"",3,"Y"]
["South West","Newton St Cyres 33/11kV S Stn","NewtonStCyres33/11kVSStn",310012,0.72699999999999998,null,1246,"",3,"Y"]
["South Wales","Neyland 33/11kV S Stn","Neyland33/11kVSStn",600188,0.66100000000000003,null,500,"Y",3,"Y"]
["South West","Ninnis Solar Farm 33kV S Stn","NinnisSolarFarm33kVSStn",438051,0.26500000000000001,null,459,null,3,"Y"]
["East Midlands","Normanton 33/11kV S Stn","Normanton33/11kVSStn",870040,0.11899999999999999,null,238,"",3,"Y"]
["South West","Norrington 132/33kV S Stn","Norrington132/33kVSStn",104098,0.2,"Y",1400,"Y",3,"Y"]
["South West","Northam 33/11kV S Stn","Northam33/11kVSStn",350016,0.11600000000000001,null,126,"",3,"Y"]
["East Midlands","Northampton 132/33kV S Stn","Northampton132/33kVSStn",690055,5.2999999999999999E-2,null,570,"",3,"Y"]
["East Midlands","Northampton 33/11kV S Stn","Northampton33/11kVSStn",940061,5.2999999999999999E-2,null,570,"",3,"Y"]
["East Midlands","Northampton 33kV S Stn","Northampton33kVSStn",940009,5.2999999999999999E-2,null,570,"",3,"Y"]
["East Midlands","Northampton East 132/33kV S Stn","NorthamptonEast132/33kVSStn",690053,0.09,null,637,"",3,"Y"]
["East Midlands","Northampton East 33/11kV S Stn","NorthamptonEast33/11kVSStn",946045,0.09,null,637,"",3,"Y"]
["East Midlands","Northampton East 33kV S Stn","NorthamptonEast33kVSStn",940010,0.09,null,637,"",3,"Y"]
["East Midlands","Northampton West 132/33kV S Stn","NorthamptonWest132/33kVSStn",690054,5.2999999999999999E-2,null,1000,"Y",3,"Y"]
["East Midlands","Northampton West 33/11kV S Stn","NorthamptonWest33/11kVSStn",940054,5.2999999999999999E-2,null,43,"",3,"Y"]
["East Midlands","Northampton West 33kV S Stn","NorthamptonWest33kVSStn",940012,5.2999999999999999E-2,null,375,"",3,"Y"]
["South Wales","Northcote St. 33/11kV S Stn","NorthcoteSt.33/11kVSStn",510190,6.8000000000000005E-2,null,500,"Y",3,"Y"]
["East Midlands","North Greetwell 132kV S Stn","NorthGreetwell132kVSStn",690063,0.23200000000000001,null,1392,"",1,"Y"]
["East Midlands","North Hykeham 33/11kV S Stn","NorthHykeham33/11kVSStn",900029,9.4E-2,null,150,"",3,"Y"]
["South West","North Intake 33kV S Stn","NorthIntake33kVSStn",330039,0.22,null,297,"",3,"Y"]
["South West","Northmoor Solar Park 132kV S Stn","NorthmoorSolarPark132kVSStn",358116,0.92,null,1400,"Y",1,"Y"]
["East Midlands","North Rauceby 33kV S Stn","NorthRauceby33kVSStn",917778,0.93,null,252,"",3,"Y"]
["South West","North Street Langport 33/11kV S Stn","NorthStreetLangport33/11kVSStn",210090,0.1,null,169,"",3,"Y"]
["South West","North Tawton 132/33kV S Stn","NorthTawton132/33kVSStn",310007,0.20399999999999999,null,255,"",3,"Y"]
["South West","North Tawton 33/11kV S Stn","NorthTawton33/11kVSStn",310058,0.20399999999999999,null,105,"",3,"Y"]
["South Wales","North Tenement Solar Park 33kV S Stn","NorthTenementSolarPark33kVSStn",600431,0.28399999999999997,null,616,"",3,"Y"]
["South West","North Wayton Solar Park 33kV S Stn","NorthWaytonSolarPark33kVSStn",458097,0.28399999999999997,null,500,"Y",3,"Y"]
["East Midlands","North Wheatley 33/11kV S Stn","NorthWheatley33/11kVSStn",890057,0.53400000000000003,null,555,"",3,"Y"]
["West Midlands","Northwick Generation 66kV S Stn","NorthwickGeneration66kVSStn",765590,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","North Wilford 33/11kV S Stn","NorthWilford33/11kVSStn",880017,6.6000000000000003E-2,null,193,"",3,"Y"]
["South West","Northwood Solar Park 33kV S Stn","NorthwoodSolarPark33kVSStn",118115,0.14000000000000001,null,500,"Y",3,"Y"]
["South Wales","Nottage 33/11kV S Stn","Nottage33/11kVSStn",560191,0.23599999999999999,null,500,"Y",3,"Y"]
["East Midlands","Nottingham 132/33kV S Stn","Nottingham132/33kVSStn",680023,7.6999999999999999E-2,null,601,"",3,"Y"]
["East Midlands","Nottingham 33kV S Stn","Nottingham33kVSStn",880003,7.6999999999999999E-2,null,601,"",3,"Y"]
["East Midlands","Nottingham East 132/33kV S Stn","NottinghamEast132/33kVSStn",680015,3.2000000000000001E-2,null,275,"",3,"Y"]
["East Midlands","Nottingham East 33kV S Stn","NottinghamEast33kVSStn",880002,3.2000000000000001E-2,null,275,"",3,"Y"]
["East Midlands","Nottingham North 132/11kV S Stn","NottinghamNorth132/11kVSStn",880021,1.7999999999999999E-2,null,160,"",1,"Y"]
["East Midlands","Nottingham North 132/33/11kV S Stn","NottinghamNorth132/33/11kVSStn",680022,1.7999999999999999E-2,null,160,"",3,"Y"]
["East Midlands","Nottingham North 33kV S Stn","NottinghamNorth33kVSStn",880005,1.7999999999999999E-2,null,160,"",3,"Y"]
["East Midlands","Nottingham Road STOR 33kV S Stn","NottinghamRoadSTOR33kVSStn",875155,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Nowhere Farm PV 33kV S Stn","NowhereFarmPV33kVSStn",917543,0.05,null,60,"",3,"Y"]
["East Midlands","Nuneaton 132/33kV S Stn","Nuneaton132/33kVSStn",690018,8.5000000000000006E-2,null,632,"",3,"Y"]
["East Midlands","Nuneaton 33/11kV S Stn","Nuneaton33/11kVSStn",930077,8.5000000000000006E-2,null,632,"",3,"Y"]
["East Midlands","Nuneaton 33kV S Stn","Nuneaton33kVSStn",930004,8.5000000000000006E-2,null,632,"",3,"Y"]
["South Wales","Oak Cottage Solar Farm 33kV S Stn","OakCottageSolarFarm33kVSStn",600393,0.27,null,500,"Y",3,"Y"]
["South Wales","Oak Grove Farm Solar Generation 33kV S Stn","OakGroveFarmSolarGeneration33kVSStn",530404,0.43,null,309,"",3,"Y"]
["East Midlands","Oakham 132/33kV S Stn","Oakham132/33kVSStn",690038,8.6999999999999994E-2,null,413,"",3,"Y"]
["East Midlands","Oakham 33/11kV S Stn","Oakham33/11kVSStn",910055,8.6999999999999994E-2,null,413,"",3,"Y"]
["East Midlands","Oakham 33kV S Stn","Oakham33kVSStn",910007,8.6999999999999994E-2,null,413,"",3,"Y"]
["South West","Oakham Farm Solar Park 33kV S Stn","OakhamFarmSolarPark33kVSStn",118157,0.14399999999999999,null,500,"Y",3,"Y"]
["East Midlands","Oakley 33/11kV S Stn","Oakley33/11kVSStn",920051,0.05,null,97,"",3,"Y"]
["West Midlands","Ocker Hill B 132/33/11kV S Stn","OckerHillB132/33/11kVSStn",670070,5.1999999999999998E-2,null,854,"",3,"Y"]
["West Midlands","Ocker Hill C 275/132kV S Stn","OckerHillC275/132kVSStn",670010,7.0000000000000007E-2,null,1266,"",1,"Y"]
["South West","Offwell 33/11kV S Stn","Offwell33/11kVSStn",310041,1.2410000000000001,null,1452,"",3,"Y"]
["South Wales","Ogmore Vale 66/11kV S Stn","OgmoreVale66/11kVSStn",560193,0.30099999999999999,null,500,"Y",3,"Y"]
["South West","Okehampton 33/11kV S Stn","Okehampton33/11kVSStn",350050,0.23,null,216,"",3,"Y"]
["West Midlands","Oldbury 132/11kV S Stn","Oldbury132/11kVSStn",670005,7.5999999999999998E-2,null,965,"",1,"Y"]
["West Midlands","Oldbury B 132/33/11kV S Stn","OldburyB132/33/11kVSStn",670154,0.2,"Y",1000,"Y",3,"Y"]
["East Midlands","Old Dalby 33/11kV S Stn","OldDalby33/11kVSStn",910043,0.26100000000000001,null,381,"",3,"Y"]
["East Midlands","Old Dalby Lodge Wind Farm 33kV S Stn","OldDalbyLodgeWindFarm33kVSStn",690071,0.13900000000000001,null,285,"",3,"Y"]
["South West","Oldfield Park33/ 6.6kV S Stn","OldfieldPark33/6.6kVSStn",160050,0.26100000000000001,null,86,"",3,"Y"]
["South West","Old Green Generation Station 132kV S Stn","OldGreenGenerationStation132kVSStn",118180,0.114,null,1400,"Y",1,"Y"]
["South West","Old Laira Road 33/11kV S Stn","OldLairaRoad33/11kVSStn",330026,0.65200000000000002,null,266,"",3,"Y"]
["South West","Old Stone Farm Solar Park 33kV S Stn","OldStoneFarmSolarPark33kVSStn",348175,1.3019229999999999,null,500,"Y",3,"Y"]
["East Midlands","Ollerton 33/11kV S Stn","Ollerton33/11kVSStn",890051,0.19,null,376,"",3,"Y"]
["East Midlands","Olney 33/11kV S Stn","Olney33/11kVSStn",940045,0.09,null,137,"",3,"Y"]
["East Midlands","Olney Hyde Farm Solar 33kV S Stn","OlneyHydeFarmSolar33kVSStn",946329,8.8999999999999996E-2,null,137,"",3,"Y"]
["South Wales","Orb Works 33kV S Stn","OrbWorks33kVSStn",530195,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Ordsall Road 33/11kV S Stn","OrdsallRoad33/11kVSStn",890053,0.19400000000000001,null,360,"",3,"Y"]
["East Midlands","Osbaston 33/11kV S Stn","Osbaston33/11kVSStn",930100,0.35,null,603,"",3,"Y"]
["East Midlands","Osmaston Road 33/6.6kv S Stn","OsmastonRoad33/6.6kvSStn",870045,0.7,"Y",500,"Y",3,"Y"]
["South West","Otterham Wind Farm 132kV S Stn","OtterhamWindFarm132kVSStn",458109,0.2,null,1400,"Y",1,"Y"]
["South West","Ottery St Mary 33/11kV S Stn","OtteryStMary33/11kVSStn",310043,0.442,null,487,"",3,"Y"]
["East Midlands","Oundle 33/11kV S Stn","Oundle33/11kVSStn",920055,0.28000000000000003,null,409,"",3,"Y"]
["South West","Outlands Wood Solar Park 33kV S Stn","OutlandsWoodSolarPark33kVSStn",438092,0.434,null,500,"Y",3,"Y"]
["West Midlands","Oxbridge 33/11kV S Stn","Oxbridge33/11kVSStn",790004,0.218,null,312,"",3,"Y"]
["East Midlands","Oxcroft Solar Farm 33kV S Stn","OxcroftSolarFarm33kVSStn",898478,0.11899999999999999,null,204,"",3,"Y"]
["South West","Padstow 33/11kV S Stn","Padstow33/11kVSStn",437430,1.21,null,975,"",3,"Y"]
["South West","Paignton 132/33kV S Stn","Paignton132/33kVSStn",340002,0.42799999999999999,null,823,"",3,"Y"]
["South West","Paignton 33/11kV S Stn","Paignton33/11kVSStn",340042,0.42799999999999999,null,823,"",3,"Y"]
["East Midlands","Pailton 132/33kV S Stn","Pailton132/33kVSStn",930018,0.19,null,807,"",3,"Y"]
["East Midlands","Pailton 33kV S Stn","Pailton33kVSStn",690067,0.19,null,807,"",3,"Y"]
["South Wales","Panteg 132/11kV S Stn","Panteg132/11kVSStn",530196,5.7000000000000002E-2,null,260,null,1,"Y"]
["South Wales","Pantyffynon 33/11kV S Stn","Pantyffynon33/11kVSStn",520197,0.20699999999999999,null,500,"Y",3,"Y"]
["South Wales","Pant Y Moch Solar Farm 33kV S Stn","PantYMochSolarFarm33kVSStn",560397,0.81,null,500,"Y",3,"Y"]
["South Wales","Pant Y Wal Wind Farm 66kV S Stn","PantYWalWindFarm66kVSStn",560342,0.86199999999999999,null,500,"Y",3,"Y"]
["South Wales","Parc Cynog Wind Farm 33kV S Stn","ParcCynogWindFarm33kVSStn",580314,0.37,null,500,"Y",3,"Y"]
["South West","Par Harbour 33/11kV S Stn","ParHarbour33/11kVSStn",437670,0.22800000000000001,null,350,"",3,"Y"]
["East Midlands","Park Farm 33/11kV S Stn","ParkFarm33/11kVSStn",920065,9.6000000000000002E-2,null,188,"",3,"Y"]
["South Wales","Park Lane 33/11kV S Stn","ParkLane33/11kVSStn",510198,8.2000000000000003E-2,null,500,"Y",3,"Y"]
["South West","Park Lane 33/11kV S Stn","ParkLane33/11kVSStn",350017,7.3999999999999996E-2,null,83,"",3,"Y"]
["South West","Park Street 33/6.6kV S Stn","ParkStreet33/6.6kVSStn",160060,3.1E-2,null,21,"",3,"Y"]
["South West","Parkview Solar Park 33kV S Stn","ParkviewSolarPark33kVSStn",348134,0.63,null,500,"Y",3,"Y"]
["South West","Park Wall Solar Park 33kV S Stn","ParkWallSolarPark33kVSStn",218002,9.4E-2,null,500,"Y",3,"Y"]
["South West","Parsonage Barn Solar Park 33kV S Stn","ParsonageBarnSolarPark33kVSStn",258065,0.16,null,500,"Y",3,"Y"]
["South West","Patchway 33/11kV S Stn","Patchway33/11kVSStn",114741,0.62,null,500,"Y",3,"Y"]
["West Midlands","Pattingham 33/11kV S Stn","Pattingham33/11kVSStn",670142,0.12,null,205,"",3,"Y"]
["South West","Paulton 33/11kV S Stn","Paulton33/11kVSStn",161315,0.19700000000000001,null,127,"",3,"Y"]
["South Wales","Peakgen Barry STOR 33kV S Stn","PeakgenBarrySTOR33kVSStn",510366,0.23,null,500,"Y",3,"Y"]
["South West","Peasedown 33/11kV S Stn","Peasedown33/11kVSStn",162406,0.10199999999999999,null,113,"",3,"Y"]
["East Midlands","Pebble Hall Generation 33kV S Stn","PebbleHallGeneration33kVSStn",939208,0.182,null,355,"",3,"Y"]
["South Wales","Pembroke Power Station 400/132kV S Stn","PembrokePowerStation400/132kVSStn",600029,0.2,"Y",2300,"",1,"Y"]
["South West","Penare Farm Solar Farm 33kV S Stn","PenareFarmSolarFarm33kVSStn",418069,0.41,null,500,"Y",3,"Y"]
["South Wales","Penarth 33/11kV S Stn","Penarth33/11kVSStn",510199,0.14199999999999999,null,500,"Y",3,"Y"]
["South Wales","Penblewin 33/11kV S Stn","Penblewin33/11kVSStn",600200,0.80200000000000005,null,500,"Y",3,"Y"]
["South Wales","Pen Bryn Oer Windfarm 33kV S Stn","PenBrynOerWindfarm33kVSStn",550437,0.55400000000000005,null,680,"",3,"Y"]
["South Wales","Pencoed BSP 132/11kV S Stn","PencoedBSP132/11kVSStn",560912,0.189,null,1000,"Y",1,"Y"]
["South West","Pencoose Solar Park 33kV S Stn","PencooseSolarPark33kVSStn",418125,1.26,null,500,"Y",3,"Y"]
["South Wales","Pendine 33/11kV S Stn","Pendine33/11kVSStn",580201,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Pengam Grid 132/11kV S Stn","PengamGrid132/11kVSStn",550202,0.13100000000000001,null,1000,"Y",1,"Y"]
["South West","Penhale Solar Farm 33kV S Stn","PenhaleSolarFarm33kVSStn",438039,0.8,null,500,"Y",3,"Y"]
["West Midlands","Penn 400/275/132kV S Stn","Penn400/275/132kVSStn",670009,9.7000000000000003E-2,null,1242,"",1,"Y"]
["South West","Penn Cross 33/11kV S Stn","PennCross33/11kVSStn",250320,0.29199999999999998,null,455,"",3,"Y"]
["South Wales","Pen Rhiw Caradog Pv Generation 33kV S Stn","PenRhiwCaradogPvGeneration33kVSStn",550409,0.751,null,500,"Y",3,"Y"]
["South West","Penryn 33/11kV S Stn","Penryn33/11kVSStn",417170,0.99399999999999999,null,1552,"",3,"Y"]
["South West","Pensilva 33/11kV S Stn","Pensilva33/11kVSStn",457470,5.0110000000000001,null,3403,"",3,"Y"]
["South Wales","Pentrebach 33/11kV S Stn","Pentrebach33/11kVSStn",550203,0.15,null,500,"Y",3,"Y"]
["South Wales","Pentre Solar Farm Generation 33kV S Stn","PentreSolarFarmGeneration33kVSStn",520365,0.8,null,500,"Y",3,"Y"]
["South Wales","Pen Y Cae Solar 33kV S Stn","PenYCaeSolar33kVSStn",520371,0.2,null,500,"Y",3,"Y"]
["South Wales","Pen Y Cymoedd Wind Farm 33kV S Stn","PenYCymoeddWindFarm33kVSStn",550400,0.7,"Y",500,"Y",3,"Y"]
["South West","Penzance Causewayhead 33/11kV S Stn","PenzanceCausewayhead33/11kVSStn",417580,0.112,null,149,"",3,"Y"]
["South West","Penzance Heamoor 33/11kV S Stn","PenzanceHeamoor33/11kVSStn",417080,0.32300000000000001,null,627,"",3,"Y"]
["South West","Periton 33/11kV S Stn","Periton33/11kVSStn",210180,0.255,null,172,"",3,"Y"]
["South West","Perranporth 33/11kV S Stn","Perranporth33/11kVSStn",417100,4.29,null,3693,"",3,"Y"]
["West Midlands","Perry Barr 132/11kV S Stn","PerryBarr132/11kVSStn",670071,0.112,null,445,"",1,"Y"]
["West Midlands","Pershore 66/11kV S Stn","Pershore66/11kVSStn",670095,0.17100000000000001,null,324,"",3,"Y"]
["West Midlands","Peterchurch 66/11kV S Stn","Peterchurch66/11kVSStn",670099,0.22,null,303,"",3,"Y"]
["East Midlands","Petsoe Manor Wind Farm 33kV S Stn","PetsoeManorWindFarm33kVSStn",940024,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Pineham 33/11kV S Stn","Pineham33/11kVSStn",940021,0.22800000000000001,null,392,"",3,"Y"]
["South West","Pinhoe 33/11kV S Stn","Pinhoe33/11kVSStn",310026,5.0999999999999997E-2,null,31,"",3,"Y"]
["East Midlands","Pinxton 132/11kV S Stn","Pinxton132/11kVSStn",890021,0.13400000000000001,null,601,"",1,"Y"]
["East Midlands","Pinxton 132kV S Stn","Pinxton132kVSStn",680010,0.13400000000000001,null,601,"",1,"Y"]
["East Midlands","Pipewell Road PV 33kV S Stn","PipewellRoadPV33kVSStn",926202,0.13,null,202,"",3,"Y"]
["West Midlands","Pitchford Solar Farm 33kV S Stn","PitchfordSolarFarm33kVSStn",841751,0.19,null,191,"",3,"Y"]
["South West","Pitts Farm Solar Park 33kV S Stn","PittsFarmSolarPark33kVSStn",168105,0.65600000000000003,null,500,"Y",3,"Y"]
["South West","Pitworthy Solar Park 33kV S Stn","PitworthySolarPark33kVSStn",358074,0.33700000000000002,null,500,"Y",3,"Y"]
["South West","Place Barton Farm Solar Park 33kV S Stn","PlaceBartonFarmSolarPark33kVSStn",348176,0.89551000000000003,null,500,"Y",3,"Y"]
["South West","Plymouth 132/33kV S Stn","Plymouth132/33kVSStn",330003,8.5999999999999993E-2,null,43,"",3,"Y"]
["South West","Plymouth BSP 33kV S Stn","PlymouthBSP33kVSStn",330045,8.5999999999999993E-2,null,43,"",3,"Y"]
["South West","Plympton 132/33kV S Stn","Plympton132/33kVSStn",330006,0.67900000000000005,null,764,"",3,"Y"]
["South West","Plymstock South 33/11kV S Stn","PlymstockSouth33/11kVSStn",330037,0.157,null,229,"",3,"Y"]
["East Midlands","Polesworth 33/11kV S Stn","Polesworth33/11kVSStn",930072,0.11,null,259,"",3,"Y"]
["South West","Polzeath 33/11kV S Stn","Polzeath33/11kVSStn",437550,2.573,null,2560,"",3,"Y"]
["South Wales","Pont Andrew PV Generation 33kV S Stn","PontAndrewPVGeneration33kVSStn",520346,0.68100000000000005,null,500,"Y",3,"Y"]
["South Wales","Pont Ar Annell 33/11kV S Stn","PontArAnnell33/11kVSStn",590206,1.28,null,500,"Y",3,"Y"]
["South Wales","Pontardawe 33/11kV S Stn","Pontardawe33/11kVSStn",520207,0.3,null,500,"Y",3,"Y"]
["South Wales","Pontllanffraith 33/11kV S Stn","Pontllanffraith33/11kVSStn",550208,0.126,null,500,"Y",3,"Y"]
["West Midlands","Pontrilas 66/11kV S Stn","Pontrilas66/11kVSStn",670106,0.2,null,380,"",3,"Y"]
["South Wales","Pontyates 33/11kV S Stn","Pontyates33/11kVSStn",520209,0.93600000000000005,null,500,"Y",3,"Y"]
["South Wales","Pontyclun 132/11kV S Stn","Pontyclun132/11kVSStn",540913,0.16200000000000001,null,1000,"Y",1,"Y"]
["South Wales","Pontypool North 132/11kV S Stn","PontypoolNorth132/11kVSStn",530907,7.0999999999999994E-2,null,307,null,1,"Y"]
["West Midlands","Port Ham 400/132kV S Stn","PortHam400/132kVSStn",670008,0.63,null,561,"",1,"Y"]
["South West","Portishead 132/33kV S Stn","Portishead132/33kVSStn",182800,5.8999999999999997E-2,null,118,"",3,"Y"]
["South West","Portishead Ashlands 33/11kV S Stn","PortisheadAshlands33/11kVSStn",182983,5.8999999999999997E-2,null,423,"",3,"Y"]
["East Midlands","Portway 33/11kV S Stn","Portway33/11kVSStn",940038,3.3000000000000002E-2,null,65,"",3,"Y"]
["South West","Portworthy Dams Solar Park 33kV S Stn","PortworthyDamsSolarPark33kVSStn",338151,0.31,null,500,"Y",3,"Y"]
["West Midlands","Presteigne 66/11kV S Stn","Presteigne66/11kVSStn",670111,0.44,null,722,"",3,"Y"]
["East Midlands","Prestop Fm Burton Rd Ashby 33kv S Stn","PrestopFmBurtonRdAshby33kvSStn",939150,0.129,null,500,"Y",3,"Y"]
["West Midlands","Priestweston 33/11kV S Stn","Priestweston33/11kVSStn",840005,0.81,null,811,"",3,"Y"]
["South West","Prince Rock 33/11kV S Stn","PrinceRock33/11kVSStn",330027,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Princess Royal 33/11kV S Stn","PrincessRoyal33/11kVSStn",790028,0.28899999999999998,null,390,"",3,"Y"]
["East Midlands","Princethorpe 33/11kV S Stn","Princethorpe33/11kVSStn",930059,0.2,null,342,"",3,"Y"]
["South West","Priorswood 33/11kV S Stn","Priorswood33/11kVSStn",210040,7.4999999999999997E-2,null,112,"",3,"Y"]
["East Midlands","Private Road No 5 Colwick STOR 33kV S Stn","PrivateRoadNo5ColwickSTOR33kVSStn",883570,0.7,"Y",500,"Y",3,"Y"]
["South West","Probus 33/11kV S Stn","Probus33/11kVSStn",417560,2.69,null,1783,"",3,"Y"]
["South West","Puriton Landfill Solar Park 33kV S Stn","PuritonLandfillSolarPark33kVSStn",218025,0.115,null,500,"Y",3,"Y"]
["South Wales","Pwllfa Gwatkin 33kV S Stn","PwllfaGwatkin33kVSStn",520318,1.6819999999999999,null,500,"Y",3,"Y"]
["South Wales","Pyle Grid 132/33/11kV S Stn","PyleGrid132/33/11kVSStn",560030,0.14299999999999999,null,2159,"",3,"Y"]
["South West","Pylle Solar Park 33kV S Stn","PylleSolarPark33kVSStn",168138,0.17699999999999999,null,500,"Y",3,"Y"]
["East Midlands","Pytchley Road 33/11kV S Stn","PytchleyRoad33/11kVSStn",920009,7.5999999999999998E-2,null,131,"",3,"Y"]
["South West","Pyworthy 132/33kV S Stn","Pyworthy132/33kVSStn",350001,0.57199999999999995,null,904,"",3,"Y"]
["South West","Quartley 33kV S Stn","Quartley33kVSStn",210540,3.95,null,2386,"",3,"Y"]
["West Midlands","Quatt 33/11kV S Stn","Quatt33/11kVSStn",770003,0.127,null,254,"",3,"Y"]
["East Midlands","Queens Park 33/11kV S Stn","QueensPark33/11kVSStn",890079,0.1,null,159,"",3,"Y"]
["East Midlands","Quorn 33/11kV S Stn","Quorn33/11kVSStn",920022,0.20100000000000001,null,390,"",3,"Y"]
["South West","R.O.F. Power House 33kV S Stn","R.O.F.PowerHouse33kVSStn",210999,6.2E-2,null,93,"",3,"Y"]
["South West","Radstock 132/33kV S Stn","Radstock132/33kVSStn",162633,0.25700000000000001,null,247,"",3,"Y"]
["East Midlands","RAF Cranwell High G Facility 33kV S Stn","RAFCranwellHighGFacility33kVSStn",917678,1.04,null,1372,"",3,"Y"]
["East Midlands","Ragdale PV Solar Park 33kV S Stn","RagdalePVSolarPark33kVSStn",926220,9.7000000000000003E-2,null,106,"",3,"Y"]
["South West","Rame132/33kV S Stn","Rame132/33kVSStn",417500,1.7230000000000001,null,2340,"",3,"Y"]
["South Wales","Rassau Industrial Estate Stor Generation 33kV S Stn","RassauIndustrialEstateStorGeneration33kVSStn",550418,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Rassau Supergrid 400/132kV S Stn","RassauSupergrid400/132kVSStn",550906,7.9000000000000001E-2,null,4870,"",1,"Y"]
["South Wales","Rassau West 132/11kV S Stn","RassauWest132/11kVSStn",550288,0.2,"Y",1000,"Y",1,"Y"]
["East Midlands","Ratcliffe 400/132kV S Stn","Ratcliffe400/132kVSStn",680002,6.4399999999999999E-2,null,1269,"",1,"Y"]
["East Midlands","Ratcliffe On Soar 33/11kV S Stn","RatcliffeOnSoar33/11kVSStn",880018,6.4399999999999999E-2,null,1269,"",3,"Y"]
["East Midlands","Raunds 33/11kV S Stn","Raunds33/11kVSStn",920062,0.12,null,190,"",3,"Y"]
["East Midlands","Raunds 33kV S Stn","Raunds33kVSStn",690074,0.12,null,190,"",3,"Y"]
["South Wales","Ravenhill 33/11kV S Stn","Ravenhill33/11kVSStn",520211,5.6259999999999998E-2,null,161,"",3,"Y"]
["East Midlands","Ravensdale Park 33/11kV S Stn","RavensdalePark33/11kVSStn",870033,0.20200000000000001,null,290,"",3,"Y"]
["South Wales","Red Court Solar Farm 33kV S Stn","RedCourtSolarFarm33kVSStn",580394,0.16900000000000001,null,500,"Y",3,"Y"]
["East Midlands","Redcross Street 33/11kV S Stn","RedcrossStreet33/11kVSStn",920032,9.7000000000000003E-2,null,148,"",3,"Y"]
["West Midlands","Redditch North 66/11kV S Stn","RedditchNorth66/11kVSStn",670119,0.122,null,232,"",3,"Y"]
["West Midlands","Redditch South 66/11kV S Stn","RedditchSouth66/11kVSStn",670118,7.3999999999999996E-2,null,221,"",3,"Y"]
["East Midlands","Redfield Road 1 STOR 33kV S Stn","RedfieldRoad1STOR33kVSStn",883447,0.42,null,593,"",3,"Y"]
["East Midlands","Redfield Road 2 STOR 33kV S Stn","RedfieldRoad2STOR33kVSStn",883503,0.36,null,683,"",3,"Y"]
["South West","Red Hill Solar Park 33kV S Stn","RedHillSolarPark33kVSStn",318155,0.27100000000000002,null,500,"Y",3,"Y"]
["East Midlands","Redhouse Farm Wind Farm Gedney 33kV S Stn","RedhouseFarmWindFarmGedney33kVSStn",910016,4.8000000000000001E-2,null,50,"",3,"Y"]
["South West","Redlands Farm Solar Park 33kV S Stn","RedlandsFarmSolarPark33kVSStn",218017,0.13,null,500,"Y",3,"Y"]
["West Midlands","Rednal 132/11kV S Stn","Rednal132/11kVSStn",670072,6.4000000000000001E-2,null,620,"",1,"Y"]
["South West","Redruth 33/11kV S Stn","Redruth33/11kVSStn",417110,0.42599999999999999,null,849,"",3,"Y"]
["East Midlands","Regent Street 33/11kV S Stn","RegentStreet33/11kVSStn",910049,0.21,null,414,"",3,"Y"]
["East Midlands","Retford 132/25kV S Stn","Retford132/25kVSStn",680021,0.253,null,1204,"",1,"Y"]
["East Midlands","Retford Road Solar Generation 33kV S Stn","RetfordRoadSolarGeneration33kVSStn",898483,0.53,null,695,"",3,"Y"]
["South West","Rew Farm Solar Park 33kV S Stn","RewFarmSolarPark33kVSStn",438037,0.57999999999999996,null,500,"Y",3,"Y"]
["South West","Rexon Cross Farm Solar Park 33kV S Stn","RexonCrossFarmSolarPark33kVSStn",358064,0.45800000000000002,null,500,"Y",3,"Y"]
["South Wales","Rhayader 66/11kV S Stn","Rhayader66/11kVSStn",610277,0.439,null,285,null,3,"Y"]
["South Wales","Rhewl Farm Solar Park 33kV S Stn","RhewlFarmSolarPark33kVSStn",530414,0.29599999999999999,null,500,"Y",3,"Y"]
["South Wales","Rhigos Road Gas Generation 33kV S Stn","RhigosRoadGasGeneration33kVSStn",550433,1.573,null,500,"Y",3,"Y"]
["South Wales","Rhos 132/33/11kV S Stn","Rhos132/33/11kVSStn",580031,1.21,null,1000,"Y",3,"Y"]
["South Wales","Rhoscrowther 132kV S Stn","Rhoscrowther132kVSStn",600448,0.2,"Y",1000,"Y",1,"Y"]
["South Wales","Rhyd Y Pandy Solar Park 33kV S Stn","RhydYPandySolarPark33kVSStn",520386,0.25,null,500,"Y",3,"Y"]
["South Wales","Ringland Newport 33/11kV S Stn","RinglandNewport33/11kVSStn",530214,6.8000000000000005E-2,null,98,null,3,"Y"]
["West Midlands","Ring O Bells Solar Farm 33kV S Stn","RingOBellsSolarFarm33kVSStn",795658,0.14599999999999999,null,203,"",3,"Y"]
["East Midlands","Ripley 33/11kV S Stn","Ripley33/11kVSStn",890088,0.16300000000000001,null,319,"",3,"Y"]
["East Midlands","Roade 33/11kV S Stn","Roade33/11kVSStn",940063,0.111,null,179,"",3,"Y"]
["East Midlands","Roade Wind Farm 33kV S Stn","RoadeWindFarm33kVSStn",945674,0.12,null,194,"",3,"Y"]
["South West","Roadford 33kV S Stn","Roadford33kVSStn",350023,0.41,null,406,"",3,"Y"]
["East Midlands","Robert Hyde 33/11kV S Stn","RobertHyde33/11kVSStn",890081,0.17699999999999999,null,350,"",3,"Y"]
["South Wales","Robeston 132/11kV S Stn","Robeston132/11kVSStn",600043,0.2,"Y",1000,"Y",1,"Y"]
["East Midlands","Robin Hood 33/11kV S Stn","RobinHood33/11kVSStn",890069,0.26800000000000002,null,359,"",3,"Y"]
["East Midlands","Rocester 33/11kV S Stn","Rocester33/11kVSStn",870026,0.13100000000000001,null,197,"",3,"Y"]
["West Midlands","Rock Farm ESS 33kV S Stn","RockFarmESS33kVSStn",745828,0.7,"Y",500,"Y",3,"Y"]
["South West","Rockhead Wind Farm 33kV S Stn","RockheadWindFarm33kVSStn",438018,1.133,null,1176,"",3,"Y"]
["South West","Rockingham 33kV S Stn","Rockingham33kVSStn",118183,0.23,null,500,"Y",3,"Y"]
["East Midlands","Rockingham Data Centre 33kV S Stn","RockinghamDataCentre33kVSStn",926100,0.25,null,408,"",3,"Y"]
["South West","Rock Park 132/33/11kV S Stn","RockPark132/33/11kVSStn",260590,6.2E-2,null,116,"",3,"Y"]
["South Wales","Rogerstone 66/11kV S Stn","Rogerstone66/11kVSStn",530333,0.20399999999999999,null,157,null,3,"Y"]
["East Midlands","Rolleston Park Solar Farm 33kV S Stn","RollestonParkSolarFarm33kVSStn",874992,0.16,null,255,"",3,"Y"]
["South West","Rolls Royce Filton 132kV S Stn","RollsRoyceFilton132kVSStn",114059,0.13300000000000001,null,291,"",1,"Y"]
["South West","Rookery Farm Solar Park 33kV S Stn","RookeryFarmSolarPark33kVSStn",188139,0.254,null,500,"Y",3,"Y"]
["East Midlands","Rookery Lane 33/11kV S Stn","RookeryLane33/11kVSStn",900030,0.13,null,208,"",3,"Y"]
["South Wales","Rosedew Solar  Farm 33kV S Stn","RosedewSolarFarm33kVSStn",560408,0.34899999999999998,null,500,"Y",3,"Y"]
["South West","Roseland 33/11kV S Stn","Roseland33/11kVSStn",417120,3.1789999999999998,null,2241,"",3,"Y"]
["South West","Roskrow Barton Solar Park 33kV S Stn","RoskrowBartonSolarPark33kVSStn",418135,0.7,null,500,"Y",3,"Y"]
["West Midlands","Ross 66/11kV S Stn","Ross66/11kVSStn",670126,0.1,null,139,"",3,"Y"]
["West Midlands","Rotherdale Farm 66kv S Stn","RotherdaleFarm66kvSStn",759000,0.13,null,270,"",3,"Y"]
["West Midlands","Rotherdale Farm Pv 66kv S Stn","RotherdaleFarmPv66kvSStn",778160,0.13,null,270,"",3,"Y"]
["West Midlands","Rotol 33/11kV S Stn","Rotol33/11kVSStn",790029,0.06,null,186,"",3,"Y"]
["South West","Roundswell 33/11kV S Stn","Roundswell33/11kVSStn",260240,0.14000000000000001,null,133,"",3,"Y"]
["West Midlands","Roushill 33/11kV S Stn","Roushill33/11kVSStn",840020,0.08,null,166,"",3,"Y"]
["South Wales","Rover Way 132/11kV S Stn","RoverWay132/11kVSStn",510911,8.6999999999999994E-2,null,1000,"Y",1,"Y"]
["West Midlands","Rowton 33/11kV S Stn","Rowton33/11kVSStn",840024,0.34,null,510,"",3,"Y"]
["South West","Royal Portbury Dock 33/11kV S Stn","RoyalPortburyDock33/11kVSStn",182150,5.0999999999999997E-2,null,20,"",3,"Y"]
["South Wales","Rudbaxton PV Farm 33kV S Stn","RudbaxtonPVFarm33kVSStn",600352,0.20200000000000001,null,500,"Y",3,"Y"]
["East Midlands","Rufford 33/11kV S Stn","Rufford33/11kVSStn",890047,0.79200000000000004,null,1052,"",3,"Y"]
["East Midlands","Rugby 132/11kV S Stn","Rugby132/11kVSStn",930064,4.2000000000000003E-2,null,361,"",1,"Y"]
["East Midlands","Rugby 132/33/25/11kV S Stn","Rugby132/33/25/11kVSStn",690017,4.2000000000000003E-2,null,361,"",3,"Y"]
["East Midlands","Rugby 33kV S Stn","Rugby33kVSStn",930006,4.2000000000000003E-2,null,361,"",3,"Y"]
["East Midlands","Rugby Gateway 33/11kV S Stn","RugbyGateway33/11kVSStn",938836,0.25,null,265,"",3,"Y"]
["East Midlands","Rugby Portland Cement 33kV S Stn","RugbyPortlandCement33kVSStn",930021,4.2000000000000003E-2,null,361,"",3,"Y"]
["West Midlands","Rugeley 132kV S Stn","Rugeley132kVSStn",680051,7.4999999999999997E-2,null,983,"",1,"Y"]
["West Midlands","Rugeley 400/132kV S Stn","Rugeley400/132kVSStn",680008,7.4999999999999997E-2,null,983,"",1,"Y"]
["West Midlands","Rugeley Town 132/11kV S Stn","RugeleyTown132/11kVSStn",680061,0.21,null,507,"",1,"Y"]
["West Midlands","Rushall 132/11kV S Stn","Rushall132/11kVSStn",670073,0.16,null,498,"",1,"Y"]
["East Midlands","Rushden 33/11kV S Stn","Rushden33/11kVSStn",920056,0.13800000000000001,null,236,"",3,"Y"]
["East Midlands","Ruskington 33/11kV S Stn","Ruskington33/11kVSStn",910033,0.129,null,235,"",3,"Y"]
["East Midlands","Ruston & Hornsby 33/11kV S Stn","Ruston&Hornsby33/11kVSStn",900031,6.4000000000000001E-2,null,278,"",3,"Y"]
["South West","Rydon Farm Solar Park 33kV S Stn","RydonFarmSolarPark33kVSStn",348121,8.5999999999999993E-2,null,500,"Y",3,"Y"]
["West Midlands","Ryeford 132/33/11kV S Stn","Ryeford132/33/11kVSStn",670015,5.6000000000000001E-2,null,209,"",3,"Y"]
["East Midlands","Ryton 33/11kV S Stn","Ryton33/11kVSStn",930049,5.0999999999999997E-2,null,82,"",3,"Y"]
["South West","Salcombe 33/11kV S Stn","Salcombe33/11kVSStn",340038,0.20100000000000001,null,270,"",3,"Y"]
["South West","Saltash Dunheved Rd 33/11kV S Stn","SaltashDunhevedRd33/11kVSStn",457520,0.27500000000000002,null,271,"",3,"Y"]
["South West","Saltash Whity Cross 33/11kV S Stn","SaltashWhityCross33/11kVSStn",457280,3.0339999999999998,null,3501,"",3,"Y"]
["East Midlands","Salutation 33/6.6kV S Stn","Salutation33/6.6kVSStn",920037,5.8000000000000003E-2,null,211,"",3,"Y"]
["South Wales","Sanatorium 33/11kV S Stn","Sanatorium33/11kVSStn",510218,5.5E-2,null,500,"Y",3,"Y"]
["East Midlands","Sandiacre 33/11kV S Stn","Sandiacre33/11kVSStn",870051,9.8000000000000004E-2,null,190,"",3,"Y"]
["South Wales","Sandon St. 33/11kV S Stn","SandonSt.33/11kVSStn",510219,0.14000000000000001,null,500,"Y",3,"Y"]
["East Midlands","Sandy Lane 33/6.6kV S Stn","SandyLane33/6.6kVSStn",930040,6.4000000000000001E-2,null,100,"",3,"Y"]
["West Midlands","Sankey 33/11kV S Stn","Sankey33/11kVSStn",840012,0.27400000000000002,null,403,"",3,"Y"]
["East Midlands","Sapcote 33/11kV S Stn","Sapcote33/11kVSStn",930089,0.13300000000000001,null,254,"",3,"Y"]
["South Wales","Saron Solar Farm 33kV S Stn","SaronSolarFarm33kVSStn",520373,0.18,null,500,"Y",3,"Y"]
["South West","Sawles Road 33/11kV S Stn","SawlesRoad33/11kVSStn",437640,0.28899999999999998,null,252,"",3,"Y"]
["West Midlands","Say Farm 33kv S Stn","SayFarm33kvSStn",798100,0.22,null,303,"",3,"Y"]
["South Wales","Schwyll 33/11kV S Stn","Schwyll33/11kVSStn",560220,0.61599999999999999,null,500,"Y",3,"Y"]
["West Midlands","Scot Hay 33/11kV S Stn","ScotHay33/11kVSStn",850014,0.34,null,595,"",3,"Y"]
["South West","Seabank 132/33kV S Stn","Seabank132/33kVSStn",114259,8.5999999999999993E-2,null,695,"",3,"Y"]
["South West","Seabank 400/132kV S Stn","Seabank400/132kVSStn",114023,8.5999999999999993E-2,null,1274,"",1,"Y"]
["East Midlands","Secklow Gate 33/11kV S Stn","SecklowGate33/11kVSStn",940025,6.3E-2,null,137,"",3,"Y"]
["West Midlands","Selly Oak 132/11kV S Stn","SellyOak132/11kVSStn",670074,8.5999999999999993E-2,null,791,"",1,"Y"]
["West Midlands","Selly Oak 132kV S Stn","SellyOak132kVSStn",670039,8.5999999999999993E-2,null,791,"",1,"Y"]
["South West","Severnside Energy Recovery Centre 132kV S Stn","SevernsideEnergyRecoveryCentre132kVSStn",114756,0.125,null,1400,"Y",1,"Y"]
["East Midlands","Shanks Generation 33kV S Stn","ShanksGeneration33kVSStn",940017,0.06,null,68,"",3,"Y"]
["South West","Shapwick 33/11kV S Stn","Shapwick33/11kVSStn",210460,0.61399999999999999,null,1166,"",3,"Y"]
["South West","Sharland Farm Solar Park 33kV S Stn","SharlandFarmSolarPark33kVSStn",318172,0.219,null,500,"Y",3,"Y"]
["East Midlands","Sharnbrook 33/11kV S Stn","Sharnbrook33/11kVSStn",920057,0.06,null,103,"",3,"Y"]
["South West","Shebbear 33/11kV S Stn","Shebbear33/11kVSStn",350013,2.5,null,1853,"",3,"Y"]
["East Midlands","Sheepbridge 33/11kV S Stn","Sheepbridge33/11kVSStn",890023,0.112,null,318,"",3,"Y"]
["East Midlands","Sheffield Road 33/11/6.6kV S Stn","SheffieldRoad33/11/6.6kVSStn",890070,0.13500000000000001,null,266,"",3,"Y"]
["East Midlands","Shelton Lodge Solar Generation 33kV S Stn","SheltonLodgeSolarGeneration33kVSStn",883456,0.20300000000000001,null,285,"",3,"Y"]
["East Midlands","Shenley Wood 33/11kV S Stn","ShenleyWood33/11kVSStn",940069,6.4000000000000001E-2,null,124,"",3,"Y"]
["East Midlands","Shepshed 33/11kV S Stn","Shepshed33/11kVSStn",920019,0.08,null,154,"",3,"Y"]
["South West","Shepton Mallet 33/11kV S Stn","SheptonMallet33/11kVSStn",161641,0.192,null,251,"",3,"Y"]
["South West","Sherford IDNO Connection 33kV S Stn","SherfordIDNOConnection33kVSStn",338181,0.51800000000000002,null,500,"Y",3,"Y"]
["West Midlands","Sheriffhales Solar Farm 33kv S Stn","SheriffhalesSolarFarm33kvSStn",841865,0.13600000000000001,null,272,"",3,"Y"]
["East Midlands","Sherwood Park 33/11kV S Stn","SherwoodPark33/11kVSStn",890099,0.14099999999999999,null,190,"",3,"Y"]
["West Midlands","Shifnal 33/11kV S Stn","Shifnal33/11kVSStn",840004,0.22600000000000001,null,407,"",3,"Y"]
["South Wales","Ship Hill Barry 33/11kV S Stn","ShipHillBarry33/11kVSStn",510223,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Shipston 66/11kV S Stn","Shipston66/11kVSStn",670093,0.14799999999999999,null,202,"",3,"Y"]
["East Midlands","Shirebrook 33/11kV S Stn","Shirebrook33/11kVSStn",890034,0.23699999999999999,null,332,"",3,"Y"]
["West Midlands","Shirley 132/11kV S Stn","Shirley132/11kVSStn",670075,6.5000000000000002E-2,null,449,"",1,"Y"]
["South West","Shooters Bottom Solar Park 33kV S Stn","ShootersBottomSolarPark33kVSStn",168001,0.90400000000000003,null,500,"Y",3,"Y"]
["South West","Shooters Bottom W/F 33kV S Stn","ShootersBottomW/F33kVSStn",162888,1.2,null,1464,"",3,"Y"]
["West Midlands","Shrewsbury 400/132/33kV S Stn","Shrewsbury400/132/33kVSStn",680004,0.11700000000000001,null,1951,"",3,"Y"]
["East Midlands","Sibthorpe 33/11kV S Stn","Sibthorpe33/11kVSStn",880038,0.23,null,414,"",3,"Y"]
["South West","Sidmouth Town 33/11kV S Stn","SidmouthTown33/11kVSStn",310046,0.124,null,110,"",3,"Y"]
["East Midlands","Silverstone 33/11kV S Stn","Silverstone33/11kVSStn",940032,0.19400000000000001,null,198,"",3,"Y"]
["South Wales","Simms Metals 132kV S Stn","SimmsMetals132kVSStn",530914,0.17299999999999999,null,1000,"Y",1,"Y"]
["West Midlands","Simplex 33/11kV S Stn","Simplex33/11kVSStn",850029,4.9000000000000002E-2,null,110,"",3,"Y"]
["East Midlands","Sinfin C 33kV S Stn","SinfinC33kVSStn",870019,8.1000000000000003E-2,null,148,"",3,"Y"]
["East Midlands","Sinfin Lane 33/11kV S Stn","SinfinLane33/11kVSStn",870041,8.1000000000000003E-2,null,148,"",3,"Y"]
["East Midlands","Skegby Lane 33/11kV S Stn","SkegbyLane33/11kVSStn",890030,7.0000000000000007E-2,null,221,"",3,"Y"]
["East Midlands","Skegness 132/33kV S Stn","Skegness132/33kVSStn",690030,5.0999999999999997E-2,null,192,"",3,"Y"]
["East Midlands","Skegness 33kV S Stn","Skegness33kVSStn",900005,5.0999999999999997E-2,null,192,"",3,"Y"]
["South Wales","Sketty Park 33/11kV S Stn","SkettyPark33/11kVSStn",520225,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Skillington 33/11kV S Stn","Skillington33/11kVSStn",910040,0.433,null,550,"",3,"Y"]
["South West","Slade Farm Solar Park 33kV S Stn","SladeFarmSolarPark33kVSStn",348033,0.498,null,500,"Y",3,"Y"]
["East Midlands","Sleaford 132/33kV S Stn","Sleaford132/33kVSStn",690037,0.13700000000000001,null,349,"",3,"Y"]
["East Midlands","Sleaford 33/11kV S Stn","Sleaford33/11kVSStn",910021,0.13700000000000001,null,349,"",3,"Y"]
["East Midlands","Sleaford 33kV S Stn","Sleaford33kVSStn",910008,0.13700000000000001,null,349,"",3,"Y"]
["East Midlands","Sleaford REP 132kV S Stn","SleafordREP132kVSStn",690068,0.2,"Y",1000,"Y",1,"Y"]
["East Midlands","Sleaford Road, Boston 33kV S Stn","SleafordRoad,Boston33kVSStn",900006,0.11,null,330,"",3,"Y"]
["West Midlands","Smethwick 132/11kV S Stn","Smethwick132/11kVSStn",670076,0.153,null,1121,"",1,"Y"]
["East Midlands","Smith Hall Farm Solar Plant 33kV S Stn","SmithHallFarmSolarPlant33kVSStn",874972,0.28999999999999998,null,235,"",3,"Y"]
["West Midlands","Snedshill 33/11kV S Stn","Snedshill33/11kVSStn",840011,0.1,null,249,"",3,"Y"]
["East Midlands","Sneinton 33/11kV S Stn","Sneinton33/11kVSStn",880030,9.1999999999999998E-2,null,141,"",3,"Y"]
["West Midlands","Solihull 132/11kV S Stn","Solihull132/11kVSStn",670077,0.09,null,252,"",1,"Y"]
["East Midlands","Somercotes 33/11kV S Stn","Somercotes33/11kVSStn",890086,9.2999999999999999E-2,null,147,"",3,"Y"]
["South West","Somerton 33/11kV S Stn","Somerton33/11kVSStn",210080,0.06,null,69,"",3,"Y"]
["South West","Somerton Door Solar Park 33kV S Stn","SomertonDoorSolarPark33kVSStn",218019,7.8E-2,null,500,"Y",3,"Y"]
["East Midlands","Southam 33/11kV S Stn","Southam33/11kVSStn",930060,0.10199999999999999,null,168,"",3,"Y"]
["South West","South Brent 33/11kV S Stn","SouthBrent33/11kVSStn",340015,0.5,null,671,"",3,"Y"]
["East Midlands","South Carlton 33kV S Stn","SouthCarlton33kVSStn",900027,0.129,null,249,"",3,"Y"]
["South Wales","South Cornelly 33kV S Stn","SouthCornelly33kVSStn",560311,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","South Croxton 33/11kV S Stn","SouthCroxton33/11kVSStn",920041,0.183,null,207,"",3,"Y"]
["East Midlands","South Holland 132/33kV S Stn","SouthHolland132/33kVSStn",690040,3.9E-2,null,359,"",3,"Y"]
["East Midlands","South Holland 33kV S Stn","SouthHolland33kVSStn",910010,3.9E-2,null,359,"",3,"Y"]
["South Wales","South Hook 132/33kV S Stn","SouthHook132/33kVSStn",600319,0.15,null,1000,"Y",3,"Y"]
["South West","South Molton 33/11kV S Stn","SouthMolton33/11kVSStn",260260,1.1100000000000001,null,1095,"",3,"Y"]
["South West","Southway 33/11kV S Stn","Southway33/11kVSStn",330023,0.245,null,70,"",3,"Y"]
["East Midlands","Southwell 33/11kV S Stn","Southwell33/11kVSStn",890059,0.153,null,289,"",3,"Y"]
["South West","Sowton 132/33/11kV S Stn","Sowton132/33/11kVSStn",310005,0.1,null,643,"",3,"Y"]
["South West","Sowton 33/11kV S Stn","Sowton33/11kVSStn",310028,0.1,null,20,"",3,"Y"]
["South West","Sowton B 33/11kV S Stn","SowtonB33/11kVSStn",310059,0.1,null,500,"Y",3,"Y"]
["East Midlands","Spalding 132/33kV S Stn","Spalding132/33kVSStn",690036,3.4000000000000002E-2,null,147,"",3,"Y"]
["East Midlands","Spalding Clay Lake 33/11kV S Stn","SpaldingClayLake33/11kVSStn",910028,3.4000000000000002E-2,null,145,"",3,"Y"]
["East Midlands","Spalding Clay Lake 33kV S Stn","SpaldingClayLake33kVSStn",910009,3.4000000000000002E-2,null,145,"",3,"Y"]
["East Midlands","Spalding Park Road 33/11kV S Stn","SpaldingParkRoad33/11kVSStn",910023,0.06,null,90,"",3,"Y"]
["West Midlands","Sparkbrook 132/11kV S Stn","Sparkbrook132/11kVSStn",670078,0.04,null,274,"",1,"Y"]
["East Midlands","Spilsby 33kV S Stn","Spilsby33kVSStn",900016,0.20300000000000001,null,357,"",3,"Y"]
["East Midlands","Spondon 33/11kV S Stn","Spondon33/11kVSStn",870046,7.1999999999999995E-2,null,984,"",3,"Y"]
["East Midlands","Spondon 33kV S Stn","Spondon33kVSStn",870006,7.1999999999999995E-2,null,984,"",3,"Y"]
["East Midlands","Spondon A 132kV S Stn","SpondonA132kVSStn",680030,0.2,"Y",1000,"Y",1,"Y"]
["East Midlands","Spondon 'B' 132/33kV S Stn","Spondon'B'132/33kVSStn",680031,0.2,"Y",1000,"Y",3,"Y"]
["East Midlands","Spon Street 33/6.6kV S Stn","SponStreet33/6.6kVSStn",930041,0.1,null,200,"",3,"Y"]
["West Midlands","Spring Gardens 33/11kV S Stn","SpringGardens33/11kVSStn",840025,0.23,null,368,"",3,"Y"]
["West Midlands","Stafford 132/25/11kV S Stn","Stafford132/25/11kVSStn",680058,5.7000000000000002E-2,null,304,"",1,"Y"]
["West Midlands","Stafford South 132/11kV S Stn","StaffordSouth132/11kVSStn",680049,4.1000000000000002E-2,null,178,"",1,"Y"]
["West Midlands","Stafford South 132/11kV S Stn","StaffordSouth132/11kVSStn",680062,0.04,null,70,"",1,"Y"]
["West Midlands","Stagefields 132/33/11kV S Stn","Stagefields132/33/11kVSStn",680059,6.3E-2,null,632,"",3,"Y"]
["South West","St Agnes 33/11kV S Stn","StAgnes33/11kVSStn",417590,4.59,null,2528,"",3,"Y"]
["East Midlands","Stamford 132/33kV S Stn","Stamford132/33kVSStn",690035,5.6000000000000001E-2,null,222,"",3,"Y"]
["East Midlands","Stamford 33/11kV S Stn","Stamford33/11kVSStn",910050,5.6000000000000001E-2,null,222,"",3,"Y"]
["East Midlands","Stamford 33kV S Stn","Stamford33kVSStn",910004,5.6000000000000001E-2,null,222,"",3,"Y"]
["South West","Stancombe Quarry 33kV S Stn","StancombeQuarry33kVSStn",182768,1.0840000000000001,null,1444,"",3,"Y"]
["East Midlands","St Anns 33/11kV S Stn","StAnns33/11kVSStn",880040,0.218,null,294,"",3,"Y"]
["East Midlands","Stanton 132/33kV S Stn","Stanton132/33kVSStn",680042,7.3200000000000001E-2,null,457,"",3,"Y"]
["East Midlands","Stanton 33kV S Stn","Stanton33kVSStn",870011,7.3200000000000001E-2,null,457,"",3,"Y"]
["South West","Staplegrove 33/11kV S Stn","Staplegrove33/11kVSStn",210500,0.14799999999999999,null,183,"",3,"Y"]
["South West","Staplehill 33kV S Stn","Staplehill33kVSStn",114393,0.43,null,132,"",3,"Y"]
["West Midlands","Star Aluminium 33/11kV S Stn","StarAluminium33/11kVSStn",770004,0.19400000000000001,null,139,"",3,"Y"]
["South Wales","St Arvans 33/11kV S Stn","StArvans33/11kVSStn",530226,1.1020000000000001,null,905,null,3,"Y"]
["East Midlands","Station Street 33/11kV S Stn","StationStreet33/11kVSStn",870032,0.26,null,248,"",3,"Y"]
["West Midlands","Staunch Standby Generation 33kv S Stn","StaunchStandbyGeneration33kvSStn",857114,0.89,null,447,"",3,"Y"]
["South West","St Austell  33/11kV S Stn","StAustell33/11kVSStn",437190,0.77,null,1482,"",3,"Y"]
["South West","St Austell BSP 132/33kV S Stn","StAustellBSP132/33kVSStn",437730,0.629,null,775,"",3,"Y"]
["East Midlands","Staveley 132/33kV S Stn","Staveley132/33kVSStn",680039,4.8599999999999997E-2,null,372,"",3,"Y"]
["East Midlands","Staveley 33/11kV S Stn","Staveley33/11kVSStn",890080,4.8599999999999997E-2,null,372,"",3,"Y"]
["East Midlands","Staveley 33kV S Stn","Staveley33kVSStn",890015,4.8599999999999997E-2,null,372,"",3,"Y"]
["East Midlands","Staveley Works 33kV S Stn","StaveleyWorks33kVSStn",890098,6.3E-2,null,156,"",3,"Y"]
["East Midlands","Staythorpe B 132kV S Stn","StaythorpeB132kVSStn",680020,0.2,"Y",1000,"Y",1,"Y"]
["East Midlands","Staythorpe C 400/132kV S Stn","StaythorpeC400/132kVSStn",680001,0.2,"Y",2800,"Y",1,"Y"]
["South West","St Blazey 33kV S Stn","StBlazey33kVSStn",437200,0.443,null,678,"",3,"Y"]
["South West","St Breock 33kV S Stn","StBreock33kVSStn",437790,0.83,null,425,"",3,"Y"]
["South West","St Buryan 33/11kV S Stn","StBuryan33/11kVSStn",417090,6.9039999999999999,null,4163,"",3,"Y"]
["South Wales","St Clears 33/11kV S Stn","StClears33/11kVSStn",580228,1.1970000000000001,null,1161,"",3,"Y"]
["South West","St Columb Major 33/11kV S Stn","StColumbMajor33/11kVSStn",437490,1.591,null,1632,"",3,"Y"]
["South Wales","St Davids 33/11kV S Stn","StDavids33/11kVSStn",600271,2.3860000000000001,null,500,"Y",3,"Y"]
["South West","St Day Landfill 33kV S Stn","StDayLandfill33kVSStn",417670,0.63,null,419,"",3,"Y"]
["South West","Stentaway 33/11kV S Stn","Stentaway33/11kVSStn",330031,8.6999999999999994E-2,null,73,"",3,"Y"]
["South Wales","Steynton 33/11kV S Stn","Steynton33/11kVSStn",600232,0.19,null,500,"Y",3,"Y"]
["South Wales","St Florence 33/11kV S Stn","StFlorence33/11kVSStn",600229,2.0499999999999998,null,500,"Y",3,"Y"]
["South West","St Germans 132/33kV S Stn","StGermans132/33kVSStn",457510,0.95299999999999996,null,3810,"",3,"Y"]
["East Midlands","Stickney 33kV S Stn","Stickney33kVSStn",900020,0.27200000000000002,null,310,"",3,"Y"]
["South West","St Ives 33/11kV S Stn","StIves33/11kVSStn",417130,3.37,null,5220,"",3,"Y"]
["South West","St Keverne 33/11kV S Stn","StKeverne33/11kVSStn",417330,4.3120000000000003,null,4271,"",3,"Y"]
["South West","St Levan Road 33/11kV S Stn","StLevanRoad33/11kVSStn",330013,8.7999999999999995E-2,null,130,"",3,"Y"]
["South West","St Mawgan 33/11kV S Stn","StMawgan33/11kVSStn",437440,0.76800000000000002,null,658,"",3,"Y"]
["South Wales","St Mellons 33/11kV S Stn","StMellons33/11kVSStn",510230,0.13600000000000001,null,500,"Y",3,"Y"]
["South West","St Neot 33/11kV S Stn","StNeot33/11kVSStn",457480,3.91,null,2491,"",3,"Y"]
["West Midlands","Stockton 33/11kV S Stn","Stockton33/11kVSStn",770002,0.375,null,348,"",3,"Y"]
["East Midlands","Stoke Bardolph 400/132kV S Stn","StokeBardolph400/132kVSStn",680068,0.2,"Y",2800,"Y",1,"Y"]
["South West","Stoke Bishop 33/11kV S Stn","StokeBishop33/11kVSStn",112389,0.12,null,500,"Y",3,"Y"]
["West Midlands","Stoke CHP 33kV S Stn","StokeCHP33kVSStn",850011,0.7,"Y",500,"Y",3,"Y"]
["South West","Stokenham 33/11kV S Stn","Stokenham33/11kVSStn",340041,0.45500000000000002,null,348,"",3,"Y"]
["South West","Stonebarrow Farm Solar Farm 33kV S Stn","StonebarrowFarmSolarFarm33kVSStn",258073,0.151,null,500,"Y",3,"Y"]
["South West","Stoneshill Solar Park 33kV S Stn","StoneshillSolarPark33kVSStn",318173,0.19600000000000001,null,500,"Y",3,"Y"]
["East Midlands","Stoneygate 33/6.6kV S Stn","Stoneygate33/6.6kVSStn",920038,6.9000000000000006E-2,null,111,"",3,"Y"]
["East Midlands","Stonish Hill Windfarm 33kV S Stn","StonishHillWindfarm33kVSStn",898181,0.14000000000000001,null,278,"",3,"Y"]
["East Midlands","Stony Stratford 132/33kV S Stn","StonyStratford132/33kVSStn",690045,9.1999999999999998E-2,null,1074,"",3,"Y"]
["East Midlands","Stony Stratford 33kV S Stn","StonyStratford33kVSStn",940005,9.1999999999999998E-2,null,1074,"",3,"Y"]
["South Wales","Stormy Down Pv Generation 33kV S Stn","StormyDownPvGeneration33kVSStn",560405,1,null,1331,"",3,"Y"]
["West Midlands","Stourport 132/66/33/11kV S Stn","Stourport132/66/33/11kVSStn",670079,0.112,null,618,"",3,"Y"]
["West Midlands","Stow 66/11kV S Stn","Stow66/11kVSStn",670091,1.66,null,2296,"",3,"Y"]
["West Midlands","Stowfield 33/11kV S Stn","Stowfield33/11kVSStn",790017,0.246,null,236,"",3,"Y"]
["South West","St Pauls 132/11kV S Stn","StPauls132/11kVSStn",113450,0.06,null,314,"",1,"Y"]
["South West","St Pauls BSP 132/11kV S Stn","StPaulsBSP132/11kVSStn",110804,0.06,null,43,"",1,"Y"]
["South Wales","St Peters Church Wind Farm 33kV S Stn","StPetersChurchWindFarm33kVSStn",540425,0.92300000000000004,null,500,"Y",3,"Y"]
["East Midlands","Stragglethorpe Road Pv Solar Park 33kv S Stn","StragglethorpeRoadPvSolarPark33kvSStn",883465,0.128,null,236,"",3,"Y"]
["South Wales","Strand Swansea 33/11kV S Stn","StrandSwansea33/11kVSStn",520233,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Stratford 66/11kV S Stn","Stratford66/11kVSStn",670101,0.12,null,304,"",3,"Y"]
["South West","Stratton 33/11kV S Stn","Stratton33/11kVSStn",350012,0.36699999999999999,null,595,"",3,"Y"]
["South West","Street 132/33kV S Stn","Street132/33kVSStn",210448,0.28000000000000003,null,580,"",3,"Y"]
["West Midlands","Strensham 66/11kV S Stn","Strensham66/11kVSStn",670104,0.20200000000000001,null,352,"",3,"Y"]
["South West","St Stephen Solar Park 33kV S Stn","StStephenSolarPark33kVSStn",438094,0.36199999999999999,null,500,"Y",3,"Y"]
["South West","St Thomas 33/11kV S Stn","StThomas33/11kVSStn",310017,3.4000000000000002E-2,null,11,"",3,"Y"]
["South West","St Tudy 132/33kV S Stn","StTudy132/33kVSStn",407450,1.069,null,1110,"",3,"Y"]
["South West","St Tudy 33/11kV S Stn","StTudy33/11kVSStn",437450,1.069,null,2071,"",3,"Y"]
["South Wales","St Twynnells 33/11kV S Stn","StTwynnells33/11kVSStn",600231,1.4179999999999999,null,500,"Y",3,"Y"]
["West Midlands","St Weonards 66/11kV S Stn","StWeonards66/11kVSStn",670113,0.38400000000000001,null,472,"",3,"Y"]
["South Wales","Sudbrook 132/33kV S Stn","Sudbrook132/33kVSStn",530034,0.11,null,440,null,1,"Y"]
["West Midlands","Sudmeadow Road STOR Generation 33kV S Stn","SudmeadowRoadSTORGeneration33kVSStn",795794,0.8,null,1029,"",3,"Y"]
["South Wales","Sully Grid Primary 132/11kV S Stn","SullyGridPrimary132/11kVSStn",510909,0.13400000000000001,null,1000,"Y",1,"Y"]
["South Wales","Sully Moors Power Station 33kV S Stn","SullyMoorsPowerStation33kVSStn",510399,0.15,null,500,"Y",3,"Y"]
["West Midlands","Summer Lane 132/11kV S Stn","SummerLane132/11kVSStn",670027,0.08,null,240,"",1,"Y"]
["West Midlands","Sundorne Solar Farm 33kV S Stn","SundorneSolarFarm33kVSStn",841809,0.12,null,291,"",3,"Y"]
["West Midlands","Sutton Coldfield 132/11kV S Stn","SuttonColdfield132/11kVSStn",670080,9.6000000000000002E-2,null,703,"",1,"Y"]
["South Wales","Sutton Farm Solar Park 33kV S Stn","SuttonFarmSolarPark33kVSStn",510362,0.109,null,500,"Y",3,"Y"]
["East Midlands","Sutton Junction 33/11kV S Stn","SuttonJunction33/11kVSStn",890031,0.10100000000000001,null,225,"",3,"Y"]
["West Midlands","Swancote AD Generation 33kV S Stn","SwancoteADGeneration33kVSStn",856916,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Swansea North Grid 132/33kV S Stn","SwanseaNorthGrid132/33kVSStn",520035,0.17,null,4216,"",3,"Y"]
["South Wales","Swansea North Local 33/11kV S Stn","SwanseaNorthLocal33/11kVSStn",520360,0.3,null,500,"Y",3,"Y"]
["South Wales","Swansea Road Merthyr 33/11kV S Stn","SwanseaRoadMerthyr33/11kVSStn",550287,0.10299999999999999,null,500,"Y",3,"Y"]
["South Wales","Swansea Trading Estate 33/11kV S Stn","SwanseaTradingEstate33/11kVSStn",520274,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Swansea University 33/11kV S Stn","SwanseaUniversity33/11kVSStn",520316,1.9504999999999999,null,500,"Y",3,"Y"]
["South Wales","Swansea Waterfront 33/11kV S Stn","SwanseaWaterfront33/11kVSStn",520317,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Swansea West Grid 132/33kV S Stn","SwanseaWestGrid132/33kVSStn",520036,0.17599999999999999,null,1000,"Y",3,"Y"]
["East Midlands","Swinderby 33/11kV S Stn","Swinderby33/11kVSStn",900025,0.27200000000000002,null,266,"",3,"Y"]
["East Midlands","Swinford Windfarm 33kV S Stn","SwinfordWindfarm33kVSStn",939003,0.192,null,536,"",3,"Y"]
["East Midlands","Syston 33/11kV S Stn","Syston33/11kVSStn",920035,6.5000000000000002E-2,null,70,"",3,"Y"]
["East Midlands","Sywell PV 33kV S Stn","SywellPV33kVSStn",926308,0.193,null,122,"",3,"Y"]
["South Wales","Taff Bank 33/11kV S Stn","TaffBank33/11kVSStn",510238,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Taff Ely Wind Farm 33kV S Stn","TaffElyWindFarm33kVSStn",540295,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Talbot Green 132/11kV S Stn","TalbotGreen132/11kVSStn",540270,0.29399999999999998,null,1000,"Y",1,"Y"]
["East Midlands","Talbot Street 33/11kV S Stn","TalbotStreet33/11kVSStn",880022,0.13500000000000001,null,204,"",3,"Y"]
["West Midlands","Talke 33/11kV S Stn","Talke33/11kVSStn",850013,0.08,null,110,"",3,"Y"]
["South West","Tamar Pumping Station 33kV S Stn","TamarPumpingStation33kVSStn",330044,1.46,null,1508,"",3,"Y"]
["South West","Tamerton Bridge STOR Generator 33kV S Stn","TamertonBridgeSTORGenerator33kVSStn",338169,1.2949999999999999,null,500,"Y",3,"Y"]
["East Midlands","Tamworth 132/33kV S Stn","Tamworth132/33kVSStn",690016,4.7E-2,null,301,"",3,"Y"]
["East Midlands","Tamworth 33kV S Stn","Tamworth33kVSStn",930010,4.7E-2,null,301,"",3,"Y"]
["East Midlands","Tamworth Br 132/25kV S Stn","TamworthBr132/25kVSStn",930015,9.2999999999999999E-2,null,579,"",1,"Y"]
["West Midlands","Tamworth Br 132/25kV S Stn","TamworthBr132/25kVSStn",690009,0.2,"Y",1000,"Y",1,"Y"]
["East Midlands","Tamworth Grid 33/11kV S Stn","TamworthGrid33/11kVSStn",930071,4.7E-2,null,301,"",3,"Y"]
["East Midlands","Tamworth Town 132/11kV S Stn","TamworthTown132/11kVSStn",930070,3.4000000000000002E-2,null,217,"",1,"Y"]
["East Midlands","Tamworth Town 132/33/11kV S Stn","TamworthTown132/33/11kVSStn",690011,3.4000000000000002E-2,null,217,"",3,"Y"]
["East Midlands","Tamworth Town 33kV S Stn","TamworthTown33kVSStn",930005,3.4000000000000002E-2,null,217,"",3,"Y"]
["East Midlands","Tattenhoe 33/11kV S Stn","Tattenhoe33/11kVSStn",946268,0.13,null,420,"",3,"Y"]
["East Midlands","Tattershall 33/11kV S Stn","Tattershall33/11kVSStn",900039,0.09,null,180,"",3,"Y"]
["South West","Taunton Local 33/11kV S Stn","TauntonLocal33/11kVSStn",210010,4.7E-2,null,24,"",3,"Y"]
["South West","Taunton Main 132/33kV S Stn","TauntonMain132/33kVSStn",210612,0.08,null,3500,"",3,"Y"]
["South West","Taunton Main 400/132kV S Stn","TauntonMain400/132kVSStn",206007,0.2,"Y",3500,"",1,"Y"]
["South West","Tavistock 33/11kV S Stn","Tavistock33/11kVSStn",330011,0.53400000000000003,null,737,"",3,"Y"]
["East Midlands","Taylor Lane STOR 33kV S Stn","TaylorLaneSTOR33kVSStn",875141,2,null,522,"",3,"Y"]
["West Midlands","Tean 33/11kV S Stn","Tean33/11kVSStn",850019,0.2,null,256,"",3,"Y"]
["South West","Teignmouth Gas Works 33/11kV S Stn","TeignmouthGasWorks33/11kVSStn",340017,6.7000000000000004E-2,null,36,"",3,"Y"]
["West Midlands","Tenbury 33/11kV S Stn","Tenbury33/11kVSStn",750002,0.16400000000000001,null,379,"",3,"Y"]
["South Wales","Tenby 33/11kV S Stn","Tenby33/11kVSStn",600273,0.248,null,500,"Y",3,"Y"]
["South West","Tengore Lane Solar Park 33kV S Stn","TengoreLaneSolarPark33kVSStn",218018,0.1,null,500,"Y",3,"Y"]
["East Midlands","Teversal 33/11kV S Stn","Teversal33/11kVSStn",890029,0.105,null,205,"",3,"Y"]
["West Midlands","Tewkesbury 132/11kV S Stn","Tewkesbury132/11kVSStn",670081,5.7000000000000002E-2,null,337,"",1,"Y"]
["West Midlands","Tewkesbury 66/11kV S Stn","Tewkesbury66/11kVSStn",670083,6.4000000000000001E-2,null,532,"",3,"Y"]
["South Wales","Texaco Grid 132/11kV S Stn","TexacoGrid132/11kVSStn",600003,0.27100000000000002,null,1000,"Y",1,"Y"]
["East Midlands","The Brek Solar 33kv S Stn","TheBrekSolar33kvSStn",898460,0.14199999999999999,null,404,"",3,"Y"]
["East Midlands","The Grange Windfarm 33kV S Stn","TheGrangeWindfarm33kVSStn",917515,5.1999999999999998E-2,null,81,"",3,"Y"]
["East Midlands","The Hollies Wind Farm 33kV S Stn","TheHolliesWindFarm33kVSStn",900010,7.0000000000000007E-2,null,165,"",3,"Y"]
["East Midlands","Thenford 33/11kV S Stn","Thenford33/11kVSStn",940026,0.59,null,965,"",3,"Y"]
["East Midlands","The Ridge Solar Park 33kV S Stn","TheRidgeSolarPark33kVSStn",926142,8.6999999999999994E-2,null,235,"",3,"Y"]
["East Midlands","Thoresby 33/11kV S Stn","Thoresby33/11kVSStn",890048,0.31,null,2814,"",3,"Y"]
["East Midlands","Thoresby Solar Farm 33kV S Stn","ThoresbySolarFarm33kVSStn",898350,0.24,null,432,"",3,"Y"]
["East Midlands","Thornborough Grounds Pv 33kv S Stn","ThornboroughGroundsPv33kvSStn",946271,0.20699999999999999,null,261,"",3,"Y"]
["East Midlands","Thrapston 33/11kV S Stn","Thrapston33/11kVSStn",920059,0.22,null,420,"",3,"Y"]
["East Midlands","Thurmaston 33/11kV S Stn","Thurmaston33/11kVSStn",920034,5.6000000000000001E-2,null,110,"",3,"Y"]
["East Midlands","Thurnby 33/11kV S Stn","Thurnby33/11kVSStn",920042,5.1999999999999998E-2,null,140,"",3,"Y"]
["South Wales","Tiers Cross Solar Park 132kV S Stn","TiersCrossSolarPark132kVSStn",600364,0.26,null,1000,"Y",1,"Y"]
["South West","Till House Solar Park 33kV S Stn","TillHouseSolarPark33kVSStn",318090,0.17699999999999999,null,500,"Y",3,"Y"]
["East Midlands","Tiln Farm Solar Generation 33kV S Stn","TilnFarmSolarGeneration33kVSStn",898347,0.19,null,246,"",3,"Y"]
["West Midlands","Timberdine 132/11kV S Stn","Timberdine132/11kVSStn",670019,0.08,null,515,"",1,"Y"]
["South West","Tinkers Cross 33/11kV S Stn","TinkersCross33/11kVSStn",260440,1.593,null,1284,"",3,"Y"]
["East Midlands","Tinwell Road 33/11kV S Stn","TinwellRoad33/11kVSStn",910054,0.17299999999999999,null,268,"",3,"Y"]
["South Wales","Tir John Primary 132/33/6.6kV S Stn","TirJohnPrimary132/33/6.6kVSStn",520037,8.4000000000000005E-2,null,1000,"Y",3,"Y"]
["South Wales","Tir John STOR Generation 33kV S Stn","TirJohnSTORGeneration33kVSStn",520348,8.4000000000000005E-2,null,500,"Y",3,"Y"]
["South West","Tiverton 132/33/11kV S Stn","Tiverton132/33/11kVSStn",310002,0.187,null,257,"",3,"Y"]
["South West","Tiverton Junction 132/33/11kV S Stn","TivertonJunction132/33/11kVSStn",310032,0.187,null,257,"",3,"Y"]
["South West","Tiverton Moorhayes 33/11kV S Stn","TivertonMoorhayes33/11kVSStn",310023,0.19900000000000001,null,220,"",3,"Y"]
["South West","Tiverton South 33/11kV S Stn","TivertonSouth33/11kVSStn",310025,7.9000000000000001E-2,null,87,"",3,"Y"]
["West Midlands","Tividale 132/11kV S Stn","Tividale132/11kVSStn",670020,0.11799999999999999,null,900,"",1,"Y"]
["South West","Tonedale Farm Solar Park 33kV S Stn","TonedaleFarmSolarPark33kVSStn",218032,0.23100000000000001,null,500,"Y",3,"Y"]
["South Wales","Tonypandy 33/11kV S Stn","Tonypandy33/11kVSStn",540240,0.22,null,500,"Y",3,"Y"]
["South Wales","Tonypandy Stor 33kv Generation 33kV S Stn","TonypandyStor33kvGeneration33kVSStn",540412,3.87,null,500,"Y",3,"Y"]
["South West","Topsham 33/11kV S Stn","Topsham33/11kVSStn",310031,0.32400000000000001,null,302,"",3,"Y"]
["South West","Torpoint Antony 33/11kV S Stn","TorpointAntony33/11kVSStn",457240,1.39,null,1936,"",3,"Y"]
["South West","Torpoint Town 33/11kV S Stn","TorpointTown33/11kVSStn",457530,0.245,null,290,"",3,"Y"]
["South West","Torquay 132/33kV S Stn","Torquay132/33kVSStn",340003,0.11799999999999999,null,38,"",3,"Y"]
["East Midlands","Torrington Avenue 33/11kV S Stn","TorringtonAvenue33/11kVSStn",930030,8.4000000000000005E-2,null,219,"",3,"Y"]
["South West","Torwood 33/11kV S Stn","Torwood33/11kVSStn",340032,8.3000000000000004E-2,null,37,"",3,"Y"]
["South West","Torycombe 33/11kV S Stn","Torycombe33/11kVSStn",330028,0.32200000000000001,null,284,"",3,"Y"]
["South West","Totnes 33/11kV S Stn","Totnes33/11kVSStn",340021,0.04,null,46,"",3,"Y"]
["South West","Totnes BSP 132/33kV S Stn","TotnesBSP132/33kVSStn",340004,0.59599999999999997,null,3699,"",3,"Y"]
["East Midlands","Toton 132/33kV S Stn","Toton132/33kVSStn",680019,9.6000000000000002E-2,null,567,"",3,"Y"]
["East Midlands","Toton 33/11kV S Stn","Toton33/11kVSStn",880009,9.6000000000000002E-2,null,567,"",3,"Y"]
["East Midlands","Toton 33kV S Stn","Toton33kVSStn",880004,9.6000000000000002E-2,null,567,"",3,"Y"]
["East Midlands","Tournament Fields 33/11kV S Stn","TournamentFields33/11kVSStn",930087,0.95,null,441,"",3,"Y"]
["East Midlands","Towcester 33/11kV S Stn","Towcester33/11kVSStn",940031,6.9000000000000006E-2,null,98,"",3,"Y"]
["South West","Towerhead Farm Solar Park 33kV S Stn","TowerheadFarmSolarPark33kVSStn",188140,0.1,null,500,"Y",3,"Y"]
["West Midlands","Tower Hill Solar Farm 33kv S Stn","TowerHillSolarFarm33kvSStn",795484,0.874,null,942,"",3,"Y"]
["East Midlands","Trafalgar Park Gas Peaking S15 33kV S Stn","TrafalgarParkGasPeakingS1533kVSStn",875086,0.23,null,406,"",3,"Y"]
["South Wales","Traston Road Stor Generation 33kV S Stn","TrastonRoadStorGeneration33kVSStn",530413,0.17,null,500,"Y",3,"Y"]
["South Wales","Travellers Rest 33/11kV S Stn","TravellersRest33/11kVSStn",520041,0.32800000000000001,null,500,"Y",3,"Y"]
["South West","Trebal 33/11kV S Stn","Trebal33/11kVSStn",437720,1.7050000000000001,null,1755,"",3,"Y"]
["South Wales","Trecatti Generation 33kV S Stn","TrecattiGeneration33kVSStn",550321,0.34,null,500,"Y",3,"Y"]
["South Wales","Tredegar 33/11kV S Stn","Tredegar33/11kVSStn",550244,6.6000000000000003E-2,null,500,"Y",3,"Y"]
["South West","Trefinnick Farm Solar Farm 33kV S Stn","TrefinnickFarmSolarFarm33kVSStn",458058,0.39,null,500,"Y",3,"Y"]
["South West","Tregarrick Farm Solar Park 33kV S Stn","TregarrickFarmSolarPark33kVSStn",438088,0.7,"Y",500,"Y",3,"Y"]
["South West","Tregassow Solar Farm 33kV S Stn","TregassowSolarFarm33kVSStn",418070,0.71,null,500,"Y",3,"Y"]
["South Wales","Treguff Farm PV Generation 33kV S Stn","TreguffFarmPVGeneration33kVSStn",560361,0.35899999999999999,null,500,"Y",3,"Y"]
["South West","Trehawke Farm Solar Park 33kV S Stn","TrehawkeFarmSolarPark33kVSStn",458082,0.308,null,500,"Y",3,"Y"]
["South West","Trekenning Farm Solar Park 33kV S Stn","TrekenningFarmSolarPark33kVSStn",438040,0.39,null,500,"Y",3,"Y"]
["South West","Treningle 33kV S Stn","Treningle33kVSStn",437750,2.0699999999999998,null,1888,"",3,"Y"]
["South West","Trenouth Farm Solar Park 33kV S Stn","TrenouthFarmSolarPark33kVSStn",438010,0.8,null,735,"",3,"Y"]
["East Midlands","Trent Alloys 33/11kV S Stn","TrentAlloys33/11kVSStn",870035,0.17399999999999999,null,216,"",3,"Y"]
["East Midlands","Trent Lane 33/11kV S Stn","TrentLane33/11kVSStn",870014,0.22600000000000001,null,339,"",3,"Y"]
["South West","Trequite Solar Farm 33kV S Stn","TrequiteSolarFarm33kVSStn",458052,0.57899999999999996,null,500,"Y",3,"Y"]
["South West","Trerule Solar Park 33kV S Stn","TreruleSolarPark33kVSStn",458162,0.29699999999999999,null,500,"",3,"Y"]
["South Wales","Trethomas 33/11kV S Stn","Trethomas33/11kVSStn",540234,0.32200000000000001,null,500,"Y",3,"Y"]
["South Wales","Trevaughan 33/11kV S Stn","Trevaughan33/11kVSStn",580247,0.7,"Y",500,"Y",3,"Y"]
["South West","Trewidland Farm Solar Park 33kV S Stn","TrewidlandFarmSolarPark33kVSStn",458095,0.34799999999999998,null,500,"Y",3,"Y"]
["South West","Tricky Warren 33kV S Stn","TrickyWarren33kVSStn",218039,0.25,null,500,"Y",3,"Y"]
["South West","Tricky Warren Solar Park 33kV S Stn","TrickyWarrenSolarPark33kVSStn",218020,0.25,null,500,"Y",3,"Y"]
["South Wales","Trident Park 33kv Waste Generation 33kV S Stn","TridentPark33kvWasteGeneration33kVSStn",510447,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Trident Park Generation 33kV S Stn","TridentParkGeneration33kVSStn",510356,0.09,null,500,"Y",3,"Y"]
["South Wales","Trostre Grid 132/33kV S Stn","TrostreGrid132/33kVSStn",520038,0.14000000000000001,null,1000,"Y",3,"Y"]
["West Midlands","Troughton Farm 132kV S Stn","TroughtonFarm132kVSStn",670170,0.2,"Y",1000,"Y",1,"Y"]
["South Wales","Trowbridge 132/11kV S Stn","Trowbridge132/11kVSStn",510902,0.2,"Y",1000,"Y",1,"Y"]
["South West","Trull 33/11kV S Stn","Trull33/11kVSStn",210020,0.06,null,46,"",3,"Y"]
["South West","Truro 132/33kV S Stn","Truro132/33kVSStn",417740,0.99,null,946,"",3,"Y"]
["South West","Truro Shortlanesend 33/11kV S Stn","TruroShortlanesend33/11kVSStn",417140,3.4020000000000001,null,3742,"",3,"Y"]
["South West","Truro Treyew Road 33/11kV S Stn","TruroTreyewRoad33/11kVSStn",417600,0.224,null,343,"",3,"Y"]
["East Midlands","Trusthorpe 33/11kV S Stn","Trusthorpe33/11kVSStn",900012,0.115,null,230,"",3,"Y"]
["West Midlands","Tuffley 33/11kV S Stn","Tuffley33/11kVSStn",790002,2.5999999999999999E-2,null,54,"",3,"Y"]
["South Wales","Tumble 33/11kV S Stn","Tumble33/11kVSStn",520248,0.154,null,500,"Y",3,"Y"]
["East Midlands","Tunnel Bank 33/11kV S Stn","TunnelBank33/11kVSStn",910042,0.17,null,340,"",3,"Y"]
["East Midlands","Turweston Airfield Solar Farm 33kV S Stn","TurwestonAirfieldSolarFarm33kVSStn",945726,0.1,null,126,"",3,"Y"]
["East Midlands","Tuxford 33/11kV S Stn","Tuxford33/11kVSStn",890058,0.23400000000000001,null,185,"",3,"Y"]
["South West","Twelveheads 33/11kV S Stn","Twelveheads33/11kVSStn",417680,7.48,null,5739,"",3,"Y"]
["South West","Twerton 33/6.6kV S Stn","Twerton33/6.6kVSStn",160390,0.08,null,119,"",3,"Y"]
["East Midlands","Twin Oaks STOR 33kV S Stn","TwinOaksSTOR33kVSStn",875166,0.56999999999999995,null,816,"",3,"Y"]
["East Midlands","Twin Yards Solar Farm 33kV S Stn","TwinYardsSolarFarm33kVSStn",898482,0.23,null,283,"",3,"Y"]
["West Midlands","Union Road Generation 33kV S Stn","UnionRoadGeneration33kVSStn",735840,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Union Street 33/11kV S Stn","UnionStreet33/11kVSStn",930065,5.2999999999999999E-2,null,80,"",3,"Y"]
["South West","University Of Bath 33/11kV S Stn","UniversityOfBath33/11kVSStn",164210,0.11700000000000001,null,500,"Y",3,"Y"]
["West Midlands","University Of Birmingham 132/11kV S Stn","UniversityOfBirmingham132/11kVSStn",670035,2.9000000000000001E-2,null,275,"",1,"Y"]
["East Midlands","University Of Warwick 33/11kV S Stn","UniversityOfWarwick33/11kVSStn",930034,0.04,null,270,"",3,"Y"]
["South Wales","Uplands Swansea 33/11kV S Stn","UplandsSwansea33/11kVSStn",520250,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Upper Bank 33/11kV S Stn","UpperBank33/11kVSStn",520251,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Upper Boat 132/11kV S Stn","UpperBoat132/11kVSStn",540039,0.2,"Y",2629,"",1,"Y"]
["West Midlands","Upper Huntingford Solar Farm 33kv S Stn","UpperHuntingfordSolarFarm33kvSStn",795655,0.1,null,162,"",3,"Y"]
["West Midlands","Upper Meadowly Pv Farm 33kv S Stn","UpperMeadowlyPvFarm33kvSStn",779493,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Upper Wick Solar Farm 33kv S Stn","UpperWickSolarFarm33kvSStn",795651,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Uppingham 33/11kV S Stn","Uppingham33/11kVSStn",910057,0.24399999999999999,null,435,"",3,"Y"]
["South West","Upton Valley 33/11kV S Stn","UptonValley33/11kVSStn",340026,6.9000000000000006E-2,null,20,"",3,"Y"]
["West Midlands","Upton Warren 132/66/11kV S Stn","UptonWarren132/66/11kVSStn",670021,0.104,null,374,"",3,"Y"]
["South Wales","Usk 66/11kV S Stn","Usk66/11kVSStn",530252,0.248,null,294,null,3,"Y"]
["South Wales","Uskmouth 275/132kV S Stn","Uskmouth275/132kVSStn",530046,0.2,"Y",901,"",1,"Y"]
["East Midlands","Uttoxeter 132/33kV S Stn","Uttoxeter132/33kVSStn",680043,0.156,null,569,"",3,"Y"]
["West Midlands","Uttoxeter 132/33kV S Stn","Uttoxeter132/33kVSStn",680043,0.2,"Y",1000,"Y",3,"Y"]
["East Midlands","Uttoxeter 33kV S Stn","Uttoxeter33kVSStn",870009,0.156,null,569,"",3,"Y"]
["East Midlands","Victoria Road 33/11kV S Stn","VictoriaRoad33/11kVSStn",940044,8.3000000000000004E-2,null,125,"",3,"Y"]
["South Wales","Victoria Road 33/11kV S Stn","VictoriaRoad33/11kVSStn",560253,0.12,null,500,"Y",3,"Y"]
["East Midlands","Victoria Road PV Ellistown 33kV S Stn","VictoriaRoadPVEllistown33kVSStn",939300,7.2999999999999995E-2,null,238,"",3,"Y"]
["South West","Victoria Wind Farm 33kV S Stn","VictoriaWindFarm33kVSStn",438107,1.121,null,500,"Y",3,"Y"]
["South West","Viridor Waste To Energy 33kV S Stn","ViridorWasteToEnergy33kVSStn",118184,9.2999999999999999E-2,null,500,"Y",3,"Y"]
["East Midlands","Waddington 33/11kV S Stn","Waddington33/11kVSStn",900033,0.13300000000000001,null,219,"",3,"Y"]
["South West","Wadebridge 33/11kV S Stn","Wadebridge33/11kVSStn",437210,3.92,null,3775,"",3,"Y"]
["East Midlands","Walkers Wood Solar Farm 33kV S Stn","WalkersWoodSolarFarm33kVSStn",898357,0.35,null,581,"",3,"Y"]
["South West","Walland Farm Solar Park 33kV S Stn","WallandFarmSolarPark33kVSStn",358129,0.3,null,500,"Y",3,"Y"]
["East Midlands","Walpole 400/132kV S Stn","Walpole400/132kVSStn",690005,0.2,"Y",2800,"Y",1,"Y"]
["West Midlands","Walsall 132/33kV S Stn","Walsall132/33kVSStn",670016,0.13600000000000001,null,352,"",3,"Y"]
["East Midlands","Walsgrave 33/11kV S Stn","Walsgrave33/11kVSStn",930047,0.16,null,128,"",3,"Y"]
["East Midlands","Walton 33/11kV S Stn","Walton33/11kVSStn",890078,0.16300000000000001,null,199,"",3,"Y"]
["South West","Wansbrough Paper Mill 33kV S Stn","WansbroughPaperMill33kVSStn",210670,7.8E-2,null,105,"",3,"Y"]
["West Midlands","Wapley 33kV S Stn","Wapley33kVSStn",790003,0.27900000000000003,null,415,"",3,"Y"]
["East Midlands","Wardentree Park 33/11kV S Stn","WardentreePark33/11kVSStn",910017,0.18,null,266,"",3,"Y"]
["South West","Warleigh Barton Solar Park 33kV S Stn","WarleighBartonSolarPark33kVSStn",338028,0.63400000000000001,null,500,"Y",3,"Y"]
["West Midlands","Warndon 132/11kV S Stn","Warndon132/11kVSStn",670022,4.3999999999999997E-2,null,290,"",1,"Y"]
["East Midlands","Warsop 33/11kV S Stn","Warsop33/11kVSStn",890046,0.25600000000000001,null,536,"",3,"Y"]
["East Midlands","Warth Lane 33/11kV S Stn","WarthLane33/11kVSStn",900018,0.12,null,360,"",3,"Y"]
["East Midlands","Warwick 132/33/11kV S Stn","Warwick132/33/11kVSStn",690020,4.1000000000000002E-2,null,274,"",3,"Y"]
["East Midlands","Warwick 33kV S Stn","Warwick33kVSStn",930007,4.1000000000000002E-2,null,274,"",3,"Y"]
["East Midlands","Warwick Grid 132/11kV S Stn","WarwickGrid132/11kVSStn",690059,4.1000000000000002E-2,null,274,"",1,"Y"]
["South West","Watchfield 33/11kV S Stn","Watchfield33/11kVSStn",210150,0.09,null,263,"",3,"Y"]
["South West","Watchfield Lawn Solar Park 33kV S Stn","WatchfieldLawnSolarPark33kVSStn",218016,0.7,"Y",500,"Y",3,"Y"]
["South West","Waterlake 33/11kV S Stn","Waterlake33/11kVSStn",250330,0.15,null,220,"",3,"Y"]
["South West","Water Lane STOR Generator 33kV S Stn","WaterLaneSTORGenerator33kVSStn",318165,0.49,null,500,"Y",3,"Y"]
["South Wales","Waterston 132/11kV S Stn","Waterston132/11kVSStn",600040,0.42,null,1000,"Y",1,"Y"]
["South Wales","Waterton Industrial Primary 132/11kV S Stn","WatertonIndustrialPrimary132/11kVSStn",560292,0.16,null,1000,"Y",1,"Y"]
["East Midlands","Watford Lodge Windfarm 33kV S Stn","WatfordLodgeWindfarm33kVSStn",945977,0.13,null,250,"",3,"Y"]
["East Midlands","Watnall Primary 33/11kV S Stn","WatnallPrimary33/11kVSStn",883362,1.04,null,592,"",3,"Y"]
["South Wales","Wattstown 33/11kV S Stn","Wattstown33/11kVSStn",540255,0.35199999999999998,null,700,"",3,"Y"]
["South Wales","Waunarlwyd 33kV S Stn","Waunarlwyd33kVSStn",520145,0.39300000000000002,null,500,"Y",3,"Y"]
["South Wales","Waunarlwydd STOR Generation 33kV S Stn","WaunarlwyddSTORGeneration33kVSStn",520344,0.39300000000000002,null,500,"Y",3,"Y"]
["South Wales","Waun Y Pound Gas Stor 33kV S Stn","WaunYPoundGasStor33kVSStn",550422,1.31,null,500,"Y",3,"Y"]
["East Midlands","Wavendon Gate 33/11kV S Stn","WavendonGate33/11kVSStn",940046,0.04,null,78,"",3,"Y"]
["South Wales","Wear Point Wind Farm 33kV S Stn","WearPointWindFarm33kVSStn",600349,0.8,null,500,"Y",3,"Y"]
["South West","Wedmore 33/11kV S Stn","Wedmore33/11kVSStn",181817,0.123,null,217,"",3,"Y"]
["West Midlands","Wednesfield 132/11kV S Stn","Wednesfield132/11kVSStn",670023,0.14699999999999999,null,1102,"",1,"Y"]
["East Midlands","Weedon 33/11kV S Stn","Weedon33/11kVSStn",940050,0.10100000000000001,null,164,"",3,"Y"]
["South West","Week Farm Solar Park 33kV S Stn","WeekFarmSolarPark33kVSStn",268008,0.43,null,500,"Y",3,"Y"]
["West Midlands","Weir Hill 33/11kV S Stn","WeirHill33/11kVSStn",840022,0.22,null,493,"",3,"Y"]
["East Midlands","Welbeck Colliery Solar Generation 33kV S Stn","WelbeckCollierySolarGeneration33kVSStn",898308,0.15,null,420,"",3,"Y"]
["East Midlands","Welbeck Solar Farm 33kV S Stn","WelbeckSolarFarm33kVSStn",898344,0.41,null,712,"",3,"Y"]
["East Midlands","Weldon Shanks Generation 33kV S Stn","WeldonShanksGeneration33kVSStn",920011,0.74,null,1110,"",3,"Y"]
["East Midlands","Wellesbourne 33/11kV S Stn","Wellesbourne33/11kVSStn",939424,0.2,null,421,"",3,"Y"]
["East Midlands","Wellingborough 132/11kV S Stn","Wellingborough132/11kVSStn",920016,4.4999999999999998E-2,null,217,"",1,"Y"]
["East Midlands","Wellingborough 132/33kV S Stn","Wellingborough132/33kVSStn",690051,4.4999999999999998E-2,null,217,"",3,"Y"]
["East Midlands","Wellingborough 33kV S Stn","Wellingborough33kVSStn",940011,4.4999999999999998E-2,null,217,"",3,"Y"]
["East Midlands","Wellingborough Road 33/11kV S Stn","WellingboroughRoad33/11kVSStn",940064,0.05,null,970,"",3,"Y"]
["South West","Wellington 33/11kV S Stn","Wellington33/11kVSStn",210200,0.44,null,903,"",3,"Y"]
["East Midlands","Wellington Street 33/11kV S Stn","WellingtonStreet33/11kVSStn",870029,8.5000000000000006E-2,null,172,"",3,"Y"]
["South West","Wellington Town 33/11kV S Stn","WellingtonTown33/11kVSStn",210380,0.28799999999999998,null,166,"",3,"Y"]
["South West","Wells 33/11kV S Stn","Wells33/11kVSStn",160824,0.14799999999999999,null,129,"",3,"Y"]
["East Midlands","Welton 33/11kV S Stn","Welton33/11kVSStn",940048,0.13100000000000001,null,262,"",3,"Y"]
["South Wales","Wern 33/11kV S Stn","Wern33/11kVSStn",560256,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Wessington 33/11kV S Stn","Wessington33/11kVSStn",890087,0.219,null,350,"",3,"Y"]
["East Midlands","Westborough 33/11kV S Stn","Westborough33/11kVSStn",910037,0.29699999999999999,null,425,"",3,"Y"]
["East Midlands","West Bridgford 33/11kV S Stn","WestBridgford33/11kVSStn",880028,7.8E-2,null,118,"",3,"Y"]
["East Midlands","West Burton 400/132kV S Stn","WestBurton400/132kVSStn",890003,3.7199999999999997E-2,null,599,"",1,"Y"]
["South West","West Carclaze Solar Park 33kV S Stn","WestCarclazeSolarPark33kVSStn",438156,0.78,null,500,"Y",3,"Y"]
["South Wales","West Cross 33/11kV S Stn","WestCross33/11kVSStn",520258,0.184,null,500,"Y",3,"Y"]
["East Midlands","West Deeping 33/11kV S Stn","WestDeeping33/11kVSStn",910046,0.41499999999999998,null,872,"",3,"Y"]
["East Midlands","West End Farm Solar Generation 33kV S Stn","WestEndFarmSolarGeneration33kVSStn",898435,0.2,null,235,"",3,"Y"]
["South West","Western Approach 33/11kV S Stn","WesternApproach33/11kVSStn",114434,0.1,null,200,"",3,"Y"]
["South Wales","Western Coal 33/11kV S Stn","WesternCoal33/11kVSStn",520334,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Westfa 33/11kV S Stn","Westfa33/11kVSStn",520118,2.04,null,500,"Y",3,"Y"]
["South Wales","Westfa 33/11kV S Stn","Westfa33/11kVSStn",520259,0.10100000000000001,null,500,"Y",3,"Y"]
["South Wales","West Farm PV Generation 33kV S Stn","WestFarmPVGeneration33kVSStn",600351,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","West Haddon 33/11kV S Stn","WestHaddon33/11kVSStn",940051,0.33200000000000002,null,637,"",3,"Y"]
["South West","West Hill Solar Farm 33kV S Stn","WestHillSolarFarm33kVSStn",268002,0.66,null,500,"Y",3,"Y"]
["East Midlands","Westhorpe 33/11kV S Stn","Westhorpe33/11kVSStn",890091,6.5000000000000002E-2,null,205,"",3,"Y"]
["South West","Weston 132/33kV S Stn","Weston132/33kVSStn",182372,6.2E-2,null,174,"",3,"Y"]
["South West","Weston Central 33/11kV S Stn","WestonCentral33/11kVSStn",181360,0.30299999999999999,null,135,"",3,"Y"]
["South West","Weston-In-Gordano 33/11kV S Stn","Weston-In-Gordano33/11kVSStn",180820,0.17199999999999999,null,351,"",3,"Y"]
["South West","Weston Locking Road 33/11kV S Stn","WestonLockingRoad33/11kVSStn",180092,6.2E-2,null,128,"",3,"Y"]
["South West","Weston Mill 33/11kV S Stn","WestonMill33/11kVSStn",330012,0.14799999999999999,null,205,"",3,"Y"]
["South West","West Wick 33/11kV S Stn","WestWick33/11kVSStn",182982,0.158,null,316,"",3,"Y"]
["East Midlands","Westwood 33/11kV S Stn","Westwood33/11kVSStn",890028,0.219,null,314,"",3,"Y"]
["South Wales","W G W B Towy Intake 33kV S Stn","WGWBTowyIntake33kVSStn",590282,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Whaplode Drove 33/11kV S Stn","WhaplodeDrove33/11kVSStn",910030,0.27800000000000002,null,325,"",3,"Y"]
["South West","Whatley Quarry 33/11kV S Stn","WhatleyQuarry33/11kVSStn",160739,0.91700000000000004,null,569,"",3,"Y"]
["South West","Wheal Reeth 33/11kV S Stn","WhealReeth33/11kVSStn",417060,4.51,null,2500,"",3,"Y"]
["East Midlands","Whetstone 33/11kV S Stn","Whetstone33/11kVSStn",930096,7.1999999999999995E-2,null,142,"",3,"Y"]
["South West","Whiddon Down 33/11kV S Stn","WhiddonDown33/11kVSStn",350021,2.2200000000000002,null,1725,"",3,"Y"]
["South West","Whitchurch 33/11kV S Stn","Whitchurch33/11kVSStn",112272,4.2000000000000003E-2,null,13,"",3,"Y"]
["South West","Whitchurch Farm Solar Park 33kV S Stn","WhitchurchFarmSolarPark33kVSStn",168000,0.20300000000000001,null,500,"Y",3,"Y"]
["East Midlands","Whitecross Lane Solar Park Burton Pedwardine 33kV S Stn","WhitecrossLaneSolarParkBurtonPedwardine33kVSStn",906124,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Whitfield 132/33/11kV S Stn","Whitfield132/33/11kVSStn",680050,0.14000000000000001,null,1249,"",3,"Y"]
["West Midlands","Whitfield 132kV S Stn","Whitfield132kVSStn",680046,0.14499999999999999,null,1767,"",1,"Y"]
["South Wales","Whitland 33/11kV S Stn","Whitland33/11kVSStn",580262,0.75,null,500,"Y",3,"Y"]
["South Wales","Whitland Solar Park 33kV S Stn","WhitlandSolarPark33kVSStn",580337,0.152,null,500,"Y",3,"Y"]
["East Midlands","Whitley 132/33kV S Stn","Whitley132/33kVSStn",930016,7.0000000000000007E-2,null,357,"",3,"Y"]
["East Midlands","Whitley 33/11kV S Stn","Whitley33/11kVSStn",930045,7.0000000000000007E-2,null,357,"",3,"Y"]
["East Midlands","Whitley 33kV S Stn","Whitley33kVSStn",930008,7.0000000000000007E-2,null,574,"",3,"Y"]
["South West","Whitley Farm Solar Farm 33kV S Stn","WhitleyFarmSolarFarm33kVSStn",218075,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Whittlebury Road PV 33kV S Stn","WhittleburyRoadPV33kVSStn",946060,6.3E-2,null,56,"",3,"Y"]
["East Midlands","Whittleford 33/11kV S Stn","Whittleford33/11kVSStn",930074,8.2000000000000003E-2,null,162,"",3,"Y"]
["South Wales","Whitton Mawr Solar Park 33kV S Stn","WhittonMawrSolarPark33kVSStn",510428,0.20599999999999999,null,405,"",3,"Y"]
["East Midlands","Whitwell 132/33kV S Stn","Whitwell132/33kVSStn",680016,0.42699999999999999,null,1320,"",3,"Y"]
["East Midlands","Whitwell 33kV S Stn","Whitwell33kVSStn",890009,0.42699999999999999,null,1320,"",3,"Y"]
["East Midlands","Wicken 33/11kV S Stn","Wicken33/11kVSStn",940033,0.45,null,878,"",3,"Y"]
["South West","Wick Farm Solar Park 33kV S Stn","WickFarmSolarPark33kVSStn",188150,7.0000000000000007E-2,null,500,"Y",3,"Y"]
["South West","Wick Farm West Solar Park 33kV S Stn","WickFarmWestSolarPark33kVSStn",188168,0.11,null,500,"Y",3,"Y"]
["West Midlands","Wickhamford 66kv S Stn","Wickhamford66kvSStn",670152,0.124,null,214,"",3,"Y"]
["East Midlands","Wide Lane Wymeswold Solar Farm 33kV S Stn","WideLaneWymeswoldSolarFarm33kVSStn",926300,7.2999999999999995E-2,null,164,"",3,"Y"]
["East Midlands","Wigston 132/11kV S Stn","Wigston132/11kVSStn",920039,6.0999999999999999E-2,null,393,"",1,"Y"]
["East Midlands","Wigston 132/33/11kV S Stn","Wigston132/33/11kVSStn",690027,0.2,"Y",393,"",3,"Y"]
["East Midlands","Wigston 33kV S Stn","Wigston33kVSStn",920005,6.0999999999999999E-2,null,393,"",3,"Y"]
["East Midlands","Wigston Magna 33/11kV S Stn","WigstonMagna33/11kVSStn",920017,7.9000000000000001E-2,null,34,"",3,"Y"]
["West Midlands","Willenhall 275/132/33/25/11kV S Stn","Willenhall275/132/33/25/11kVSStn",670006,7.0000000000000007E-2,null,211,"",3,"Y"]
["East Midlands","Willesley 33/11kV S Stn","Willesley33/11kVSStn",690060,0.23200000000000001,null,220,"",3,"Y"]
["East Midlands","Willington 400/275/132kV S Stn","Willington400/275/132kVSStn",680006,0.2,"Y",2800,"Y",1,"Y"]
["East Midlands","Willoughby 132/33kV S Stn","Willoughby132/33kVSStn",680014,7.9000000000000001E-2,null,329,"",3,"Y"]
["East Midlands","Willoughby 33/11kV S Stn","Willoughby33/11kVSStn",880032,7.9000000000000001E-2,null,329,"",3,"Y"]
["East Midlands","Willoughby 33kV S Stn","Willoughby33kVSStn",880006,7.9000000000000001E-2,null,329,"",3,"Y"]
["East Midlands","Willoughby STOR 33kV S Stn","WilloughbySTOR33kVSStn",883330,7.9000000000000001E-2,null,500,"Y",3,"Y"]
["South West","Willsland Solar Park 33kV S Stn","WillslandSolarPark33kVSStn",358067,0.7,"Y",500,"Y",3,"Y"]
["South West","Wilton 33kV S Stn","Wilton33kVSStn",458145,0.95299999999999996,null,500,"Y",3,"Y"]
["South West","Wilton Farm Solar Park 33kV S Stn","WiltonFarmSolarPark33kVSStn",458142,1.0369999999999999,null,500,"Y",3,"Y"]
["South West","Wilton Farm Wind Farm 33kV S Stn","WiltonFarmWindFarm33kVSStn",458147,1.01,null,500,"Y",3,"Y"]
["East Midlands","Wingerworth 33/11kV S Stn","Wingerworth33/11kVSStn",890072,4.2999999999999997E-2,null,117,"",3,"Y"]
["South West","Winnards Perch Solar Farm 33kV S Stn","WinnardsPerchSolarFarm33kVSStn",438038,0.38,null,500,"Y",3,"Y"]
["South West","Winscombe 33/11kV S Stn","Winscombe33/11kVSStn",180952,0.21199999999999999,null,428,"",3,"Y"]
["South West","Winslakefoot 33kV S Stn","Winslakefoot33kVSStn",310047,0.55000000000000004,null,553,"",3,"Y"]
["East Midlands","Winslow 33/11kV S Stn","Winslow33/11kVSStn",940035,8.3000000000000004E-2,null,160,"",3,"Y"]
["West Midlands","Winson Green 132/11kV S Stn","WinsonGreen132/11kVSStn",670038,0.05,null,279,"",1,"Y"]
["East Midlands","Winster 132/33kV S Stn","Winster132/33kVSStn",680040,0.2,"Y",565,"",3,"Y"]
["East Midlands","Winster 33kV S Stn","Winster33kVSStn",890013,0.17899999999999999,null,565,"",3,"Y"]
["South West","Winterbourne 33/11kV S Stn","Winterbourne33/11kVSStn",112130,0.30099999999999999,null,474,"",3,"Y"]
["South West","Winterbourne Abbas 33kV S Stn","WinterbourneAbbas33kVSStn",200433,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Winwick Windfarm 33kV S Stn","WinwickWindfarm33kVSStn",945978,0.13,null,145,"",3,"Y"]
["East Midlands","Wise Street 33/11kV S Stn","WiseStreet33/11kVSStn",930054,0.05,null,73,"",3,"Y"]
["West Midlands","Witches Solar Park 66kV S Stn","WitchesSolarPark66kVSStn",756593,0.21,null,340,"",3,"Y"]
["South West","Witheridge 33/11kV S Stn","Witheridge33/11kVSStn",310011,3.806,null,3342,"",3,"Y"]
["South West","Withycombe Raleigh 33/11kV S Stn","WithycombeRaleigh33/11kVSStn",310037,4.4999999999999998E-2,null,14,"",3,"Y"]
["South West","Withy Drove Solar Park 33kV S Stn","WithyDroveSolarPark33kVSStn",218040,6.3E-2,null,500,"Y",3,"Y"]
["South Wales","Withyhedges 33kV S Stn","Withyhedges33kVSStn",600323,0.27,null,500,"Y",3,"Y"]
["East Midlands","Wittering 33/11kV S Stn","Wittering33/11kVSStn",910053,0.08,null,98,"",3,"Y"]
["South West","Wiveliscombe 33/11kV S Stn","Wiveliscombe33/11kVSStn",210070,2.06,null,2616,"",3,"Y"]
["East Midlands","Wollaton Road 33/11kV S Stn","WollatonRoad33/11kVSStn",880020,6.5000000000000002E-2,null,130,"",3,"Y"]
["West Midlands","Wolverhampton 132/33/11kV S Stn","Wolverhampton132/33/11kVSStn",670024,0.114,null,376,"",3,"Y"]
["West Midlands","Wolverhampton Power 33kv S Stn","WolverhamptonPower33kvSStn",736099,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Wolverhampton Waste Services 33kv S Stn","WolverhamptonWasteServices33kvSStn",670150,0.7,"Y",500,"Y",3,"Y"]
["West Midlands","Wolverhampton West 132/33/11kV S Stn","WolverhamptonWest132/33/11kVSStn",670025,0.13300000000000001,null,1157,"",3,"Y"]
["East Midlands","Wolverton 132/25kV S Stn","Wolverton132/25kVSStn",940015,0.2,"Y",1000,"Y",1,"Y"]
["East Midlands","Wolverton 33/11kV S Stn","Wolverton33/11kVSStn",940036,6.8000000000000005E-2,null,351,"",3,"Y"]
["East Midlands","Woodbeck 33/11kV S Stn","Woodbeck33/11kVSStn",890062,0.499,null,528,"",3,"Y"]
["South West","Woodbury 33/11kV S Stn","Woodbury33/11kVSStn",310035,0.74,null,842,"",3,"Y"]
["South West","Woodcote 132/33kV S Stn","Woodcote132/33kVSStn",250437,0.17699999999999999,null,283,"",3,"Y"]
["East Midlands","Wood End 33/11kV S Stn","WoodEnd33/11kVSStn",930073,0.16500000000000001,null,383,"",3,"Y"]
["East Midlands","Woodford Halse 33/11kV S Stn","WoodfordHalse33/11kVSStn",940027,8.5999999999999993E-2,null,157,"",3,"Y"]
["East Midlands","Woodhall Spa 33/11kV S Stn","WoodhallSpa33/11kVSStn",900038,0.219,null,799,"",3,"Y"]
["South West","Woodland Barton Solar Park 33kV S Stn","WoodlandBartonSolarPark33kVSStn",438024,0.71,null,500,"Y",3,"Y"]
["South West","Woodland Way 33/11kV S Stn","WoodlandWay33/11kVSStn",110375,8.7999999999999995E-2,null,151,"",3,"Y"]
["East Midlands","Wood Lane 33/11kV S Stn","WoodLane33/11kVSStn",939062,0.2,null,226,"",3,"Y"]
["West Midlands","Woodside 132/11kV S Stn","Woodside132/11kVSStn",670026,7.0999999999999994E-2,null,333,"",1,"Y"]
["South Wales","Wood Street 33/11kV S Stn","WoodStreet33/11kVSStn",510310,0.61,null,500,"Y",3,"Y"]
["East Midlands","Woodville 33/11kV S Stn","Woodville33/11kVSStn",870037,0.28199999999999997,null,333,"",3,"Y"]
["West Midlands","Woofferton 66/11kV S Stn","Woofferton66/11kVSStn",670110,0.14000000000000001,null,211,"",3,"Y"]
["South West","Woolavington Solar Park 33kV S Stn","WoolavingtonSolarPark33kVSStn",218005,4.2999999999999997E-2,null,500,"Y",3,"Y"]
["East Midlands","Wootton 33/11kV S Stn","Wootton33/11kVSStn",940062,0.14000000000000001,null,140,"",3,"Y"]
["West Midlands","Worcester 132/11kV S Stn","Worcester132/11kVSStn",670014,9.5000000000000001E-2,null,486,"",1,"Y"]
["West Midlands","Worfield 33/11kV S Stn","Worfield33/11kVSStn",840003,0.36,null,490,"",3,"Y"]
["East Midlands","Worksop 132/33kV S Stn","Worksop132/33kVSStn",680017,0.14399999999999999,null,586,"",3,"Y"]
["East Midlands","Worksop 33kV S Stn","Worksop33kVSStn",890011,0.14399999999999999,null,586,"",3,"Y"]
["East Midlands","Worksop West 33/11kV S Stn","WorksopWest33/11kVSStn",890038,0.157,null,308,"",3,"Y"]
["West Midlands","Wormington 66/11kV S Stn","Wormington66/11kVSStn",670092,0.7,"Y",500,"Y",3,"Y"]
["East Midlands","Worthington 33/11kV S Stn","Worthington33/11kVSStn",930104,0.253,null,314,"",3,"Y"]
["East Midlands","Wragby 33/11kV S Stn","Wragby33/11kVSStn",900036,6.7000000000000004E-2,null,122,"",3,"Y"]
["East Midlands","Wrangle 33/11kV S Stn","Wrangle33/11kVSStn",900019,0.17299999999999999,null,322,"",3,"Y"]
["West Midlands","Wribbenhall 33/11kV S Stn","Wribbenhall33/11kVSStn",770001,0.26,null,338,"",3,"Y"]
["West Midlands","Wrockwardine Farm 33kV S Stn","WrockwardineFarm33kVSStn",841517,0.14000000000000001,null,275,"",3,"Y"]
["West Midlands","Wyelands 33kV S Stn","Wyelands33kVSStn",790019,0.42599999999999999,null,443,"",3,"Y"]
["South West","Wyld Meadow Solar Park 33kV S Stn","WyldMeadowSolarPark33kVSStn",258023,0.15,null,500,"Y",3,"Y"]
["East Midlands","Wymeswold Airfield PV Farm 33kV S Stn","WymeswoldAirfieldPVFarm33kVSStn",926096,0.1,null,148,"",3,"Y"]
["East Midlands","Wymington Wykes Generation 33kV S Stn","WymingtonWykesGeneration33kVSStn",920010,4.8000000000000001E-2,null,78,"",3,"Y"]
["East Midlands","Yelvertoft Windfarm 33kV S Stn","YelvertoftWindfarm33kVSStn",946091,0.2,null,135,"",3,"Y"]
["South West","Yelverton 33/11kV S Stn","Yelverton33/11kVSStn",330016,0.42699999999999999,null,445,"",3,"Y"]
["South West","Yeovil 33kV S Stn","Yeovil33kVSStn",200435,0.7,"Y",500,"Y",3,"Y"]
["South Wales","Yerbeston Chapel Hill Solar Farm 33kV S Stn","YerbestonChapelHillSolarFarm33kVSStn",600385,0.39,null,500,"Y",3,"Y"]
["South Wales","Yerbeston Solar Farm 33kV S Stn","YerbestonSolarFarm33kVSStn",600370,0.252,null,500,"Y",3,"Y"]
["South Wales","Ynysfeio 33/11kV S Stn","Ynysfeio33/11kVSStn",540263,0.20399999999999999,null,500,"Y",3,"Y"]
["South Wales","Ynys Street 33/11kV S Stn","YnysStreet33/11kVSStn",560265,0.106,null,500,"Y",3,"Y"]
["South West","Yonder Netherton 33kV Solar Farm 33/11kV S Stn","YonderNetherton33kVSolarFarm33/11kVSStn",458053,0.7,"Y",500,"Y",3,"Y"]
["South West","Yonder Parks Solar Park 33kV S Stn","YonderParksSolarPark33kVSStn",348111,0.86,null,500,"Y",3,"Y"]
["West Midlands","Yorkley Solar Farm 33kV S Stn","YorkleySolarFarm33kVSStn",795731,0.19,null,402,"",3,"Y"]

{"sheet":"Source-SWE-Num","index":14,"n_rows":602,"n_cols":8,"rows_kept":602,"cut":false,"hidden":true,"merged":[]}
[1,2,3,4,5,6,7,8]
["SUBSTATION_NUMBER_SWE","SUBSTATION_NAME","ZE","Assumed ZE","UE","Assumed UE","t","Assumed t"]
[104098,"Norrington 132/33kV S Stn",0.2,"Y",1400,"Y",3,"Y"]
[106009,"Iron Acton 275/132kV S Stn",0.2,"Y",1486,"",1,"Y"]
[106010,"Melksham 400/275/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
[110375,"Woodland Way 33/11kV S Stn",8.7999999999999995E-2,null,151,"",3,"Y"]
[110641,"Bedminster 33/11kV S Stn",0.12,null,348,"",3,"Y"]
[110644,"Eastville 33/11kV S Stn",0.10199999999999999,null,500,"Y",3,"Y"]
[110772,"Lockleaze 33/11kV S Stn",5.7000000000000002E-2,null,21,"",3,"Y"]
[110803,"Cairns Road 33/11kV S Stn",0.09,null,207,"",3,"Y"]
[110804,"St Pauls BSP 132/11kV S Stn",0.06,null,43,"",3,"Y"]
[111158,"Clifton 33/11kV S Stn",0.12,null,251,"",3,"Y"]
[111481,"Keynsham East 33/11kV S Stn",0.108,null,130,"",3,"Y"]
[111800,"Mangotsfield 33/11kV S Stn",9.2999999999999999E-2,null,23,"",3,"Y"]
[111935,"Almondsbury 33/11kV S Stn",0.121,null,143,"",3,"Y"]
[112130,"Winterbourne 33/11kV S Stn",0.30099999999999999,null,474,"",3,"Y"]
[112272,"Whitchurch 33/11kV S Stn",4.2000000000000003E-2,null,13,"",3,"Y"]
[112389,"Stoke Bishop 33/11kV S Stn",0.12,null,500,"Y",3,"Y"]
[113180,"Keynsham West 33/11kV S Stn",0.108,null,170,"",3,"Y"]
[113193,"Bishopsworth 33/11kV S Stn",0.12,null,198,"",3,"Y"]
[113277,"Avonmouth Docks 33/6.6kV S Stn",0.08,null,119,"",3,"Y"]
[113339,"Kingsweston 33/11kV S Stn",0.11,null,206,"",3,"Y"]
[113367,"Avonmouth BSP 132/33kV S Stn",1.4999999999999999E-2,null,92,"",3,"Y"]
[113368,"Avonmouth 33/11kV S Stn",7.0000000000000007E-2,null,109,"",3,"Y"]
[113369,"Filton Dc 33/11kV S Stn",0.13,null,201,"",3,"Y"]
[113370,"Lockleaze 132/33/11kV S Stn",5.7000000000000002E-2,null,184,"",3,"Y"]
[113371,"Bower Ashton 33/11kV S Stn",0.12,null,186,"",3,"Y"]
[113372,"Feeder Road 33kV S Stn",0.05,null,79,"",3,"Y"]
[113373,"Feeder Road A 33/11kV S Stn",0.05,null,140,"",3,"Y"]
[113374,"Feeder Road B 33/11kV S Stn",0.05,null,140,"",3,"Y"]
[113429,"British Gas Hallen 33/11kV S Stn",7.0999999999999994E-2,null,110,"",3,"Y"]
[113449,"Feeder Road 132/33kV S Stn",0.05,null,251,"",3,"Y"]
[113450,"St Pauls 132/11kV S Stn",0.06,null,314,"",1,"Y"]
[113572,"Bradley Stoke 132/33kV S Stn",0.21,null,1024,"",3,"Y"]
[113720,"Hewlett Packard 33/11kV S Stn",6.3E-2,null,28,"",3,"Y"]
[113760,"Bradley Stoke 33/11kV S Stn",0.21,null,500,"Y",3,"Y"]
[113884,"Abbeywood 33/11kV S Stn",0.77900000000000003,null,265,"",3,"Y"]
[113983,"Cribbs Causeway 33/11kV S Stn",7.6999999999999999E-2,null,32,"",3,"Y"]
[114023,"Seabank 400/132kV S Stn",8.5999999999999993E-2,null,1274,"",1,"Y"]
[114059,"Rolls Royce Filton 132kV S Stn",0.13300000000000001,null,291,"",1,"Y"]
[114258,"Astrazeneca 33/11kV S Stn",0.47,null,348,"",3,"Y"]
[114259,"Seabank 132/33kV S Stn",8.5999999999999993E-2,null,695,"",3,"Y"]
[114260,"Broadweir 33/11kV S Stn",0.06,null,13.5,"",3,"Y"]
[114389,"Cotham 33/11kV S Stn",0.16500000000000001,null,81,"",3,"Y"]
[114391,"Emersons Green 33/11kV S Stn",0.33,null,144,"",3,"Y"]
[114393,"Staplehill 33kV S Stn",0.43,null,132,"",3,"Y"]
[114434,"Western Approach 33/11kV S Stn",0.1,null,200,"",3,"Y"]
[114632,"Hewlett Packard 33kV S Stn",6.3E-2,null,500,"Y",3,"Y"]
[114652,"Avonmouth Biogas 33kV S Stn",0.183,null,500,"Y",3,"Y"]
[114741,"Patchway 33/11kV S Stn",0.62,null,500,"Y",3,"Y"]
[114756,"Severnside Energy Recovery Centre 132kV S Stn",0.125,null,1400,"Y",1,"Y"]
[118093,"Avonmouth Wind Farm 33kV S Stn",8.5000000000000006E-2,null,500,"Y",3,"Y"]
[118115,"Northwood Solar Park 33kV S Stn",0.14000000000000001,null,500,"Y",3,"Y"]
[118117,"Marksbury Solar Park 33kV S Stn",9.6000000000000002E-2,null,500,"Y",3,"Y"]
[118154,"Chelwood Solar Park 33kV S Stn",0.125,null,500,"Y",3,"Y"]
[118157,"Oakham Farm Solar Park 33kV S Stn",0.14399999999999999,null,500,"Y",3,"Y"]
[118166,"Lawrence Weston Solar Park 33kV S Stn",0.186,null,278.8,"",3,"Y"]
[118179,"Lockleaze Battery Storage 33kV S Stn",0.69,null,500,"Y",3,"Y"]
[118180,"Old Green Generation Station 132kV S Stn",0.114,null,1400,"Y",1,"Y"]
[118183,"Rockingham 33kV S Stn",0.23,null,500,"Y",3,"Y"]
[118184,"Viridor Waste To Energy 33kV S Stn",9.2999999999999999E-2,null,500,"Y",3,"Y"]
[160050,"Oldfield Park33/ 6.6kV S Stn",0.26100000000000001,null,86,"",3,"Y"]
[160060,"Park Street 33/6.6kV S Stn",3.1E-2,null,21,"",3,"Y"]
[160355,"Entry Hill 33/6.6kV S Stn",6.5000000000000002E-2,null,88,"",3,"Y"]
[160389,"Batheaston 33/6.6kV S Stn",4.3999999999999997E-2,null,59,"",3,"Y"]
[160390,"Twerton 33/6.6kV S Stn",0.08,null,119,"",3,"Y"]
[160415,"Chewton Mendip 33/11kV S Stn",2,null,2670,"",3,"Y"]
[160423,"Midsomer Norton 33/11kV S Stn",0.05,null,82,"",3,"Y"]
[160739,"Whatley Quarry 33/11kV S Stn",0.91700000000000004,null,569,"",3,"Y"]
[160811,"Dinder 33/11kV S Stn",4.2699999999999996,null,4582,"",3,"Y"]
[160824,"Wells 33/11kV S Stn",0.14799999999999999,null,129,"",3,"Y"]
[161315,"Paulton 33/11kV S Stn",0.19700000000000001,null,127,"",3,"Y"]
[161532,"High Littleton 33/11kV S Stn",0.24,null,401,"",3,"Y"]
[161641,"Shepton Mallet 33/11kV S Stn",0.192,null,251,"",3,"Y"]
[161701,"Newbury 33/11kV S Stn",0.97099999999999997,null,1035,"",3,"Y"]
[161823,"Evercreech 33/11kV S Stn",0.129,null,103,"",3,"Y"]
[162344,"Foxhills 33/11kV S Stn",0.16200000000000001,null,226,"",3,"Y"]
[162406,"Peasedown 33/11kV S Stn",0.10199999999999999,null,113,"",3,"Y"]
[162633,"Radstock 132/33kV S Stn",0.25700000000000001,null,247,"",3,"Y"]
[162888,"Shooters Bottom W/F 33kV S Stn",1.2,null,1464,"",3,"Y"]
[164016,"Combe Park 33/6.6kV S Stn",7.5999999999999998E-2,null,96,"",3,"Y"]
[164087,"Bath Dolemeads 132/33/6.6kV S Stn",7.1999999999999995E-2,null,68,"",3,"Y"]
[164170,"Dorchester Street 33/6.6kV S Stn",7.1999999999999995E-2,null,105,"",3,"Y"]
[164210,"University Of Bath 33/11kV S Stn",0.11700000000000001,null,500,"Y",3,"Y"]
[168000,"Whitchurch Farm Solar Park 33kV S Stn",0.20300000000000001,null,500,"Y",3,"Y"]
[168001,"Shooters Bottom Solar Park 33kV S Stn",0.90400000000000003,null,500,"Y",3,"Y"]
[168104,"New Row Farm Solar Park 33kV S Stn",0.66600000000000004,null,500,"Y",3,"Y"]
[168105,"Pitts Farm Solar Park 33kV S Stn",0.65600000000000003,null,500,"Y",3,"Y"]
[168106,"Dinder Farm Solar Park 33kV S Stn",0.65600000000000003,null,500,"Y",3,"Y"]
[168138,"Pylle Solar Park 33kV S Stn",0.17699999999999999,null,500,"Y",3,"Y"]
[180003,"Gas Lane 33/11kV S Stn",3.7999999999999999E-2,null,36,"",3,"Y"]
[180006,"Congresbury 33/11kV S Stn",0.153,null,325,"",3,"Y"]
[180017,"Axbridge 33/11kV S Stn",0.19,null,281,"",3,"Y"]
[180092,"Weston Locking Road 33/11kV S Stn",6.2E-2,null,128,"",3,"Y"]
[180173,"Blagdon 33/11kV S Stn",0.11799999999999999,null,160,"",3,"Y"]
[180198,"Clevedon 33/11kV S Stn",0.26200000000000001,null,275,"",3,"Y"]
[180471,"Bournville 33/11kV S Stn",7.9000000000000001E-2,null,141,"",3,"Y"]
[180820,"Weston-In-Gordano 33/11kV S Stn",0.17199999999999999,null,351,"",3,"Y"]
[180952,"Winscombe 33/11kV S Stn",0.21199999999999999,null,428,"",3,"Y"]
[181000,"Nailsea 33/11kV S Stn",0.23499999999999999,null,404,"",3,"Y"]
[181216,"Lypstone Farm 33/11kV S Stn",6.2E-2,null,143,"",3,"Y"]
[181230,"Chew Stoke 33/11kV S Stn",0.40200000000000002,null,339,"",3,"Y"]
[181345,"Cheddar 33/11kV S Stn",8.2000000000000003E-2,null,128,"",3,"Y"]
[181346,"Compton Martin 33/11kV S Stn",0.46899999999999997,null,935,"",3,"Y"]
[181360,"Weston Central 33/11kV S Stn",0.30299999999999999,null,135,"",3,"Y"]
[181414,"Easton-In-Gordano 33/11kV S Stn",0.189,null,417,"",3,"Y"]
[181425,"East Brent 33/11kV S Stn",0.158,null,144,"",3,"Y"]
[181817,"Wedmore 33/11kV S Stn",0.123,null,217,"",3,"Y"]
[182000,"Frys Hill Radio 33kV/LV S Stn",0.7,"Y",500,"Y",3,"Y"]
[182150,"Royal Portbury Dock 33/11kV S Stn",5.0999999999999997E-2,null,20,"",3,"Y"]
[182332,"Brent Knoll 33kV S Stn",0.191,null,154,"",3,"Y"]
[182372,"Weston 132/33kV S Stn",6.2E-2,null,174,"",3,"Y"]
[182373,"Churchill 132/33kV S Stn",0.18,null,271,"",3,"Y"]
[182570,"Churchill Gate 33/11kV S Stn",0.55000000000000004,null,853,"",3,"Y"]
[182736,"Bristol International Airport 33/11kV S Stn",0.28299999999999997,null,406,"",3,"Y"]
[182768,"Stancombe Quarry 33kV S Stn",1.0840000000000001,null,1444,"",3,"Y"]
[182800,"Portishead 132/33kV S Stn",5.8999999999999997E-2,null,118,"",3,"Y"]
[182982,"West Wick 33/11kV S Stn",0.158,null,316,"",3,"Y"]
[182983,"Portishead Ashlands 33/11kV S Stn",5.8999999999999997E-2,null,423,"",3,"Y"]
[188112,"Carditch Drove Solar Park 33kV S Stn",0.1,null,500,"Y",3,"Y"]
[188122,"Iwood Lane Solar Park 33kV S Stn",8.5000000000000006E-2,null,500,"Y",3,"Y"]
[188123,"Ashlawn Farm Solar Park 33kV S Stn",8.5000000000000006E-2,null,500,"Y",3,"Y"]
[188124,"Hawkers Farm Solar Park 33kV S Stn",0.109,null,500,"Y",3,"Y"]
[188139,"Rookery Farm Solar Park 33kV S Stn",0.254,null,500,"Y",3,"Y"]
[188140,"Towerhead Farm Solar Park 33kV S Stn",0.1,null,500,"Y",3,"Y"]
[188150,"Wick Farm Solar Park 33kV S Stn",7.0000000000000007E-2,null,500,"Y",3,"Y"]
[188168,"Wick Farm West Solar Park 33kV S Stn",0.11,null,500,"Y",3,"Y"]
[200433,"Winterbourne Abbas 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[200435,"Yeovil 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[206001,"Alverdiscott 400/132kV S Stn",0.2,"Y",2028,"",1,"Y"]
[206006,"Axminster GSP 400/132kV S Stn",0.2,"Y",2096,"",1,"Y"]
[206007,"Taunton Main 400/132kV S Stn",0.2,"Y",3500,"",1,"Y"]
[206008,"Bridgwater GSP 275/132kV S Stn",5.6000000000000001E-2,null,820,"",1,"Y"]
[210010,"Taunton Local 33/11kV S Stn",4.7E-2,null,24,"",3,"Y"]
[210020,"Trull 33/11kV S Stn",0.06,null,46,"",3,"Y"]
[210030,"Creech St Michael 33/11kV S Stn",0.30399999999999999,null,333,"",3,"Y"]
[210040,"Priorswood 33/11kV S Stn",7.4999999999999997E-2,null,112,"",3,"Y"]
[210050,"Lydeard St Lawrence 33/11kV S Stn",0.86799999999999999,null,1075,"",3,"Y"]
[210060,"Bridgwater Local 33/11kV S Stn",9.0999999999999998E-2,null,358,"",3,"Y"]
[210070,"Wiveliscombe 33/11kV S Stn",2.06,null,2616,"",3,"Y"]
[210080,"Somerton 33/11kV S Stn",0.06,null,69,"",3,"Y"]
[210090,"North Street Langport 33/11kV S Stn",0.1,null,169,"",3,"Y"]
[210100,"Millfield 33/11kV S Stn",0.189,null,275,"",3,"Y"]
[210110,"Edgarley 33/11kV S Stn",0.14799999999999999,null,194,"",3,"Y"]
[210120,"Colley Lane 33/11kV S Stn",8.2000000000000003E-2,null,295,"",3,"Y"]
[210130,"Nether Stowey 33/11kV S Stn",0.443,null,269,"",3,"Y"]
[210140,"Exebridge 33/11kV S Stn",1.25,null,689,"",3,"Y"]
[210150,"Watchfield 33/11kV S Stn",0.09,null,263,"",3,"Y"]
[210160,"Bath Road 33/11kV S Stn",0.06,null,90,"",3,"Y"]
[210180,"Periton 33/11kV S Stn",0.255,null,172,"",3,"Y"]
[210190,"Alcombe 33/11kV S Stn",0.107,null,103,"",3,"Y"]
[210200,"Wellington 33/11kV S Stn",0.44,null,903,"",3,"Y"]
[210210,"Bowhays Cross 132/33kV S Stn",0.192,null,396,"",3,"Y"]
[210210,"Bowhays Cross 33/11kV S Stn",0.192,null,396,"",3,"Y"]
[210260,"Bradon Fm Generator 33kV S Stn",7.6999999999999999E-2,null,54,"",3,"Y"]
[210270,"Huntworth Generator 33kV S Stn",0.219,null,494.9,"",3,"Y"]
[210380,"Wellington Town 33/11kV S Stn",0.28799999999999998,null,166,"",3,"Y"]
[210390,"Culmhead 33/11kV S Stn",0.79300000000000004,null,948,"",3,"Y"]
[210444,"Bridgwater Grid 132/33kV S Stn",6.0999999999999999E-2,null,431,"",3,"Y"]
[210448,"Street 132/33kV S Stn",0.28000000000000003,null,580,"",3,"Y"]
[210450,"Curry Mallet 33/11kV S Stn",0.78800000000000003,null,871,"",3,"Y"]
[210460,"Shapwick 33/11kV S Stn",0.61399999999999999,null,1166,"",3,"Y"]
[210470,"Burnham 33/11kV S Stn",4.2999999999999997E-2,null,54,"",3,"Y"]
[210490,"Luckwell Bridge 33/11kV S Stn",4.79,null,2476,"",3,"Y"]
[210500,"Staplegrove 33/11kV S Stn",0.14799999999999999,null,183,"",3,"Y"]
[210540,"Quartley 33kV S Stn",3.95,null,2386,"",3,"Y"]
[210560,"Holford 33/11kV S Stn",1.7,null,430,"",3,"Y"]
[210600,"Blackditch 33kV S Stn",0.123,null,369,"",3,"Y"]
[210612,"Taunton Main 132/33kV S Stn",0.08,null,3500,"",3,"Y"]
[210670,"Wansbrough Paper Mill 33kV S Stn",7.8E-2,null,105,"",3,"Y"]
[210999,"R.O.F. Power House 33kV S Stn",6.2E-2,null,93,"",3,"Y"]
[218000,"New Rendy Farm Solar Farm 33kV S Stn",0.11600000000000001,null,500,"Y",3,"Y"]
[218002,"Park Wall Solar Park 33kV S Stn",9.4E-2,null,500,"Y",3,"Y"]
[218004,"Grange Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[218005,"Woolavington Solar Park 33kV S Stn",4.2999999999999997E-2,null,500,"Y",3,"Y"]
[218009,"Culmhead Solar Park 33kV S Stn",0.13700000000000001,null,500,"Y",3,"Y"]
[218016,"Watchfield Lawn Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[218017,"Redlands Farm Solar Park 33kV S Stn",0.13,null,500,"Y",3,"Y"]
[218018,"Tengore Lane Solar Park 33kV S Stn",0.1,null,500,"Y",3,"Y"]
[218019,"Somerton Door Solar Park 33kV S Stn",7.8E-2,null,500,"Y",3,"Y"]
[218020,"Tricky Warren Solar Park 33kV S Stn",0.25,null,500,"Y",3,"Y"]
[218021,"Higher Bye Farm Solar Park 33kV S Stn",6.5000000000000002E-2,null,500,"Y",3,"Y"]
[218025,"Puriton Landfill Solar Park 33kV S Stn",0.115,null,500,"Y",3,"Y"]
[218032,"Tonedale Farm Solar Park 33kV S Stn",0.23100000000000001,null,500,"Y",3,"Y"]
[218039,"Tricky Warren 33kV S Stn",0.25,null,500,"Y",3,"Y"]
[218040,"Withy Drove Solar Park 33kV S Stn",6.3E-2,null,500,"Y",3,"Y"]
[218041,"Montys Farm Solar Park 33kV S Stn",0.19700000000000001,null,500,"Y",3,"Y"]
[218043,"Halse Solar Farm 33kV S Stn",0.09,null,112,null,3,"Y"]
[218044,"Glebe Farm 2 Solar Farm 33kV S Stn",0.69,null,578,null,3,"Y"]
[218045,"Hele Manor STOR 33kV S Stn",0.26500000000000001,null,133,"",3,"Y"]
[218061,"Cobbs Cross Solar Farm 33kV S Stn",0.157,null,500,"Y",3,"Y"]
[218071,"Aller Court Solar Farm 33kV S Stn",0.17,null,500,"Y",3,"Y"]
[218075,"Whitley Farm Solar Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[250280,"Axminster 33/11kV S Stn",0.11600000000000001,null,196,"",3,"Y"]
[250290,"East Chinnock 33/11kV S Stn",0.29599999999999999,null,413,"",3,"Y"]
[250300,"Martock 33/11kV S Stn",0.33600000000000002,null,265,"",3,"Y"]
[250310,"Colyford 33/11kV S Stn",0.60899999999999999,null,605,"",3,"Y"]
[250320,"Penn Cross 33/11kV S Stn",0.29199999999999998,null,455,"",3,"Y"]
[250330,"Waterlake 33/11kV S Stn",0.15,null,220,"",3,"Y"]
[250340,"Bridport 33/11kV S Stn",5.8000000000000003E-2,null,56,"",3,"Y"]
[250350,"Dowlish Ford 33/11kV S Stn",0.16,null,202,"",3,"Y"]
[250360,"Chard 33/11kV S Stn",2.9000000000000001E-2,null,39,"",3,"Y"]
[250370,"Crewkerne 33/11kV S Stn",8.8999999999999996E-2,null,307,"",3,"Y"]
[250400,"Montacute 33/11kV S Stn",0.42799999999999999,null,537,"",3,"Y"]
[250437,"Woodcote 132/33kV S Stn",0.17699999999999999,null,283,"",3,"Y"]
[250530,"Coker 33/11kV S Stn",1.1120000000000001,null,1672,"",3,"Y"]
[250620,"Beaminster 33/11kV S Stn",0.439,null,358,"",3,"Y"]
[258019,"Beechgrove Farm Solar Park 33kV S Stn",0.16700000000000001,null,274,"",3,"Y"]
[258023,"Wyld Meadow Solar Park 33kV S Stn",0.15,null,500,"Y",3,"Y"]
[258062,"Newlands Farm Solar Park 33kV S Stn",0.23,null,500,"Y",3,"Y"]
[258063,"Cricket St Thomas Solar Park 33kV S Stn",0.13600000000000001,null,500,"Y",3,"Y"]
[258065,"Parsonage Barn Solar Park 33kV S Stn",0.16,null,500,"Y",3,"Y"]
[258073,"Stonebarrow Farm Solar Farm 33kV S Stn",0.151,null,500,"Y",3,"Y"]
[258083,"Higher Berechapel Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[258127,"Hurcott Solar Park 33kV S Stn",8.4000000000000005E-2,null,500,"Y",3,"Y"]
[258130,"Hurcott 33kV S Stn",0.55000000000000004,null,500,"Y",3,"Y"]
[258153,"Crewkerne Solar Park 33kV S Stn",0.13800000000000001,null,500,"Y",3,"Y"]
[258174,"Axe View Solar Farm 33kV S Stn",3.1E-2,null,500,"Y",3,"Y"]
[260006,"Fullabrook Windfarm 132kV S Stn",0.4,null,580,"",1,"Y"]
[260180,"Darracott Moor Windfarm 33kV S Stn",0.82,null,792,"",3,"Y"]
[260220,"Braunton 33/11kV S Stn",0.372,null,463,"",3,"Y"]
[260230,"Ilfracombe 33/11kV S Stn",0.36899999999999999,null,349,"",3,"Y"]
[260240,"Roundswell 33/11kV S Stn",0.14000000000000001,null,133,"",3,"Y"]
[260250,"Barnstaple Quay 33/11kV S Stn",0.1,null,115,"",3,"Y"]
[260260,"South Molton 33/11kV S Stn",1.1100000000000001,null,1095,"",3,"Y"]
[260270,"Great Torrington 33/11kV S Stn",0.28999999999999998,null,234,"",3,"Y"]
[260410,"Lynton 33/11kV S Stn",4.5,null,2133,"",3,"Y"]
[260420,"Middle Barlington 33/11kV S Stn",2.4500000000000002,null,1581,"",3,"Y"]
[260430,"Heddon Cross 33/11kV S Stn",1.68,null,1054,"",3,"Y"]
[260440,"Tinkers Cross 33/11kV S Stn",1.593,null,1284,"",3,"Y"]
[260465,"East Yelland 132/33kV S Stn",0.22,null,263,"",3,"Y"]
[260467,"Barnstaple 132/33/11kV S Stn",6.2E-2,null,93,"",3,"Y"]
[260480,"Fremington 33/11kV S Stn",1.7090000000000001,null,2616,"",3,"Y"]
[260550,"Bratton Fleming 33/11kV S Stn",3.82,null,2475,"",3,"Y"]
[260570,"Georgeham 33/11kV S Stn",3.23,null,2061,"",3,"Y"]
[260580,"Aaronsons 33kV S Stn",0.32,null,322,"",3,"Y"]
[260590,"Rock Park 132/33/11kV S Stn",6.2E-2,null,116,"",3,"Y"]
[268000,"Bratton Fleming Solar Park 33kV S Stn",0.81,null,500,"Y",3,"Y"]
[268001,"Knockworthy Farm Solar Park 33kV S Stn",0.57999999999999996,null,500,"Y",3,"Y"]
[268002,"West Hill Solar Farm 33kV S Stn",0.66,null,500,"Y",3,"Y"]
[268004,"Horsacott Solar Farm 33kV S Stn",0.17,null,500,"Y",3,"Y"]
[268005,"Beaford Solar Farm 33kV S Stn",0.375,null,500,"Y",3,"Y"]
[268007,"Kingsland Barton Solar Park 33kV S Stn",0.29199999999999998,null,500,"Y",3,"Y"]
[268008,"Week Farm Solar Park 33kV S Stn",0.43,null,500,"Y",3,"Y"]
[268078,"Luscott Barton Solar Farm 33kV S Stn",0.46899999999999997,null,500,"Y",3,"Y"]
[268081,"Bommerton Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[268091,"Cleave Farm Solar Park 33kV S Stn",0.29199999999999998,null,500,"Y",3,"Y"]
[268113,"Capelands Farm Solar Park 33kV S Stn",0.86,null,500,"Y",3,"Y"]
[268136,"Bommertown Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[306004,"Abham 400/132kV S Stn",0.2,"Y",6635,"",1,"Y"]
[306005,"Exeter Main 400/132kV S Stn",0.115,null,1648,"",1,"Y"]
[310001,"Exeter City 132/33kV S Stn",0.1,null,467,"",3,"Y"]
[310002,"Tiverton 132/33/11kV S Stn",0.187,null,257,"",3,"Y"]
[310003,"Exeter Main 33kV S Stn",0.15,null,1648,"",3,"Y"]
[310004,"Exmouth 132/33kV S Stn",7.5999999999999998E-2,null,323,"",3,"Y"]
[310005,"Sowton 132/33/11kV S Stn",0.1,null,643,"",3,"Y"]
[310006,"Marsh Barton Power Station 132kV S Stn",0.10170999999999999,null,612.70000000000005,"",1,"Y"]
[310007,"North Tawton 132/33kV S Stn",0.20399999999999999,null,255,"",3,"Y"]
[310011,"Witheridge 33/11kV S Stn",3.806,null,3342,"",3,"Y"]
[310012,"Newton St Cyres 33/11kV S Stn",0.72699999999999998,null,1246,"",3,"Y"]
[310013,"Lapford 33/11kV S Stn",0.73099999999999998,null,681,"",3,"Y"]
[310014,"Cowley Road 33/11kV S Stn",6.4000000000000001E-2,null,77,"",3,"Y"]
[310015,"Crediton 33/11kV S Stn",0.11700000000000001,null,120,"",3,"Y"]
[310016,"Folly Bridge 33/11kV S Stn",0.621,null,631,"",3,"Y"]
[310017,"St Thomas 33/11kV S Stn",3.4000000000000002E-2,null,11,"",3,"Y"]
[310018,"Bridge Mills 33/11kV S Stn",0.21,null,201,"",3,"Y"]
[310020,"Athelstan Road 33/11kV S Stn",0.2,null,261,"",3,"Y"]
[310022,"Marsh Barton 33/11kV S Stn",0.7,"Y",87,"",3,"Y"]
[310023,"Tiverton Moorhayes 33/11kV S Stn",0.19900000000000001,null,220,"",3,"Y"]
[310024,"Cullompton 33/11kV S Stn",0.27100000000000002,null,298,"",3,"Y"]
[310025,"Tiverton South 33/11kV S Stn",7.9000000000000001E-2,null,87,"",3,"Y"]
[310026,"Pinhoe 33/11kV S Stn",5.0999999999999997E-2,null,31,"",3,"Y"]
[310028,"Sowton 33/11kV S Stn",0.1,null,20,"",3,"Y"]
[310029,"Heavitree 33/11kV S Stn",0.26,null,323,"",3,"Y"]
[310030,"Exminster 33/11kV S Stn",0.16400000000000001,null,187,"",3,"Y"]
[310031,"Topsham 33/11kV S Stn",0.32400000000000001,null,302,"",3,"Y"]
[310032,"Tiverton Junction 132/33/11kV S Stn",0.187,null,257,"",3,"Y"]
[310033,"Burlescombe 33/11kV S Stn",0.52300000000000002,null,1029,"",3,"Y"]
[310034,"Clyst Honiton 33/11kV S Stn",0.5,null,565,"",3,"Y"]
[310035,"Woodbury 33/11kV S Stn",0.74,null,842,"",3,"Y"]
[310036,"Marsh Green 33/11kV S Stn",0.82799999999999996,null,800,"",3,"Y"]
[310037,"Withycombe Raleigh 33/11kV S Stn",4.4999999999999998E-2,null,14,"",3,"Y"]
[310038,"Exmouth Works 33/11kV S Stn",0.11,null,151,"",3,"Y"]
[310039,"Budleigh Salterton 33/11kV S Stn",9.9000000000000005E-2,null,118,"",3,"Y"]
[310040,"East Budleigh 33/11kV S Stn",2.5,null,2390,"",3,"Y"]
[310041,"Offwell 33/11kV S Stn",1.2410000000000001,null,1452,"",3,"Y"]
[310042,"Honiton Heathfield 33/11kV S Stn",0.21099999999999999,null,180,"",3,"Y"]
[310043,"Ottery St Mary 33/11kV S Stn",0.442,null,487,"",3,"Y"]
[310044,"Core Hill 33/11kV S Stn",0.17799999999999999,null,160,"",3,"Y"]
[310045,"Newton Poppleford 33/11kV S Stn",0.34,null,284,"",3,"Y"]
[310046,"Sidmouth Town 33/11kV S Stn",0.124,null,110,"",3,"Y"]
[310047,"Winslakefoot 33kV S Stn",0.55000000000000004,null,553,"",3,"Y"]
[310048,"Countess Wear 33/11kV S Stn",0.124,null,35,"",3,"Y"]
[310049,"Haven Road 33/11kV S Stn",0.19,null,253,"",3,"Y"]
[310056,"Hemyock 33/11kV S Stn",0.60699999999999998,null,715,"",3,"Y"]
[310057,"Dunkeswell 33/11kV S Stn",0.29099999999999998,null,203,"",3,"Y"]
[310058,"North Tawton 33/11kV S Stn",0.20399999999999999,null,105,"",3,"Y"]
[310059,"Sowton B 33/11kV S Stn",0.1,null,500,"Y",3,"Y"]
[310060,"Exeter Science Park 33/11kV S Stn",0.32,null,500,"Y",3,"Y"]
[310061,"Hill Barton Primary 33/11kV S Stn",0.16900000000000001,null,500,"Y",3,"Y"]
[318026,"Burrowton Farm Solar Park 33kV S Stn",0.16,null,500,"Y",3,"Y"]
[318031,"Fulford Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[318032,"Nether Mill Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[318035,"Ayshford Court Farm Solar Park 33kV S Stn",0.17499999999999999,null,500,"Y",3,"Y"]
[318090,"Till House Solar Park 33kV S Stn",0.17699999999999999,null,500,"Y",3,"Y"]
[318098,"Cullompton Solar Park 33kV S Stn",0.2,null,500,"Y",3,"Y"]
[318110,"Liverton Farm Solar Park 33kV S Stn",0.245,null,500,"Y",3,"Y"]
[318118,"Francis Court Farm Solar Park 33kV S Stn",0.41499999999999998,null,500,"Y",3,"Y"]
[318137,"Bystock Farm Solar Park 33kV S Stn",0.185,null,500,"Y",3,"Y"]
[318146,"Coombe Farm Solar Park 33kV S Stn",0.25,null,500,"Y",3,"Y"]
[318152,"Batsworthy Cross Wind Farm 33kV S Stn",0.49,null,500,"Y",3,"Y"]
[318155,"Red Hill Solar Park 33kV S Stn",0.27100000000000002,null,500,"Y",3,"Y"]
[318161,"Makro Exeter STOR Generator 33kV S Stn",0.34499999999999997,null,500,"Y",3,"Y"]
[318164,"Great Houndbeare Farm Solar Park 33kV S Stn",0.22900000000000001,null,500,"Y",3,"Y"]
[318165,"Water Lane STOR Generator 33kV S Stn",0.49,null,500,"Y",3,"Y"]
[318172,"Sharland Farm Solar Park 33kV S Stn",0.219,null,500,"Y",3,"Y"]
[318173,"Stoneshill Solar Park 33kV S Stn",0.19600000000000001,null,500,"Y",3,"Y"]
[330001,"Ernesettle 132/33kV S Stn",0.153,null,1232,"",3,"Y"]
[330002,"Milehouse 132/33kV S Stn",0.11700000000000001,null,303,"",3,"Y"]
[330003,"Plymouth 132/33kV S Stn",8.5999999999999993E-2,null,43,"",3,"Y"]
[330006,"Plympton 132/33kV S Stn",0.67900000000000005,null,764,"",3,"Y"]
[330011,"Tavistock 33/11kV S Stn",0.53400000000000003,null,737,"",3,"Y"]
[330012,"Weston Mill 33/11kV S Stn",0.14799999999999999,null,205,"",3,"Y"]
[330013,"St Levan Road 33/11kV S Stn",8.7999999999999995E-2,null,130,"",3,"Y"]
[330014,"Adelaide Road 33/11kV S Stn",0.47,null,85,"",3,"Y"]
[330015,"Newport Street 33/11kV S Stn",0.55300000000000005,null,147,"",3,"Y"]
[330016,"Yelverton 33/11kV S Stn",0.42699999999999999,null,445,"",3,"Y"]
[330017,"Merrivale 33/11kV S Stn",0.153,null,214,"",3,"Y"]
[330018,"Alexandra Road 33/11kV S Stn",0.36,null,113,"",3,"Y"]
[330019,"Elim Terrace 33/11kV S Stn",0.16,null,281,"",3,"Y"]
[330020,"Alma Road 33/11kV S Stn",0.16500000000000001,null,244,"",3,"Y"]
[330021,"Armada Street 33/11kV S Stn",0.27,null,113,"",3,"Y"]
[330022,"Buckwell Street 33/11kV S Stn",0.57999999999999996,null,229,"",3,"Y"]
[330023,"Southway 33/11kV S Stn",0.245,null,70,"",3,"Y"]
[330024,"Longbridge 33/11kV S Stn",0.20899999999999999,null,341,"",3,"Y"]
[330025,"Eggbuckland 33/11kV S Stn",7.1999999999999995E-2,null,24,"",3,"Y"]
[330026,"Old Laira Road 33/11kV S Stn",0.65200000000000002,null,266,"",3,"Y"]
[330027,"Prince Rock 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[330028,"Torycombe 33/11kV S Stn",0.32200000000000001,null,284,"",3,"Y"]
[330029,"Linketty Lane 33/11kV S Stn",0.161,null,162,"",3,"Y"]
[330030,"Ivybridge 33/11kV S Stn",0.20200000000000001,null,245,"",3,"Y"]
[330031,"Stentaway 33/11kV S Stn",8.6999999999999994E-2,null,73,"",3,"Y"]
[330032,"Newton Ferrers 33/11kV S Stn",0.46,null,457,"",3,"Y"]
[330037,"Plymstock South 33/11kV S Stn",0.157,null,229,"",3,"Y"]
[330038,"Ernesettle B & S 33/11kV S Stn",0.153,null,216,"",3,"Y"]
[330039,"North Intake 33kV S Stn",0.22,null,297,"",3,"Y"]
[330040,"Lifton 33/11kV S Stn",0.09,null,58,"",3,"Y"]
[330041,"Central Intake 33kV S Stn",0.3,null,421,"",3,"Y"]
[330042,"Langage 33/11kV S Stn",0.121,null,157,"",3,"Y"]
[330044,"Tamar Pumping Station 33kV S Stn",1.46,null,1508,"",3,"Y"]
[330045,"Plymouth BSP 33kV S Stn",8.5999999999999993E-2,null,43,"",3,"Y"]
[330046,"Chelson Generator 33kV S Stn",0.24,null,326,"",3,"Y"]
[330047,"Langage Energy Centre 33kV S Stn",0.61699999999999999,null,5577,null,3,"Y"]
[333718,"Faraday Road STOR Generator 33kV S Stn",0.124,null,500,"Y",3,"Y"]
[333743,"Ernesettle Lane STOR Generator 33kV S Stn",0.156,null,1171,"",3,"Y"]
[333760,"Hemerdon Mine 33/11kV S Stn",0.53,null,500,"Y",3,"Y"]
[338028,"Warleigh Barton Solar Park 33kV S Stn",0.63400000000000001,null,500,"Y",3,"Y"]
[338120,"Balls Wood Solar Park 33kV S Stn",0.28899999999999998,null,500,"Y",3,"Y"]
[338133,"Newnham Farm Solar Park 33kV S Stn",0.56000000000000005,null,500,"Y",3,"Y"]
[338151,"Portworthy Dams Solar Park 33kV S Stn",0.31,null,500,"Y",3,"Y"]
[338169,"Tamerton Bridge STOR Generator 33kV S Stn",1.2949999999999999,null,500,"Y",3,"Y"]
[338177,"Cattledown STOR Generator 33kV S Stn",0.124,null,500,"Y",3,"Y"]
[338181,"Sherford IDNO Connection 33kV S Stn",0.51800000000000002,null,500,"Y",3,"Y"]
[338185,"Marlands Fields Creacombe Solar Park 33kV S Stn",0.48399999999999999,null,483,"",3,"Y"]
[338190,"Newton Downs Solar Park 33kV S Stn",0.46,null,457,"",3,"Y"]
[340001,"Newton Abbot 132/33/11kV S Stn",0.11,null,405,"",3,"Y"]
[340002,"Paignton 132/33kV S Stn",0.42799999999999999,null,823,"",3,"Y"]
[340003,"Torquay 132/33kV S Stn",0.11799999999999999,null,38,"",3,"Y"]
[340004,"Totnes BSP 132/33kV S Stn",0.59599999999999997,null,3699,"",3,"Y"]
[340011,"Chudleigh Knighton 33/11kV S Stn",0.24199999999999999,null,222,"",3,"Y"]
[340012,"Mortonhampstead 33/11kV S Stn",0.20899999999999999,null,116,"",3,"Y"]
[340013,"Ashburton 33/11kV S Stn",0.34,null,481,"",3,"Y"]
[340014,"Buckfastleigh 33/11kV S Stn",0.55700000000000005,null,495,"",3,"Y"]
[340015,"South Brent 33/11kV S Stn",0.5,null,671,"",3,"Y"]
[340016,"Kingsbridge 33/11kV S Stn",0.18,null,118,"",3,"Y"]
[340017,"Teignmouth Gas Works 33/11kV S Stn",6.7000000000000004E-2,null,36,"",3,"Y"]
[340018,"Higher Woodway 33/11kV S Stn",0.16800000000000001,null,198,"",3,"Y"]
[340019,"Newton Abbot Main 33/11kV S Stn",8.5000000000000006E-2,null,23,"",3,"Y"]
[340020,"Bradley Lane 33/11kV S Stn",8.3000000000000004E-2,null,78,"",3,"Y"]
[340021,"Totnes 33/11kV S Stn",0.04,null,46,"",3,"Y"]
[340022,"Blackawton 33/11kV S Stn",1.3859999999999999,null,1249,"",3,"Y"]
[340023,"Dawlish 33/11kV S Stn",0.14299999999999999,null,125,"",3,"Y"]
[340024,"Barton 33/11kV S Stn",0.58099999999999996,null,109,"",3,"Y"]
[340025,"Lawes Bridge 33/11kV S Stn",0.26,null,384,"",3,"Y"]
[340026,"Upton Valley 33/11kV S Stn",6.9000000000000006E-2,null,20,"",3,"Y"]
[340027,"Marldon 33/11kV S Stn",0.14899999999999999,null,119,"",3,"Y"]
[340029,"Churston 33/11kV S Stn",0.621,null,384,"",3,"Y"]
[340030,"Dartmouth 33/11kV S Stn",0.39300000000000002,null,381,"",3,"Y"]
[340032,"Torwood 33/11kV S Stn",8.3000000000000004E-2,null,37,"",3,"Y"]
[340033,"Hollicombe 33/11kV S Stn",0.08,null,23,"",3,"Y"]
[340034,"Colley End 33/11kV S Stn",0.18,null,214,"",3,"Y"]
[340035,"Laywell Brixham 33/11kV S Stn",0.39500000000000002,null,499,"",3,"Y"]
[340038,"Salcombe 33/11kV S Stn",0.20100000000000001,null,270,"",3,"Y"]
[340039,"Bovey Tracey 33/11kV S Stn",0.19700000000000001,null,215,"",3,"Y"]
[340040,"Modbury 33/11kV S Stn",0.21299999999999999,null,218,"",3,"Y"]
[340041,"Stokenham 33/11kV S Stn",0.45500000000000002,null,348,"",3,"Y"]
[340042,"Paignton 33/11kV S Stn",0.42799999999999999,null,823,"",3,"Y"]
[340043,"Heathfield Landfill 33kV S Stn",0.28999999999999998,null,341,"",3,"Y"]
[341542,"Laywell 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[348027,"Marley Thatch Farm Solar Park 33kV S Stn",0.76200000000000001,null,500,"Y",3,"Y"]
[348033,"Slade Farm Solar Park 33kV S Stn",0.498,null,500,"Y",3,"Y"]
[348045,"Hatchlands Farm Solar Park 33kV S Stn",0.4,null,500,"Y",3,"Y"]
[348077,"Hazard Farm Solar Park 33kV S Stn",0.496,null,500,"Y",3,"Y"]
[348103,"Bidwell Solar Park 33kV S Stn",0.29799999999999999,null,500,"Y",3,"Y"]
[348111,"Yonder Parks Solar Park 33kV S Stn",0.86,null,500,"Y",3,"Y"]
[348121,"Rydon Farm Solar Park 33kV S Stn",8.5999999999999993E-2,null,500,"Y",3,"Y"]
[348131,"Coombeshead Farm Solar Park 33kV S Stn",0.56000000000000005,null,500,"Y",3,"Y"]
[348132,"Ashcombe Solar Park 33kV S Stn",6.6000000000000003E-2,null,500,"Y",3,"Y"]
[348134,"Parkview Solar Park 33kV S Stn",0.63,null,500,"Y",3,"Y"]
[348175,"Old Stone Farm Solar Park 33kV S Stn",1.3019229999999999,null,500,"Y",3,"Y"]
[348176,"Place Barton Farm Solar Park 33kV S Stn",0.89551000000000003,null,500,"Y",3,"Y"]
[348178,"Barton Hill STOR Generator 33kV S Stn",0.41,null,500,"Y",3,"Y"]
[348182,"Alders Way STOR 33kV S Stn",0.42799999999999999,null,500,"Y",3,"Y"]
[350001,"Pyworthy 132/33kV S Stn",0.57199999999999995,null,904,"",3,"Y"]
[350011,"Clovelly 33/11kV S Stn",2.1,null,1338,"",3,"Y"]
[350012,"Stratton 33/11kV S Stn",0.36699999999999999,null,595,"",3,"Y"]
[350013,"Shebbear 33/11kV S Stn",2.5,null,1853,"",3,"Y"]
[350014,"Holsworthy 33/11kV S Stn",0.251,null,402,"",3,"Y"]
[350015,"East Curry 33/11kV S Stn",0.93100000000000005,null,865,"",3,"Y"]
[350016,"Northam 33/11kV S Stn",0.11600000000000001,null,126,"",3,"Y"]
[350017,"Park Lane 33/11kV S Stn",7.3999999999999996E-2,null,83,"",3,"Y"]
[350018,"Bideford Main 33/11kV S Stn",0.104,null,115,"",3,"Y"]
[350019,"Hatherleigh 33/11kV S Stn",0.155,null,177,"",3,"Y"]
[350021,"Whiddon Down 33/11kV S Stn",2.2200000000000002,null,1725,"",3,"Y"]
[350022,"Ashwater 33/11kV S Stn",2.8330000000000002,null,3043,"",3,"Y"]
[350023,"Roadford 33kV S Stn",0.41,null,406,"",3,"Y"]
[350024,"Morwenstow 33/11kV S Stn",2.09,null,2036,"",3,"Y"]
[350025,"Forestmoor 33/11kV S Stn",0.72,null,715,"",3,"Y"]
[350050,"Okehampton 33/11kV S Stn",0.23,null,216,"",3,"Y"]
[357295,"Galsworthy Wind Farm 132kV S Stn",0.54,null,1400,"Y",1,"Y"]
[357304,"Carnworthy Solar Park 132kV S Stn",1.254,null,1400,"Y",1,"Y"]
[358017,"East Langford Solar Park 33kV S Stn",0.28999999999999998,null,402,"",3,"Y"]
[358022,"Eastacombe Solar Farm 33kV S Stn",0.33500000000000002,null,500,"Y",3,"Y"]
[358050,"Lower Tinacre Solar Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[358056,"Higher North Beer Farm Solar Park 33kV S Stn",0.20699999999999999,null,500,"Y",3,"Y"]
[358057,"Bradford Manor Solar Farm 33kV S Stn",0.34,null,500,"Y",3,"Y"]
[358064,"Rexon Cross Farm Solar Park 33kV S Stn",0.45800000000000002,null,500,"Y",3,"Y"]
[358067,"Willsland Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[358068,"Crinacott Farm Solar Park 33kV S Stn",0.14000000000000001,null,500,"Y",3,"Y"]
[358074,"Pitworthy Solar Park 33kV S Stn",0.33700000000000002,null,500,"Y",3,"Y"]
[358076,"Foxcombe Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[358079,"Alverdiscott Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[358080,"Derriton Fields Solar Park 33kV S Stn",0.28499999999999998,null,500,"Y",3,"Y"]
[358085,"Chalhanger Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[358114,"East Youlstone Windfarm 33kV S Stn",0.7,null,500,"Y",3,"Y"]
[358116,"Northmoor Solar Park 132kV S Stn",0.92,null,1400,"Y",1,"Y"]
[358129,"Walland Farm Solar Park 33kV S Stn",0.3,null,500,"Y",3,"Y"]
[358159,"Denbrook Wind Farm 33kV S Stn",0.16600000000000001,null,500,"Y",3,"Y"]
[358160,"Ashwater Solar Park 33kV S Stn",0.5,null,500,"Y",3,"Y"]
[358167,"Dunsland Cross Wind Farm 33kV S Stn",0.29799999999999999,null,500,"Y",3,"Y"]
[406002,"Indian Queens 400/132kV S Stn",0.2,"Y",3070,"",1,"Y"]
[406003,"Landulph GSP 400/132kV S Stn",0.43,null,3182,"",1,"Y"]
[407020,"Camborne 132/33kV S Stn",0.23200000000000001,null,512,"",3,"Y"]
[407150,"Hayle 132/33kV S Stn",9.5000000000000001E-2,null,112,"",3,"Y"]
[407380,"Fraddon 132/33kV S Stn",0.27400000000000002,null,2392,"",3,"Y"]
[407450,"St Tudy 132/33kV S Stn",1.069,null,1110,"",3,"Y"]
[415927,"Goonhilly Wind Farm 33kV S Stn",0.52,null,388,"",3,"Y"]
[417010,"Camborne Treswithian 33/11kV S Stn",2.2789999999999999,null,3519,"",3,"Y"]
[417020,"Camborne Carn Brea 33/11kV S Stn",0.216,null,177,"",3,"Y"]
[417030,"Lanner 33/11kV S Stn",8.4740000000000002,null,4813,"",3,"Y"]
[417040,"Geevor 33/11kV S Stn",3.4,null,2309,"",3,"Y"]
[417050,"Helston 33/11kV S Stn",0.25900000000000001,null,336,"",3,"Y"]
[417060,"Wheal Reeth 33/11kV S Stn",4.51,null,2500,"",3,"Y"]
[417070,"Marazion 33/11kV S Stn",1.347,null,1611,"",3,"Y"]
[417080,"Penzance Heamoor 33/11kV S Stn",0.32300000000000001,null,627,"",3,"Y"]
[417090,"St Buryan 33/11kV S Stn",6.9039999999999999,null,4163,"",3,"Y"]
[417100,"Perranporth 33/11kV S Stn",4.29,null,3693,"",3,"Y"]
[417110,"Redruth 33/11kV S Stn",0.42599999999999999,null,849,"",3,"Y"]
[417120,"Roseland 33/11kV S Stn",3.1789999999999998,null,2241,"",3,"Y"]
[417130,"St Ives 33/11kV S Stn",3.37,null,5220,"",3,"Y"]
[417140,"Truro Shortlanesend 33/11kV S Stn",3.4020000000000001,null,3742,"",3,"Y"]
[417150,"Hayle 33/11kV S Stn",9.5000000000000001E-2,null,131,"",3,"Y"]
[417160,"Falmouth Bickland Hill 33/11kV S Stn",0.186,null,275,"",3,"Y"]
[417170,"Penryn 33/11kV S Stn",0.99399999999999999,null,1552,"",3,"Y"]
[417180,"Falmouth Docks 33/11kV S Stn",0.13400000000000001,null,182,"",3,"Y"]
[417310,"Devoran 33/11kV S Stn",2.1150000000000002,null,2563,"",3,"Y"]
[417320,"Constantine 33/11kV S Stn",3.8519999999999999,null,4898,"",3,"Y"]
[417330,"St Keverne 33/11kV S Stn",4.3120000000000003,null,4271,"",3,"Y"]
[417340,"Mousehole 33/11kV S Stn",3.3639999999999999,null,2301,"",3,"Y"]
[417500,"Rame132/33kV S Stn",1.7230000000000001,null,2340,"",3,"Y"]
[417540,"Camborne Holmans 33/11kV S Stn",0.23699999999999999,null,390,"",3,"Y"]
[417560,"Probus 33/11kV S Stn",2.69,null,1783,"",3,"Y"]
[417580,"Penzance Causewayhead 33/11kV S Stn",0.112,null,149,"",3,"Y"]
[417590,"St Agnes 33/11kV S Stn",4.59,null,2528,"",3,"Y"]
[417600,"Truro Treyew Road 33/11kV S Stn",0.224,null,343,"",3,"Y"]
[417670,"St Day Landfill 33kV S Stn",0.63,null,419,"",3,"Y"]
[417680,"Twelveheads 33/11kV S Stn",7.48,null,5739,"",3,"Y"]
[417690,"Newlyn 33/11kV S Stn",0.55100000000000005,null,1160,"",3,"Y"]
[417740,"Truro 132/33kV S Stn",0.99,null,946,"",3,"Y"]
[417760,"Isles Of Scilly 33/11kV S Stn",0.52400000000000002,null,214,"",3,"Y"]
[417780,"Mullion 33/11kV S Stn",0.443,null,338,"",3,"Y"]
[417800,"Carland Cross Wind Farm 33kV S Stn",0.52,null,1435,"",3,"Y"]
[417820,"Four Burrows Windfarm 33kV S Stn",0.38200000000000001,null,845,"",3,"Y"]
[418008,"Churchtown Farm Solar Park 33kV S Stn",0.37,null,262,"",3,"Y"]
[418009,"Chynoweth Solar Park 33kV S Stn",0.38,null,821,null,3,"Y"]
[418029,"Hope Solar Park 33kV S Stn",0.432,null,500,"Y",3,"Y"]
[418034,"Higher Trenhayle Farm Solar Park 33kV S Stn",0.93300000000000005,null,500,"Y",3,"Y"]
[418041,"Fourburrows Pendown 33kV S Stn",0.48,null,500,"Y",3,"Y"]
[418046,"Causilgey Solar Farm 33kV S Stn",1.1100000000000001,null,500,"Y",3,"Y"]
[418049,"Higher Tregarne Solar Farm 33kV S Stn",1.04,null,500,"Y",3,"Y"]
[418060,"Little Trevease Farm Solar Farm 33kV S Stn",1.79,null,500,"Y",3,"Y"]
[418069,"Penare Farm Solar Farm 33kV S Stn",0.41,null,500,"Y",3,"Y"]
[418070,"Tregassow Solar Farm 33kV S Stn",0.71,null,500,"Y",3,"Y"]
[418096,"Gover Park Solar Park 33kV S Stn",0.54900000000000004,null,500,"Y",3,"Y"]
[418101,"Nanteague Solar Park 33kV S Stn",0.75,null,500,"Y",3,"Y"]
[418102,"Goonhilly Solar Park 33kV S Stn",0.36,null,500,"Y",3,"Y"]
[418108,"Four Burrows Blackdown Solar Park 33kV S Stn",0.878,null,500,"Y",3,"Y"]
[418125,"Pencoose Solar Park 33kV S Stn",1.26,null,500,"Y",3,"Y"]
[418126,"Garvinack Farm Solar Park 33kV S Stn",0.7,null,500,"Y",3,"Y"]
[418135,"Roskrow Barton Solar Park 33kV S Stn",0.7,null,500,"Y",3,"Y"]
[418141,"Burthy Solar Park 33kV S Stn",0.46,null,500,"Y",3,"Y"]
[418158,"Carnemough Farm Solar Park 33kV S Stn",0.56100000000000005,null,500,"Y",3,"Y"]
[418163,"Nancrossa Solar Park 33kV S Stn",1.9279999999999999,null,500,"Y",3,"Y"]
[437150,"Bears Down Wind Farm 33kV S Stn",0.55000000000000004,null,282,"",3,"Y"]
[437190,"St Austell  33/11kV S Stn",0.77,null,1482,"",3,"Y"]
[437200,"St Blazey 33kV S Stn",0.443,null,678,"",3,"Y"]
[437210,"Wadebridge 33/11kV S Stn",3.92,null,3775,"",3,"Y"]
[437220,"Newquay Trevemper 33/11kV S Stn",0.66600000000000004,null,1010,"",3,"Y"]
[437230,"Bodmin 33/11kV S Stn",0.189,null,242,"",3,"Y"]
[437340,"Connon Bridge Landfill 33kV S Stn",1.7,null,1513,"",3,"Y"]
[437350,"Blackpool 33/11kV S Stn",0.53300000000000003,null,534,"",3,"Y"]
[437360,"Bugle 33/11kV S Stn",0.43,null,476,"",3,"Y"]
[437370,"Drinnick 33/11kV S Stn",0.96699999999999997,null,1462,"",3,"Y"]
[437380,"Fraddon 33/11kV S Stn",0.27400000000000002,null,2121,"",3,"Y"]
[437390,"Lostwithiel 33/11kV S Stn",1.377,null,1526,"",3,"Y"]
[437400,"Mevagissey 33/11kV S Stn",0.9,null,1128,"",3,"Y"]
[437410,"Davidstow 33/11kV S Stn",4.3,null,3677,"",3,"Y"]
[437420,"Delabole 33/11kV S Stn",1.278,null,1388,"",3,"Y"]
[437430,"Padstow 33/11kV S Stn",1.21,null,975,"",3,"Y"]
[437440,"St Mawgan 33/11kV S Stn",0.76800000000000002,null,658,"",3,"Y"]
[437450,"St Tudy 33/11kV S Stn",1.069,null,2071,"",3,"Y"]
[437460,"Lanreath 33/11kV S Stn",1.4710000000000001,null,1352,"",3,"Y"]
[437470,"Dairy Crest Davidstow 33/11kV S Stn",1.1499999999999999,null,771,"",3,"Y"]
[437490,"St Columb Major 33/11kV S Stn",1.591,null,1632,"",3,"Y"]
[437550,"Polzeath 33/11kV S Stn",2.573,null,2560,"",3,"Y"]
[437570,"Fowey 33/11kV S Stn",1.448,null,1725,"",3,"Y"]
[437610,"Newquay Trencreek Ln 33/11kV S Stn",0.46899999999999997,null,463,"",3,"Y"]
[437640,"Sawles Road 33/11kV S Stn",0.28899999999999998,null,252,"",3,"Y"]
[437670,"Par Harbour 33/11kV S Stn",0.22800000000000001,null,350,"",3,"Y"]
[437720,"Trebal 33/11kV S Stn",1.7050000000000001,null,1755,"",3,"Y"]
[437730,"St Austell BSP 132/33kV S Stn",0.629,null,775,"",3,"Y"]
[437750,"Treningle 33kV S Stn",2.0699999999999998,null,1888,"",3,"Y"]
[437790,"St Breock 33kV S Stn",0.83,null,425,"",3,"Y"]
[437830,"Callywith 33/11kV S Stn",0.46800000000000003,null,394,"",3,"Y"]
[438010,"Trenouth Farm Solar Park 33kV S Stn",0.8,null,735,"",3,"Y"]
[438011,"Manor Farm Solar Park 33kV S Stn",0.214,null,350,"",3,"Y"]
[438018,"Rockhead Wind Farm 33kV S Stn",1.133,null,1176,"",3,"Y"]
[438020,"Bodiniel Solar Park 33kV S Stn",0.9,null,500,"Y",3,"Y"]
[438024,"Woodland Barton Solar Park 33kV S Stn",0.71,null,500,"Y",3,"Y"]
[438025,"Luxulyan Solar Park 33kV S Stn",1.89,null,500,"Y",3,"Y"]
[438036,"Middle Treworder Farm Solar Park 33kV S Stn",0.68100000000000005,null,500,"Y",3,"Y"]
[438037,"Rew Farm Solar Park 33kV S Stn",0.57999999999999996,null,500,"Y",3,"Y"]
[438038,"Winnards Perch Solar Farm 33kV S Stn",0.38,null,500,"Y",3,"Y"]
[438039,"Penhale Solar Farm 33kV S Stn",0.8,null,500,"Y",3,"Y"]
[438040,"Trekenning Farm Solar Park 33kV S Stn",0.39,null,500,"Y",3,"Y"]
[438051,"Ninnis Solar Farm 33kV S Stn",0.26500000000000001,null,459,null,3,"Y"]
[438059,"Langunnett Farm Solar Farm 33kV S Stn",0.38,null,500,"Y",3,"Y"]
[438066,"Hewas Solar Farm 33kV S Stn",0.32,null,500,"Y",3,"Y"]
[438084,"Garlenick Wind Farm 33kV S Stn",1.306,null,500,"Y",3,"Y"]
[438087,"Carloggas Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[438088,"Tregarrick Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[438092,"Outlands Wood Solar Park 33kV S Stn",0.434,null,500,"Y",3,"Y"]
[438094,"St Stephen Solar Park 33kV S Stn",0.36199999999999999,null,500,"Y",3,"Y"]
[438099,"Kerriers Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[438107,"Victoria Wind Farm 33kV S Stn",1.121,null,500,"Y",3,"Y"]
[438148,"Denzell Downs Wind Farm 33kV S Stn",0.15640000000000001,null,500,"Y",3,"Y"]
[438149,"Cornwall Energy Recovery Centre 132kV S Stn",0.78,null,1400,"Y",1,"Y"]
[438156,"West Carclaze Solar Park 33kV S Stn",0.78,null,500,"Y",3,"Y"]
[438171,"Bodwen Solar Farm 33kV S Stn",1.46,null,500,"Y",3,"Y"]
[457240,"Torpoint Antony 33/11kV S Stn",1.39,null,1936,"",3,"Y"]
[457250,"Launceston 33/11kV S Stn",0.13,null,296,"",3,"Y"]
[457260,"Callington 33/11kV S Stn",0.13800000000000001,null,180,"",3,"Y"]
[457270,"Gunnislake 33/11kV S Stn",8.6,null,4954,"",3,"Y"]
[457280,"Saltash Whity Cross 33/11kV S Stn",3.0339999999999998,null,3501,"",3,"Y"]
[457290,"Liskeard 33/11kV S Stn",0.432,null,638,"",3,"Y"]
[457300,"Looe 33/11kV S Stn",0.94099999999999995,null,1622,"",3,"Y"]
[457470,"Pensilva 33/11kV S Stn",5.0110000000000001,null,3403,"",3,"Y"]
[457480,"St Neot 33/11kV S Stn",3.91,null,2491,"",3,"Y"]
[457510,"St Germans 132/33kV S Stn",0.95299999999999996,null,3810,"",3,"Y"]
[457520,"Saltash Dunheved Rd 33/11kV S Stn",0.27500000000000002,null,271,"",3,"Y"]
[457530,"Torpoint Town 33/11kV S Stn",0.245,null,290,"",3,"Y"]
[457620,"Laneast 33/11kV S Stn",5.55,null,2270,"",3,"Y"]
[457710,"Landulph 132/33kV S Stn",0.32,null,3050,"",3,"Y"]
[457810,"Cold Northcott Wind Farm 33kV S Stn",0.12,null,69,"",3,"Y"]
[458013,"Howton Farm Solar Park 33kV S Stn",0.57999999999999996,null,1148,"",3,"Y"]
[458030,"Haye Lane Solar Park 33kV S Stn",0.112,null,500,"Y",3,"Y"]
[458047,"Ford Farm Solar Farm 33kV S Stn",1.1499999999999999,null,500,"Y",3,"Y"]
[458048,"Higher Trevartha Solar Farm 33kV S Stn",1.46,null,500,"Y",3,"Y"]
[458052,"Trequite Solar Farm 33kV S Stn",0.57899999999999996,null,500,"Y",3,"Y"]
[458053,"Yonder Netherton 33kV Solar Farm 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[458058,"Trefinnick Farm Solar Farm 33kV S Stn",0.39,null,500,"Y",3,"Y"]
[458082,"Trehawke Farm Solar Park 33kV S Stn",0.308,null,500,"Y",3,"Y"]
[458086,"Hexworthy Barton Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[458089,"Freathy Farm Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[458095,"Trewidland Farm Solar Park 33kV S Stn",0.34799999999999998,null,500,"Y",3,"Y"]
[458097,"North Wayton Solar Park 33kV S Stn",0.28399999999999997,null,500,"Y",3,"Y"]
[458109,"Otterham Wind Farm 132kV S Stn",0.2,null,1400,"Y",1,"Y"]
[458128,"Newton Barton Solar Park 33kV S Stn",0.32,null,500,"Y",3,"Y"]
[458142,"Wilton Farm Solar Park 33kV S Stn",1.0369999999999999,null,500,"Y",3,"Y"]
[458145,"Wilton 33kV S Stn",0.95299999999999996,null,500,"Y",3,"Y"]
[458147,"Wilton Farm Wind Farm 33kV S Stn",1.01,null,500,"Y",3,"Y"]
[458162,"Trerule Solar Park 33kV S Stn",0.29699999999999999,null,500,"",3,"Y"]

{"sheet":"Source-SWE-Name","index":15,"n_rows":602,"n_cols":9,"rows_kept":602,"cut":false,"hidden":true,"merged":[]}
[null,1,2,3,4,5,6,7,8]
["SUBSTATION_NAME_SWE","SUBSTATION_NAME_TRUNC_SWE","SUBSTATION_NUMBER_SWE","ZE","Assumed ZE","UE","Assumed UE","t","Assumed t"]
["Aaronsons 33kV S Stn","Aaronsons33kVSStn",260580,0.32,null,322,"",3,"Y"]
["Abbeywood 33/11kV S Stn","Abbeywood33/11kVSStn",113884,0.77900000000000003,null,265,"",3,"Y"]
["Abham 400/132kV S Stn","Abham400/132kVSStn",306004,0.2,"Y",6635,"",1,"Y"]
["Adelaide Road 33/11kV S Stn","AdelaideRoad33/11kVSStn",330014,0.47,null,85,"",3,"Y"]
["Alcombe 33/11kV S Stn","Alcombe33/11kVSStn",210190,0.107,null,103,"",3,"Y"]
["Alders Way STOR 33kV S Stn","AldersWaySTOR33kVSStn",348182,0.42799999999999999,null,500,"Y",3,"Y"]
["Alexandra Road 33/11kV S Stn","AlexandraRoad33/11kVSStn",330018,0.36,null,113,"",3,"Y"]
["Aller Court Solar Farm 33kV S Stn","AllerCourtSolarFarm33kVSStn",218071,0.17,null,500,"Y",3,"Y"]
["Alma Road 33/11kV S Stn","AlmaRoad33/11kVSStn",330020,0.16500000000000001,null,244,"",3,"Y"]
["Almondsbury 33/11kV S Stn","Almondsbury33/11kVSStn",111935,0.121,null,143,"",3,"Y"]
["Alverdiscott 400/132kV S Stn","Alverdiscott400/132kVSStn",206001,0.2,"Y",2028,"",1,"Y"]
["Alverdiscott Wind Farm 33kV S Stn","AlverdiscottWindFarm33kVSStn",358079,0.7,"Y",500,"Y",3,"Y"]
["Armada Street 33/11kV S Stn","ArmadaStreet33/11kVSStn",330021,0.27,null,113,"",3,"Y"]
["Ashburton 33/11kV S Stn","Ashburton33/11kVSStn",340013,0.34,null,481,"",3,"Y"]
["Ashcombe Solar Park 33kV S Stn","AshcombeSolarPark33kVSStn",348132,6.6000000000000003E-2,null,500,"Y",3,"Y"]
["Ashlawn Farm Solar Park 33kV S Stn","AshlawnFarmSolarPark33kVSStn",188123,8.5000000000000006E-2,null,500,"Y",3,"Y"]
["Ashwater 33/11kV S Stn","Ashwater33/11kVSStn",350022,2.8330000000000002,null,3043,"",3,"Y"]
["Ashwater Solar Park 33kV S Stn","AshwaterSolarPark33kVSStn",358160,0.5,null,500,"Y",3,"Y"]
["Astrazeneca 33/11kV S Stn","Astrazeneca33/11kVSStn",114258,0.47,null,348,"",3,"Y"]
["Athelstan Road 33/11kV S Stn","AthelstanRoad33/11kVSStn",310020,0.2,null,261,"",3,"Y"]
["Avonmouth 33/11kV S Stn","Avonmouth33/11kVSStn",113368,7.0000000000000007E-2,null,109,"",3,"Y"]
["Avonmouth Biogas 33kV S Stn","AvonmouthBiogas33kVSStn",114652,0.183,null,500,"Y",3,"Y"]
["Avonmouth BSP 132/33kV S Stn","AvonmouthBSP132/33kVSStn",113367,1.4999999999999999E-2,null,92,"",3,"Y"]
["Avonmouth Docks 33/6.6kV S Stn","AvonmouthDocks33/6.6kVSStn",113277,0.08,null,119,"",3,"Y"]
["Avonmouth Wind Farm 33kV S Stn","AvonmouthWindFarm33kVSStn",118093,8.5000000000000006E-2,null,500,"Y",3,"Y"]
["Axbridge 33/11kV S Stn","Axbridge33/11kVSStn",180017,0.19,null,281,"",3,"Y"]
["Axe View Solar Farm 33kV S Stn","AxeViewSolarFarm33kVSStn",258174,3.1E-2,null,500,"Y",3,"Y"]
["Axminster 33/11kV S Stn","Axminster33/11kVSStn",250280,0.11600000000000001,null,196,"",3,"Y"]
["Axminster GSP 400/132kV S Stn","AxminsterGSP400/132kVSStn",206006,0.2,"Y",2096,"",1,"Y"]
["Ayshford Court Farm Solar Park 33kV S Stn","AyshfordCourtFarmSolarPark33kVSStn",318035,0.17499999999999999,null,500,"Y",3,"Y"]
["Balls Wood Solar Park 33kV S Stn","BallsWoodSolarPark33kVSStn",338120,0.28899999999999998,null,500,"Y",3,"Y"]
["Barnstaple 132/33/11kV S Stn","Barnstaple132/33/11kVSStn",260467,6.2E-2,null,93,"",3,"Y"]
["Barnstaple Quay 33/11kV S Stn","BarnstapleQuay33/11kVSStn",260250,0.1,null,115,"",3,"Y"]
["Barton 33/11kV S Stn","Barton33/11kVSStn",340024,0.58099999999999996,null,109,"",3,"Y"]
["Barton Hill STOR Generator 33kV S Stn","BartonHillSTORGenerator33kVSStn",348178,0.41,null,500,"Y",3,"Y"]
["Bath Dolemeads 132/33/6.6kV S Stn","BathDolemeads132/33/6.6kVSStn",164087,7.1999999999999995E-2,null,68,"",3,"Y"]
["Batheaston 33/6.6kV S Stn","Batheaston33/6.6kVSStn",160389,4.3999999999999997E-2,null,59,"",3,"Y"]
["Bath Road 33/11kV S Stn","BathRoad33/11kVSStn",210160,0.06,null,90,"",3,"Y"]
["Batsworthy Cross Wind Farm 33kV S Stn","BatsworthyCrossWindFarm33kVSStn",318152,0.49,null,500,"Y",3,"Y"]
["Beaford Solar Farm 33kV S Stn","BeafordSolarFarm33kVSStn",268005,0.375,null,500,"Y",3,"Y"]
["Beaminster 33/11kV S Stn","Beaminster33/11kVSStn",250620,0.439,null,358,"",3,"Y"]
["Bears Down Wind Farm 33kV S Stn","BearsDownWindFarm33kVSStn",437150,0.55000000000000004,null,282,"",3,"Y"]
["Bedminster 33/11kV S Stn","Bedminster33/11kVSStn",110641,0.12,null,348,"",3,"Y"]
["Beechgrove Farm Solar Park 33kV S Stn","BeechgroveFarmSolarPark33kVSStn",258019,0.16700000000000001,null,274,"",3,"Y"]
["Bideford Main 33/11kV S Stn","BidefordMain33/11kVSStn",350018,0.104,null,115,"",3,"Y"]
["Bidwell Solar Park 33kV S Stn","BidwellSolarPark33kVSStn",348103,0.29799999999999999,null,500,"Y",3,"Y"]
["Bishopsworth 33/11kV S Stn","Bishopsworth33/11kVSStn",113193,0.12,null,198,"",3,"Y"]
["Blackawton 33/11kV S Stn","Blackawton33/11kVSStn",340022,1.3859999999999999,null,1249,"",3,"Y"]
["Blackditch 33kV S Stn","Blackditch33kVSStn",210600,0.123,null,369,"",3,"Y"]
["Blackpool 33/11kV S Stn","Blackpool33/11kVSStn",437350,0.53300000000000003,null,534,"",3,"Y"]
["Blagdon 33/11kV S Stn","Blagdon33/11kVSStn",180173,0.11799999999999999,null,160,"",3,"Y"]
["Bodiniel Solar Park 33kV S Stn","BodinielSolarPark33kVSStn",438020,0.9,null,500,"Y",3,"Y"]
["Bodmin 33/11kV S Stn","Bodmin33/11kVSStn",437230,0.189,null,242,"",3,"Y"]
["Bodwen Solar Farm 33kV S Stn","BodwenSolarFarm33kVSStn",438171,1.46,null,500,"Y",3,"Y"]
["Bommerton Farm Solar Park 33kV S Stn","BommertonFarmSolarPark33kVSStn",268081,0.7,"Y",500,"Y",3,"Y"]
["Bommertown Solar Park 33kV S Stn","BommertownSolarPark33kVSStn",268136,0.7,"Y",500,"Y",3,"Y"]
["Bournville 33/11kV S Stn","Bournville33/11kVSStn",180471,7.9000000000000001E-2,null,141,"",3,"Y"]
["Bovey Tracey 33/11kV S Stn","BoveyTracey33/11kVSStn",340039,0.19700000000000001,null,215,"",3,"Y"]
["Bower Ashton 33/11kV S Stn","BowerAshton33/11kVSStn",113371,0.12,null,186,"",3,"Y"]
["Bowhays Cross 132/33kV S Stn","BowhaysCross132/33kVSStn",210210,0.192,null,396,"",3,"Y"]
["Bowhays Cross 33/11kV S Stn","BowhaysCross33/11kVSStn",210210,0.192,null,396,"",3,"Y"]
["Bradford Manor Solar Farm 33kV S Stn","BradfordManorSolarFarm33kVSStn",358057,0.34,null,500,"Y",3,"Y"]
["Bradley Lane 33/11kV S Stn","BradleyLane33/11kVSStn",340020,8.3000000000000004E-2,null,78,"",3,"Y"]
["Bradley Stoke 132/33kV S Stn","BradleyStoke132/33kVSStn",113572,0.21,null,1024,"",3,"Y"]
["Bradley Stoke 33/11kV S Stn","BradleyStoke33/11kVSStn",113760,0.21,null,500,"Y",3,"Y"]
["Bradon Fm Generator 33kV S Stn","BradonFmGenerator33kVSStn",210260,7.6999999999999999E-2,null,54,"",3,"Y"]
["Bratton Fleming 33/11kV S Stn","BrattonFleming33/11kVSStn",260550,3.82,null,2475,"",3,"Y"]
["Bratton Fleming Solar Park 33kV S Stn","BrattonFlemingSolarPark33kVSStn",268000,0.81,null,500,"Y",3,"Y"]
["Braunton 33/11kV S Stn","Braunton33/11kVSStn",260220,0.372,null,463,"",3,"Y"]
["Brent Knoll 33kV S Stn","BrentKnoll33kVSStn",182332,0.191,null,154,"",3,"Y"]
["Bridge Mills 33/11kV S Stn","BridgeMills33/11kVSStn",310018,0.21,null,201,"",3,"Y"]
["Bridgwater Grid 132/33kV S Stn","BridgwaterGrid132/33kVSStn",210444,6.0999999999999999E-2,null,431,"",3,"Y"]
["Bridgwater GSP 275/132kV S Stn","BridgwaterGSP275/132kVSStn",206008,5.6000000000000001E-2,null,820,"",1,"Y"]
["Bridgwater Local 33/11kV S Stn","BridgwaterLocal33/11kVSStn",210060,9.0999999999999998E-2,null,358,"",3,"Y"]
["Bridport 33/11kV S Stn","Bridport33/11kVSStn",250340,5.8000000000000003E-2,null,56,"",3,"Y"]
["Bristol International Airport 33/11kV S Stn","BristolInternationalAirport33/11kVSStn",182736,0.28299999999999997,null,406,"",3,"Y"]
["British Gas Hallen 33/11kV S Stn","BritishGasHallen33/11kVSStn",113429,7.0999999999999994E-2,null,110,"",3,"Y"]
["Broadweir 33/11kV S Stn","Broadweir33/11kVSStn",114260,0.06,null,13.5,"",3,"Y"]
["Buckfastleigh 33/11kV S Stn","Buckfastleigh33/11kVSStn",340014,0.55700000000000005,null,495,"",3,"Y"]
["Buckwell Street 33/11kV S Stn","BuckwellStreet33/11kVSStn",330022,0.57999999999999996,null,229,"",3,"Y"]
["Budleigh Salterton 33/11kV S Stn","BudleighSalterton33/11kVSStn",310039,9.9000000000000005E-2,null,118,"",3,"Y"]
["Bugle 33/11kV S Stn","Bugle33/11kVSStn",437360,0.43,null,476,"",3,"Y"]
["Burlescombe 33/11kV S Stn","Burlescombe33/11kVSStn",310033,0.52300000000000002,null,1029,"",3,"Y"]
["Burnham 33/11kV S Stn","Burnham33/11kVSStn",210470,4.2999999999999997E-2,null,54,"",3,"Y"]
["Burrowton Farm Solar Park 33kV S Stn","BurrowtonFarmSolarPark33kVSStn",318026,0.16,null,500,"Y",3,"Y"]
["Burthy Solar Park 33kV S Stn","BurthySolarPark33kVSStn",418141,0.46,null,500,"Y",3,"Y"]
["Bystock Farm Solar Park 33kV S Stn","BystockFarmSolarPark33kVSStn",318137,0.185,null,500,"Y",3,"Y"]
["Cairns Road 33/11kV S Stn","CairnsRoad33/11kVSStn",110803,0.09,null,207,"",3,"Y"]
["Callington 33/11kV S Stn","Callington33/11kVSStn",457260,0.13800000000000001,null,180,"",3,"Y"]
["Callywith 33/11kV S Stn","Callywith33/11kVSStn",437830,0.46800000000000003,null,394,"",3,"Y"]
["Camborne 132/33kV S Stn","Camborne132/33kVSStn",407020,0.23200000000000001,null,512,"",3,"Y"]
["Camborne Carn Brea 33/11kV S Stn","CamborneCarnBrea33/11kVSStn",417020,0.216,null,177,"",3,"Y"]
["Camborne Holmans 33/11kV S Stn","CamborneHolmans33/11kVSStn",417540,0.23699999999999999,null,390,"",3,"Y"]
["Camborne Treswithian 33/11kV S Stn","CamborneTreswithian33/11kVSStn",417010,2.2789999999999999,null,3519,"",3,"Y"]
["Capelands Farm Solar Park 33kV S Stn","CapelandsFarmSolarPark33kVSStn",268113,0.86,null,500,"Y",3,"Y"]
["Carditch Drove Solar Park 33kV S Stn","CarditchDroveSolarPark33kVSStn",188112,0.1,null,500,"Y",3,"Y"]
["Carland Cross Wind Farm 33kV S Stn","CarlandCrossWindFarm33kVSStn",417800,0.52,null,1435,"",3,"Y"]
["Carloggas Farm Solar Park 33kV S Stn","CarloggasFarmSolarPark33kVSStn",438087,0.7,"Y",500,"Y",3,"Y"]
["Carnemough Farm Solar Park 33kV S Stn","CarnemoughFarmSolarPark33kVSStn",418158,0.56100000000000005,null,500,"Y",3,"Y"]
["Carnworthy Solar Park 132kV S Stn","CarnworthySolarPark132kVSStn",357304,1.254,null,1400,"Y",1,"Y"]
["Cattledown STOR Generator 33kV S Stn","CattledownSTORGenerator33kVSStn",338177,0.124,null,500,"Y",3,"Y"]
["Causilgey Solar Farm 33kV S Stn","CausilgeySolarFarm33kVSStn",418046,1.1100000000000001,null,500,"Y",3,"Y"]
["Central Intake 33kV S Stn","CentralIntake33kVSStn",330041,0.3,null,421,"",3,"Y"]
["Chalhanger Farm Solar Park 33kV S Stn","ChalhangerFarmSolarPark33kVSStn",358085,0.7,"Y",500,"Y",3,"Y"]
["Chard 33/11kV S Stn","Chard33/11kVSStn",250360,2.9000000000000001E-2,null,39,"",3,"Y"]
["Cheddar 33/11kV S Stn","Cheddar33/11kVSStn",181345,8.2000000000000003E-2,null,128,"",3,"Y"]
["Chelson Generator 33kV S Stn","ChelsonGenerator33kVSStn",330046,0.24,null,326,"",3,"Y"]
["Chelwood Solar Park 33kV S Stn","ChelwoodSolarPark33kVSStn",118154,0.125,null,500,"Y",3,"Y"]
["Chew Stoke 33/11kV S Stn","ChewStoke33/11kVSStn",181230,0.40200000000000002,null,339,"",3,"Y"]
["Chewton Mendip 33/11kV S Stn","ChewtonMendip33/11kVSStn",160415,2,null,2670,"",3,"Y"]
["Chudleigh Knighton 33/11kV S Stn","ChudleighKnighton33/11kVSStn",340011,0.24199999999999999,null,222,"",3,"Y"]
["Churchill 132/33kV S Stn","Churchill132/33kVSStn",182373,0.18,null,271,"",3,"Y"]
["Churchill Gate 33/11kV S Stn","ChurchillGate33/11kVSStn",182570,0.55000000000000004,null,853,"",3,"Y"]
["Churchtown Farm Solar Park 33kV S Stn","ChurchtownFarmSolarPark33kVSStn",418008,0.37,null,262,"",3,"Y"]
["Churston 33/11kV S Stn","Churston33/11kVSStn",340029,0.621,null,384,"",3,"Y"]
["Chynoweth Solar Park 33kV S Stn","ChynowethSolarPark33kVSStn",418009,0.38,null,821,null,3,"Y"]
["Cleave Farm Solar Park 33kV S Stn","CleaveFarmSolarPark33kVSStn",268091,0.29199999999999998,null,500,"Y",3,"Y"]
["Clevedon 33/11kV S Stn","Clevedon33/11kVSStn",180198,0.26200000000000001,null,275,"",3,"Y"]
["Clifton 33/11kV S Stn","Clifton33/11kVSStn",111158,0.12,null,251,"",3,"Y"]
["Clovelly 33/11kV S Stn","Clovelly33/11kVSStn",350011,2.1,null,1338,"",3,"Y"]
["Clyst Honiton 33/11kV S Stn","ClystHoniton33/11kVSStn",310034,0.5,null,565,"",3,"Y"]
["Cobbs Cross Solar Farm 33kV S Stn","CobbsCrossSolarFarm33kVSStn",218061,0.157,null,500,"Y",3,"Y"]
["Coker 33/11kV S Stn","Coker33/11kVSStn",250530,1.1120000000000001,null,1672,"",3,"Y"]
["Cold Northcott Wind Farm 33kV S Stn","ColdNorthcottWindFarm33kVSStn",457810,0.12,null,69,"",3,"Y"]
["Colley End 33/11kV S Stn","ColleyEnd33/11kVSStn",340034,0.18,null,214,"",3,"Y"]
["Colley Lane 33/11kV S Stn","ColleyLane33/11kVSStn",210120,8.2000000000000003E-2,null,295,"",3,"Y"]
["Colyford 33/11kV S Stn","Colyford33/11kVSStn",250310,0.60899999999999999,null,605,"",3,"Y"]
["Combe Park 33/6.6kV S Stn","CombePark33/6.6kVSStn",164016,7.5999999999999998E-2,null,96,"",3,"Y"]
["Compton Martin 33/11kV S Stn","ComptonMartin33/11kVSStn",181346,0.46899999999999997,null,935,"",3,"Y"]
["Congresbury 33/11kV S Stn","Congresbury33/11kVSStn",180006,0.153,null,325,"",3,"Y"]
["Connon Bridge Landfill 33kV S Stn","ConnonBridgeLandfill33kVSStn",437340,1.7,null,1513,"",3,"Y"]
["Constantine 33/11kV S Stn","Constantine33/11kVSStn",417320,3.8519999999999999,null,4898,"",3,"Y"]
["Coombe Farm Solar Park 33kV S Stn","CoombeFarmSolarPark33kVSStn",318146,0.25,null,500,"Y",3,"Y"]
["Coombeshead Farm Solar Park 33kV S Stn","CoombesheadFarmSolarPark33kVSStn",348131,0.56000000000000005,null,500,"Y",3,"Y"]
["Core Hill 33/11kV S Stn","CoreHill33/11kVSStn",310044,0.17799999999999999,null,160,"",3,"Y"]
["Cornwall Energy Recovery Centre 132kV S Stn","CornwallEnergyRecoveryCentre132kVSStn",438149,0.78,null,1400,"Y",1,"Y"]
["Cotham 33/11kV S Stn","Cotham33/11kVSStn",114389,0.16500000000000001,null,81,"",3,"Y"]
["Countess Wear 33/11kV S Stn","CountessWear33/11kVSStn",310048,0.124,null,35,"",3,"Y"]
["Cowley Road 33/11kV S Stn","CowleyRoad33/11kVSStn",310014,6.4000000000000001E-2,null,77,"",3,"Y"]
["Crediton 33/11kV S Stn","Crediton33/11kVSStn",310015,0.11700000000000001,null,120,"",3,"Y"]
["Creech St Michael 33/11kV S Stn","CreechStMichael33/11kVSStn",210030,0.30399999999999999,null,333,"",3,"Y"]
["Crewkerne 33/11kV S Stn","Crewkerne33/11kVSStn",250370,8.8999999999999996E-2,null,307,"",3,"Y"]
["Crewkerne Solar Park 33kV S Stn","CrewkerneSolarPark33kVSStn",258153,0.13800000000000001,null,500,"Y",3,"Y"]
["Cribbs Causeway 33/11kV S Stn","CribbsCauseway33/11kVSStn",113983,7.6999999999999999E-2,null,32,"",3,"Y"]
["Cricket St Thomas Solar Park 33kV S Stn","CricketStThomasSolarPark33kVSStn",258063,0.13600000000000001,null,500,"Y",3,"Y"]
["Crinacott Farm Solar Park 33kV S Stn","CrinacottFarmSolarPark33kVSStn",358068,0.14000000000000001,null,500,"Y",3,"Y"]
["Cullompton 33/11kV S Stn","Cullompton33/11kVSStn",310024,0.27100000000000002,null,298,"",3,"Y"]
["Cullompton Solar Park 33kV S Stn","CullomptonSolarPark33kVSStn",318098,0.2,null,500,"Y",3,"Y"]
["Culmhead 33/11kV S Stn","Culmhead33/11kVSStn",210390,0.79300000000000004,null,948,"",3,"Y"]
["Culmhead Solar Park 33kV S Stn","CulmheadSolarPark33kVSStn",218009,0.13700000000000001,null,500,"Y",3,"Y"]
["Curry Mallet 33/11kV S Stn","CurryMallet33/11kVSStn",210450,0.78800000000000003,null,871,"",3,"Y"]
["Dairy Crest Davidstow 33/11kV S Stn","DairyCrestDavidstow33/11kVSStn",437470,1.1499999999999999,null,771,"",3,"Y"]
["Darracott Moor Windfarm 33kV S Stn","DarracottMoorWindfarm33kVSStn",260180,0.82,null,792,"",3,"Y"]
["Dartmouth 33/11kV S Stn","Dartmouth33/11kVSStn",340030,0.39300000000000002,null,381,"",3,"Y"]
["Davidstow 33/11kV S Stn","Davidstow33/11kVSStn",437410,4.3,null,3677,"",3,"Y"]
["Dawlish 33/11kV S Stn","Dawlish33/11kVSStn",340023,0.14299999999999999,null,125,"",3,"Y"]
["Delabole 33/11kV S Stn","Delabole33/11kVSStn",437420,1.278,null,1388,"",3,"Y"]
["Denbrook Wind Farm 33kV S Stn","DenbrookWindFarm33kVSStn",358159,0.16600000000000001,null,500,"Y",3,"Y"]
["Denzell Downs Wind Farm 33kV S Stn","DenzellDownsWindFarm33kVSStn",438148,0.15640000000000001,null,500,"Y",3,"Y"]
["Derriton Fields Solar Park 33kV S Stn","DerritonFieldsSolarPark33kVSStn",358080,0.28499999999999998,null,500,"Y",3,"Y"]
["Devoran 33/11kV S Stn","Devoran33/11kVSStn",417310,2.1150000000000002,null,2563,"",3,"Y"]
["Dinder 33/11kV S Stn","Dinder33/11kVSStn",160811,4.2699999999999996,null,4582,"",3,"Y"]
["Dinder Farm Solar Park 33kV S Stn","DinderFarmSolarPark33kVSStn",168106,0.65600000000000003,null,500,"Y",3,"Y"]
["Dorchester Street 33/6.6kV S Stn","DorchesterStreet33/6.6kVSStn",164170,7.1999999999999995E-2,null,105,"",3,"Y"]
["Dowlish Ford 33/11kV S Stn","DowlishFord33/11kVSStn",250350,0.16,null,202,"",3,"Y"]
["Drinnick 33/11kV S Stn","Drinnick33/11kVSStn",437370,0.96699999999999997,null,1462,"",3,"Y"]
["Dunkeswell 33/11kV S Stn","Dunkeswell33/11kVSStn",310057,0.29099999999999998,null,203,"",3,"Y"]
["Dunsland Cross Wind Farm 33kV S Stn","DunslandCrossWindFarm33kVSStn",358167,0.29799999999999999,null,500,"Y",3,"Y"]
["Eastacombe Solar Farm 33kV S Stn","EastacombeSolarFarm33kVSStn",358022,0.33500000000000002,null,500,"Y",3,"Y"]
["East Brent 33/11kV S Stn","EastBrent33/11kVSStn",181425,0.158,null,144,"",3,"Y"]
["East Budleigh 33/11kV S Stn","EastBudleigh33/11kVSStn",310040,2.5,null,2390,"",3,"Y"]
["East Chinnock 33/11kV S Stn","EastChinnock33/11kVSStn",250290,0.29599999999999999,null,413,"",3,"Y"]
["East Curry 33/11kV S Stn","EastCurry33/11kVSStn",350015,0.93100000000000005,null,865,"",3,"Y"]
["East Langford Solar Park 33kV S Stn","EastLangfordSolarPark33kVSStn",358017,0.28999999999999998,null,402,"",3,"Y"]
["Easton-In-Gordano 33/11kV S Stn","Easton-In-Gordano33/11kVSStn",181414,0.189,null,417,"",3,"Y"]
["Eastville 33/11kV S Stn","Eastville33/11kVSStn",110644,0.10199999999999999,null,500,"Y",3,"Y"]
["East Yelland 132/33kV S Stn","EastYelland132/33kVSStn",260465,0.22,null,263,"",3,"Y"]
["East Youlstone Windfarm 33kV S Stn","EastYoulstoneWindfarm33kVSStn",358114,0.7,null,500,"Y",3,"Y"]
["Edgarley 33/11kV S Stn","Edgarley33/11kVSStn",210110,0.14799999999999999,null,194,"",3,"Y"]
["Eggbuckland 33/11kV S Stn","Eggbuckland33/11kVSStn",330025,7.1999999999999995E-2,null,24,"",3,"Y"]
["Elim Terrace 33/11kV S Stn","ElimTerrace33/11kVSStn",330019,0.16,null,281,"",3,"Y"]
["Emersons Green 33/11kV S Stn","EmersonsGreen33/11kVSStn",114391,0.33,null,144,"",3,"Y"]
["Entry Hill 33/6.6kV S Stn","EntryHill33/6.6kVSStn",160355,6.5000000000000002E-2,null,88,"",3,"Y"]
["Ernesettle 132/33kV S Stn","Ernesettle132/33kVSStn",330001,0.153,null,1232,"",3,"Y"]
["Ernesettle B & S 33/11kV S Stn","ErnesettleB&S33/11kVSStn",330038,0.153,null,216,"",3,"Y"]
["Ernesettle Lane STOR Generator 33kV S Stn","ErnesettleLaneSTORGenerator33kVSStn",333743,0.156,null,1171,"",3,"Y"]
["Evercreech 33/11kV S Stn","Evercreech33/11kVSStn",161823,0.129,null,103,"",3,"Y"]
["Exebridge 33/11kV S Stn","Exebridge33/11kVSStn",210140,1.25,null,689,"",3,"Y"]
["Exeter City 132/33kV S Stn","ExeterCity132/33kVSStn",310001,0.1,null,467,"",3,"Y"]
["Exeter Main 33kV S Stn","ExeterMain33kVSStn",310003,0.15,null,1648,"",3,"Y"]
["Exeter Main 400/132kV S Stn","ExeterMain400/132kVSStn",306005,0.115,null,1648,"",1,"Y"]
["Exeter Science Park 33/11kV S Stn","ExeterSciencePark33/11kVSStn",310060,0.32,null,500,"Y",3,"Y"]
["Exminster 33/11kV S Stn","Exminster33/11kVSStn",310030,0.16400000000000001,null,187,"",3,"Y"]
["Exmouth 132/33kV S Stn","Exmouth132/33kVSStn",310004,7.5999999999999998E-2,null,323,"",3,"Y"]
["Exmouth Works 33/11kV S Stn","ExmouthWorks33/11kVSStn",310038,0.11,null,151,"",3,"Y"]
["Falmouth Bickland Hill 33/11kV S Stn","FalmouthBicklandHill33/11kVSStn",417160,0.186,null,275,"",3,"Y"]
["Falmouth Docks 33/11kV S Stn","FalmouthDocks33/11kVSStn",417180,0.13400000000000001,null,182,"",3,"Y"]
["Faraday Road STOR Generator 33kV S Stn","FaradayRoadSTORGenerator33kVSStn",333718,0.124,null,500,"Y",3,"Y"]
["Feeder Road 132/33kV S Stn","FeederRoad132/33kVSStn",113449,0.05,null,251,"",3,"Y"]
["Feeder Road 33kV S Stn","FeederRoad33kVSStn",113372,0.05,null,79,"",3,"Y"]
["Feeder Road A 33/11kV S Stn","FeederRoadA33/11kVSStn",113373,0.05,null,140,"",3,"Y"]
["Feeder Road B 33/11kV S Stn","FeederRoadB33/11kVSStn",113374,0.05,null,140,"",3,"Y"]
["Filton Dc 33/11kV S Stn","FiltonDc33/11kVSStn",113369,0.13,null,201,"",3,"Y"]
["Folly Bridge 33/11kV S Stn","FollyBridge33/11kVSStn",310016,0.621,null,631,"",3,"Y"]
["Ford Farm Solar Farm 33kV S Stn","FordFarmSolarFarm33kVSStn",458047,1.1499999999999999,null,500,"Y",3,"Y"]
["Forestmoor 33/11kV S Stn","Forestmoor33/11kVSStn",350025,0.72,null,715,"",3,"Y"]
["Four Burrows Blackdown Solar Park 33kV S Stn","FourBurrowsBlackdownSolarPark33kVSStn",418108,0.878,null,500,"Y",3,"Y"]
["Fourburrows Pendown 33kV S Stn","FourburrowsPendown33kVSStn",418041,0.48,null,500,"Y",3,"Y"]
["Four Burrows Windfarm 33kV S Stn","FourBurrowsWindfarm33kVSStn",417820,0.38200000000000001,null,845,"",3,"Y"]
["Fowey 33/11kV S Stn","Fowey33/11kVSStn",437570,1.448,null,1725,"",3,"Y"]
["Foxcombe Solar Park 33kV S Stn","FoxcombeSolarPark33kVSStn",358076,0.7,"Y",500,"Y",3,"Y"]
["Foxhills 33/11kV S Stn","Foxhills33/11kVSStn",162344,0.16200000000000001,null,226,"",3,"Y"]
["Fraddon 132/33kV S Stn","Fraddon132/33kVSStn",407380,0.27400000000000002,null,2392,"",3,"Y"]
["Fraddon 33/11kV S Stn","Fraddon33/11kVSStn",437380,0.27400000000000002,null,2121,"",3,"Y"]
["Francis Court Farm Solar Park 33kV S Stn","FrancisCourtFarmSolarPark33kVSStn",318118,0.41499999999999998,null,500,"Y",3,"Y"]
["Freathy Farm Solar Park 33kV S Stn","FreathyFarmSolarPark33kVSStn",458089,0.7,"Y",500,"Y",3,"Y"]
["Fremington 33/11kV S Stn","Fremington33/11kVSStn",260480,1.7090000000000001,null,2616,"",3,"Y"]
["Frys Hill Radio 33kV/LV S Stn","FrysHillRadio33kV/LVSStn",182000,0.7,"Y",500,"Y",3,"Y"]
["Fulford Solar Park 33kV S Stn","FulfordSolarPark33kVSStn",318031,0.7,"Y",500,"Y",3,"Y"]
["Fullabrook Windfarm 132kV S Stn","FullabrookWindfarm132kVSStn",260006,0.4,null,580,"",1,"Y"]
["Galsworthy Wind Farm 132kV S Stn","GalsworthyWindFarm132kVSStn",357295,0.54,null,1400,"Y",1,"Y"]
["Garlenick Wind Farm 33kV S Stn","GarlenickWindFarm33kVSStn",438084,1.306,null,500,"Y",3,"Y"]
["Garvinack Farm Solar Park 33kV S Stn","GarvinackFarmSolarPark33kVSStn",418126,0.7,null,500,"Y",3,"Y"]
["Gas Lane 33/11kV S Stn","GasLane33/11kVSStn",180003,3.7999999999999999E-2,null,36,"",3,"Y"]
["Geevor 33/11kV S Stn","Geevor33/11kVSStn",417040,3.4,null,2309,"",3,"Y"]
["Georgeham 33/11kV S Stn","Georgeham33/11kVSStn",260570,3.23,null,2061,"",3,"Y"]
["Glebe Farm 2 Solar Farm 33kV S Stn","GlebeFarm2SolarFarm33kVSStn",218044,0.69,null,578,null,3,"Y"]
["Goonhilly Solar Park 33kV S Stn","GoonhillySolarPark33kVSStn",418102,0.36,null,500,"Y",3,"Y"]
["Goonhilly Wind Farm 33kV S Stn","GoonhillyWindFarm33kVSStn",415927,0.52,null,388,"",3,"Y"]
["Gover Park Solar Park 33kV S Stn","GoverParkSolarPark33kVSStn",418096,0.54900000000000004,null,500,"Y",3,"Y"]
["Grange Farm Solar Park 33kV S Stn","GrangeFarmSolarPark33kVSStn",218004,0.7,"Y",500,"Y",3,"Y"]
["Great Houndbeare Farm Solar Park 33kV S Stn","GreatHoundbeareFarmSolarPark33kVSStn",318164,0.22900000000000001,null,500,"Y",3,"Y"]
["Great Torrington 33/11kV S Stn","GreatTorrington33/11kVSStn",260270,0.28999999999999998,null,234,"",3,"Y"]
["Gunnislake 33/11kV S Stn","Gunnislake33/11kVSStn",457270,8.6,null,4954,"",3,"Y"]
["Halse Solar Farm 33kV S Stn","HalseSolarFarm33kVSStn",218043,0.09,null,112,null,3,"Y"]
["Hatchlands Farm Solar Park 33kV S Stn","HatchlandsFarmSolarPark33kVSStn",348045,0.4,null,500,"Y",3,"Y"]
["Hatherleigh 33/11kV S Stn","Hatherleigh33/11kVSStn",350019,0.155,null,177,"",3,"Y"]
["Haven Road 33/11kV S Stn","HavenRoad33/11kVSStn",310049,0.19,null,253,"",3,"Y"]
["Hawkers Farm Solar Park 33kV S Stn","HawkersFarmSolarPark33kVSStn",188124,0.109,null,500,"Y",3,"Y"]
["Haye Lane Solar Park 33kV S Stn","HayeLaneSolarPark33kVSStn",458030,0.112,null,500,"Y",3,"Y"]
["Hayle 132/33kV S Stn","Hayle132/33kVSStn",407150,9.5000000000000001E-2,null,112,"",3,"Y"]
["Hayle 33/11kV S Stn","Hayle33/11kVSStn",417150,9.5000000000000001E-2,null,131,"",3,"Y"]
["Hazard Farm Solar Park 33kV S Stn","HazardFarmSolarPark33kVSStn",348077,0.496,null,500,"Y",3,"Y"]
["Heathfield Landfill 33kV S Stn","HeathfieldLandfill33kVSStn",340043,0.28999999999999998,null,341,"",3,"Y"]
["Heavitree 33/11kV S Stn","Heavitree33/11kVSStn",310029,0.26,null,323,"",3,"Y"]
["Heddon Cross 33/11kV S Stn","HeddonCross33/11kVSStn",260430,1.68,null,1054,"",3,"Y"]
["Hele Manor STOR 33kV S Stn","HeleManorSTOR33kVSStn",218045,0.26500000000000001,null,133,"",3,"Y"]
["Helston 33/11kV S Stn","Helston33/11kVSStn",417050,0.25900000000000001,null,336,"",3,"Y"]
["Hemerdon Mine 33/11kV S Stn","HemerdonMine33/11kVSStn",333760,0.53,null,500,"Y",3,"Y"]
["Hemyock 33/11kV S Stn","Hemyock33/11kVSStn",310056,0.60699999999999998,null,715,"",3,"Y"]
["Hewas Solar Farm 33kV S Stn","HewasSolarFarm33kVSStn",438066,0.32,null,500,"Y",3,"Y"]
["Hewlett Packard 33/11kV S Stn","HewlettPackard33/11kVSStn",113720,6.3E-2,null,28,"",3,"Y"]
["Hewlett Packard 33kV S Stn","HewlettPackard33kVSStn",114632,6.3E-2,null,500,"Y",3,"Y"]
["Hexworthy Barton Solar Park 33kV S Stn","HexworthyBartonSolarPark33kVSStn",458086,0.7,"Y",500,"Y",3,"Y"]
["Higher Berechapel Farm Solar Park 33kV S Stn","HigherBerechapelFarmSolarPark33kVSStn",258083,0.7,"Y",500,"Y",3,"Y"]
["Higher Bye Farm Solar Park 33kV S Stn","HigherByeFarmSolarPark33kVSStn",218021,6.5000000000000002E-2,null,500,"Y",3,"Y"]
["Higher North Beer Farm Solar Park 33kV S Stn","HigherNorthBeerFarmSolarPark33kVSStn",358056,0.20699999999999999,null,500,"Y",3,"Y"]
["Higher Tregarne Solar Farm 33kV S Stn","HigherTregarneSolarFarm33kVSStn",418049,1.04,null,500,"Y",3,"Y"]
["Higher Trenhayle Farm Solar Park 33kV S Stn","HigherTrenhayleFarmSolarPark33kVSStn",418034,0.93300000000000005,null,500,"Y",3,"Y"]
["Higher Trevartha Solar Farm 33kV S Stn","HigherTrevarthaSolarFarm33kVSStn",458048,1.46,null,500,"Y",3,"Y"]
["Higher Woodway 33/11kV S Stn","HigherWoodway33/11kVSStn",340018,0.16800000000000001,null,198,"",3,"Y"]
["High Littleton 33/11kV S Stn","HighLittleton33/11kVSStn",161532,0.24,null,401,"",3,"Y"]
["Hill Barton Primary 33/11kV S Stn","HillBartonPrimary33/11kVSStn",310061,0.16900000000000001,null,500,"Y",3,"Y"]
["Holford 33/11kV S Stn","Holford33/11kVSStn",210560,1.7,null,430,"",3,"Y"]
["Hollicombe 33/11kV S Stn","Hollicombe33/11kVSStn",340033,0.08,null,23,"",3,"Y"]
["Holsworthy 33/11kV S Stn","Holsworthy33/11kVSStn",350014,0.251,null,402,"",3,"Y"]
["Honiton Heathfield 33/11kV S Stn","HonitonHeathfield33/11kVSStn",310042,0.21099999999999999,null,180,"",3,"Y"]
["Hope Solar Park 33kV S Stn","HopeSolarPark33kVSStn",418029,0.432,null,500,"Y",3,"Y"]
["Horsacott Solar Farm 33kV S Stn","HorsacottSolarFarm33kVSStn",268004,0.17,null,500,"Y",3,"Y"]
["Howton Farm Solar Park 33kV S Stn","HowtonFarmSolarPark33kVSStn",458013,0.57999999999999996,null,1148,"",3,"Y"]
["Huntworth Generator 33kV S Stn","HuntworthGenerator33kVSStn",210270,0.219,null,494.9,"",3,"Y"]
["Hurcott 33kV S Stn","Hurcott33kVSStn",258130,0.55000000000000004,null,500,"Y",3,"Y"]
["Hurcott Solar Park 33kV S Stn","HurcottSolarPark33kVSStn",258127,8.4000000000000005E-2,null,500,"Y",3,"Y"]
["Ilfracombe 33/11kV S Stn","Ilfracombe33/11kVSStn",260230,0.36899999999999999,null,349,"",3,"Y"]
["Indian Queens 400/132kV S Stn","IndianQueens400/132kVSStn",406002,0.2,"Y",3070,"",1,"Y"]
["Iron Acton 275/132kV S Stn","IronActon275/132kVSStn",106009,0.2,"Y",1486,"",1,"Y"]
["Isles Of Scilly 33/11kV S Stn","IslesOfScilly33/11kVSStn",417760,0.52400000000000002,null,214,"",3,"Y"]
["Ivybridge 33/11kV S Stn","Ivybridge33/11kVSStn",330030,0.20200000000000001,null,245,"",3,"Y"]
["Iwood Lane Solar Park 33kV S Stn","IwoodLaneSolarPark33kVSStn",188122,8.5000000000000006E-2,null,500,"Y",3,"Y"]
["Kerriers Solar Park 33kV S Stn","KerriersSolarPark33kVSStn",438099,0.7,"Y",500,"Y",3,"Y"]
["Keynsham East 33/11kV S Stn","KeynshamEast33/11kVSStn",111481,0.108,null,130,"",3,"Y"]
["Keynsham West 33/11kV S Stn","KeynshamWest33/11kVSStn",113180,0.108,null,170,"",3,"Y"]
["Kingsbridge 33/11kV S Stn","Kingsbridge33/11kVSStn",340016,0.18,null,118,"",3,"Y"]
["Kingsland Barton Solar Park 33kV S Stn","KingslandBartonSolarPark33kVSStn",268007,0.29199999999999998,null,500,"Y",3,"Y"]
["Kingsweston 33/11kV S Stn","Kingsweston33/11kVSStn",113339,0.11,null,206,"",3,"Y"]
["Knockworthy Farm Solar Park 33kV S Stn","KnockworthyFarmSolarPark33kVSStn",268001,0.57999999999999996,null,500,"Y",3,"Y"]
["Landulph 132/33kV S Stn","Landulph132/33kVSStn",457710,0.32,null,3050,"",3,"Y"]
["Landulph GSP 400/132kV S Stn","LandulphGSP400/132kVSStn",406003,0.43,null,3182,"",1,"Y"]
["Laneast 33/11kV S Stn","Laneast33/11kVSStn",457620,5.55,null,2270,"",3,"Y"]
["Langage 33/11kV S Stn","Langage33/11kVSStn",330042,0.121,null,157,"",3,"Y"]
["Langage Energy Centre 33kV S Stn","LangageEnergyCentre33kVSStn",330047,0.61699999999999999,null,5577,"",3,"Y"]
["Langunnett Farm Solar Farm 33kV S Stn","LangunnettFarmSolarFarm33kVSStn",438059,0.38,null,500,"Y",3,"Y"]
["Lanner 33/11kV S Stn","Lanner33/11kVSStn",417030,8.4740000000000002,null,4813,"",3,"Y"]
["Lanreath 33/11kV S Stn","Lanreath33/11kVSStn",437460,1.4710000000000001,null,1352,"",3,"Y"]
["Lapford 33/11kV S Stn","Lapford33/11kVSStn",310013,0.73099999999999998,null,681,"",3,"Y"]
["Launceston 33/11kV S Stn","Launceston33/11kVSStn",457250,0.13,null,296,"",3,"Y"]
["Lawes Bridge 33/11kV S Stn","LawesBridge33/11kVSStn",340025,0.26,null,384,"",3,"Y"]
["Lawrence Weston Solar Park 33kV S Stn","LawrenceWestonSolarPark33kVSStn",118166,0.186,null,278.8,"",3,"Y"]
["Laywell 33/11kV S Stn","Laywell33/11kVSStn",341542,0.7,"Y",500,"Y",3,"Y"]
["Laywell Brixham 33/11kV S Stn","LaywellBrixham33/11kVSStn",340035,0.39500000000000002,null,499,"",3,"Y"]
["Lifton 33/11kV S Stn","Lifton33/11kVSStn",330040,0.09,null,58,"",3,"Y"]
["Linketty Lane 33/11kV S Stn","LinkettyLane33/11kVSStn",330029,0.161,null,162,"",3,"Y"]
["Liskeard 33/11kV S Stn","Liskeard33/11kVSStn",457290,0.432,null,638,"",3,"Y"]
["Little Trevease Farm Solar Farm 33kV S Stn","LittleTreveaseFarmSolarFarm33kVSStn",418060,1.79,null,500,"Y",3,"Y"]
["Liverton Farm Solar Park 33kV S Stn","LivertonFarmSolarPark33kVSStn",318110,0.245,null,500,"Y",3,"Y"]
["Lockleaze 132/33/11kV S Stn","Lockleaze132/33/11kVSStn",113370,5.7000000000000002E-2,null,184,"",3,"Y"]
["Lockleaze 33/11kV S Stn","Lockleaze33/11kVSStn",110772,5.7000000000000002E-2,null,21,"",3,"Y"]
["Lockleaze Battery Storage 33kV S Stn","LockleazeBatteryStorage33kVSStn",118179,0.69,null,500,"Y",3,"Y"]
["Longbridge 33/11kV S Stn","Longbridge33/11kVSStn",330024,0.20899999999999999,null,341,"",3,"Y"]
["Looe 33/11kV S Stn","Looe33/11kVSStn",457300,0.94099999999999995,null,1622,"",3,"Y"]
["Lostwithiel 33/11kV S Stn","Lostwithiel33/11kVSStn",437390,1.377,null,1526,"",3,"Y"]
["Lower Tinacre Solar Farm 33kV S Stn","LowerTinacreSolarFarm33kVSStn",358050,0.7,"Y",500,"Y",3,"Y"]
["Luckwell Bridge 33/11kV S Stn","LuckwellBridge33/11kVSStn",210490,4.79,null,2476,"",3,"Y"]
["Luscott Barton Solar Farm 33kV S Stn","LuscottBartonSolarFarm33kVSStn",268078,0.46899999999999997,null,500,"Y",3,"Y"]
["Luxulyan Solar Park 33kV S Stn","LuxulyanSolarPark33kVSStn",438025,1.89,null,500,"Y",3,"Y"]
["Lydeard St Lawrence 33/11kV S Stn","LydeardStLawrence33/11kVSStn",210050,0.86799999999999999,null,1075,"",3,"Y"]
["Lynton 33/11kV S Stn","Lynton33/11kVSStn",260410,4.5,null,2133,"",3,"Y"]
["Lypstone Farm 33/11kV S Stn","LypstoneFarm33/11kVSStn",181216,6.2E-2,null,143,"",3,"Y"]
["Makro Exeter STOR Generator 33kV S Stn","MakroExeterSTORGenerator33kVSStn",318161,0.34499999999999997,null,500,"Y",3,"Y"]
["Mangotsfield 33/11kV S Stn","Mangotsfield33/11kVSStn",111800,9.2999999999999999E-2,null,23,"",3,"Y"]
["Manor Farm Solar Park 33kV S Stn","ManorFarmSolarPark33kVSStn",438011,0.214,null,350,"",3,"Y"]
["Marazion 33/11kV S Stn","Marazion33/11kVSStn",417070,1.347,null,1611,"",3,"Y"]
["Marksbury Solar Park 33kV S Stn","MarksburySolarPark33kVSStn",118117,9.6000000000000002E-2,null,500,"Y",3,"Y"]
["Marlands Fields Creacombe Solar Park 33kV S Stn","MarlandsFieldsCreacombeSolarPark33kVSStn",338185,0.48399999999999999,null,483,"",3,"Y"]
["Marldon 33/11kV S Stn","Marldon33/11kVSStn",340027,0.14899999999999999,null,119,"",3,"Y"]
["Marley Thatch Farm Solar Park 33kV S Stn","MarleyThatchFarmSolarPark33kVSStn",348027,0.76200000000000001,null,500,"Y",3,"Y"]
["Marsh Barton 33/11kV S Stn","MarshBarton33/11kVSStn",310022,0.7,"Y",87,"",3,"Y"]
["Marsh Barton Power Station 132kV S Stn","MarshBartonPowerStation132kVSStn",310006,0.10170999999999999,null,612.70000000000005,"",1,"Y"]
["Marsh Green 33/11kV S Stn","MarshGreen33/11kVSStn",310036,0.82799999999999996,null,800,"",3,"Y"]
["Martock 33/11kV S Stn","Martock33/11kVSStn",250300,0.33600000000000002,null,265,"",3,"Y"]
["Melksham 400/275/132kV S Stn","Melksham400/275/132kVSStn",106010,0.2,"Y",2800,"Y",1,"Y"]
["Merrivale 33/11kV S Stn","Merrivale33/11kVSStn",330017,0.153,null,214,"",3,"Y"]
["Mevagissey 33/11kV S Stn","Mevagissey33/11kVSStn",437400,0.9,null,1128,"",3,"Y"]
["Middle Barlington 33/11kV S Stn","MiddleBarlington33/11kVSStn",260420,2.4500000000000002,null,1581,"",3,"Y"]
["Middle Treworder Farm Solar Park 33kV S Stn","MiddleTreworderFarmSolarPark33kVSStn",438036,0.68100000000000005,null,500,"Y",3,"Y"]
["Midsomer Norton 33/11kV S Stn","MidsomerNorton33/11kVSStn",160423,0.05,null,82,"",3,"Y"]
["Milehouse 132/33kV S Stn","Milehouse132/33kVSStn",330002,0.11700000000000001,null,303,"",3,"Y"]
["Millfield 33/11kV S Stn","Millfield33/11kVSStn",210100,0.189,null,275,"",3,"Y"]
["Modbury 33/11kV S Stn","Modbury33/11kVSStn",340040,0.21299999999999999,null,218,"",3,"Y"]
["Montacute 33/11kV S Stn","Montacute33/11kVSStn",250400,0.42799999999999999,null,537,"",3,"Y"]
["Montys Farm Solar Park 33kV S Stn","MontysFarmSolarPark33kVSStn",218041,0.19700000000000001,null,500,"Y",3,"Y"]
["Mortonhampstead 33/11kV S Stn","Mortonhampstead33/11kVSStn",340012,0.20899999999999999,null,116,"",3,"Y"]
["Morwenstow 33/11kV S Stn","Morwenstow33/11kVSStn",350024,2.09,null,2036,"",3,"Y"]
["Mousehole 33/11kV S Stn","Mousehole33/11kVSStn",417340,3.3639999999999999,null,2301,"",3,"Y"]
["Mullion 33/11kV S Stn","Mullion33/11kVSStn",417780,0.443,null,338,"",3,"Y"]
["Nailsea 33/11kV S Stn","Nailsea33/11kVSStn",181000,0.23499999999999999,null,404,"",3,"Y"]
["Nancrossa Solar Park 33kV S Stn","NancrossaSolarPark33kVSStn",418163,1.9279999999999999,null,500,"Y",3,"Y"]
["Nanteague Solar Park 33kV S Stn","NanteagueSolarPark33kVSStn",418101,0.75,null,500,"Y",3,"Y"]
["Nether Mill Farm Solar Park 33kV S Stn","NetherMillFarmSolarPark33kVSStn",318032,0.7,"Y",500,"Y",3,"Y"]
["Nether Stowey 33/11kV S Stn","NetherStowey33/11kVSStn",210130,0.443,null,269,"",3,"Y"]
["Newbury 33/11kV S Stn","Newbury33/11kVSStn",161701,0.97099999999999997,null,1035,"",3,"Y"]
["Newlands Farm Solar Park 33kV S Stn","NewlandsFarmSolarPark33kVSStn",258062,0.23,null,500,"Y",3,"Y"]
["Newlyn 33/11kV S Stn","Newlyn33/11kVSStn",417690,0.55100000000000005,null,1160,"",3,"Y"]
["Newnham Farm Solar Park 33kV S Stn","NewnhamFarmSolarPark33kVSStn",338133,0.56000000000000005,null,500,"Y",3,"Y"]
["Newport Street 33/11kV S Stn","NewportStreet33/11kVSStn",330015,0.55300000000000005,null,147,"",3,"Y"]
["Newquay Trencreek Ln 33/11kV S Stn","NewquayTrencreekLn33/11kVSStn",437610,0.46899999999999997,null,463,"",3,"Y"]
["Newquay Trevemper 33/11kV S Stn","NewquayTrevemper33/11kVSStn",437220,0.66600000000000004,null,1010,"",3,"Y"]
["New Rendy Farm Solar Farm 33kV S Stn","NewRendyFarmSolarFarm33kVSStn",218000,0.11600000000000001,null,500,"Y",3,"Y"]
["New Row Farm Solar Park 33kV S Stn","NewRowFarmSolarPark33kVSStn",168104,0.66600000000000004,null,500,"Y",3,"Y"]
["Newton Abbot 132/33/11kV S Stn","NewtonAbbot132/33/11kVSStn",340001,0.11,null,405,"",3,"Y"]
["Newton Abbot Main 33/11kV S Stn","NewtonAbbotMain33/11kVSStn",340019,8.5000000000000006E-2,null,23,"",3,"Y"]
["Newton Barton Solar Park 33kV S Stn","NewtonBartonSolarPark33kVSStn",458128,0.32,null,500,"Y",3,"Y"]
["Newton Downs Solar Park 33kV S Stn","NewtonDownsSolarPark33kVSStn",338190,0.46,null,457,"",3,"Y"]
["Newton Ferrers 33/11kV S Stn","NewtonFerrers33/11kVSStn",330032,0.46,null,457,"",3,"Y"]
["Newton Poppleford 33/11kV S Stn","NewtonPoppleford33/11kVSStn",310045,0.34,null,284,"",3,"Y"]
["Newton St Cyres 33/11kV S Stn","NewtonStCyres33/11kVSStn",310012,0.72699999999999998,null,1246,"",3,"Y"]
["Ninnis Solar Farm 33kV S Stn","NinnisSolarFarm33kVSStn",438051,0.26500000000000001,null,459,null,3,"Y"]
["Norrington 132/33kV S Stn","Norrington132/33kVSStn",104098,0.2,"Y",1400,"Y",3,"Y"]
["Northam 33/11kV S Stn","Northam33/11kVSStn",350016,0.11600000000000001,null,126,"",3,"Y"]
["North Intake 33kV S Stn","NorthIntake33kVSStn",330039,0.22,null,297,"",3,"Y"]
["Northmoor Solar Park 132kV S Stn","NorthmoorSolarPark132kVSStn",358116,0.92,null,1400,"Y",1,"Y"]
["North Street Langport 33/11kV S Stn","NorthStreetLangport33/11kVSStn",210090,0.1,null,169,"",3,"Y"]
["North Tawton 132/33kV S Stn","NorthTawton132/33kVSStn",310007,0.20399999999999999,null,255,"",3,"Y"]
["North Tawton 33/11kV S Stn","NorthTawton33/11kVSStn",310058,0.20399999999999999,null,105,"",3,"Y"]
["North Wayton Solar Park 33kV S Stn","NorthWaytonSolarPark33kVSStn",458097,0.28399999999999997,null,500,"Y",3,"Y"]
["Northwood Solar Park 33kV S Stn","NorthwoodSolarPark33kVSStn",118115,0.14000000000000001,null,500,"Y",3,"Y"]
["Oakham Farm Solar Park 33kV S Stn","OakhamFarmSolarPark33kVSStn",118157,0.14399999999999999,null,500,"Y",3,"Y"]
["Offwell 33/11kV S Stn","Offwell33/11kVSStn",310041,1.2410000000000001,null,1452,"",3,"Y"]
["Okehampton 33/11kV S Stn","Okehampton33/11kVSStn",350050,0.23,null,216,"",3,"Y"]
["Oldfield Park33/ 6.6kV S Stn","OldfieldPark33/6.6kVSStn",160050,0.26100000000000001,null,86,"",3,"Y"]
["Old Green Generation Station 132kV S Stn","OldGreenGenerationStation132kVSStn",118180,0.114,null,1400,"Y",1,"Y"]
["Old Laira Road 33/11kV S Stn","OldLairaRoad33/11kVSStn",330026,0.65200000000000002,null,266,"",3,"Y"]
["Old Stone Farm Solar Park 33kV S Stn","OldStoneFarmSolarPark33kVSStn",348175,1.3019229999999999,null,500,"Y",3,"Y"]
["Otterham Wind Farm 132kV S Stn","OtterhamWindFarm132kVSStn",458109,0.2,null,1400,"Y",1,"Y"]
["Ottery St Mary 33/11kV S Stn","OtteryStMary33/11kVSStn",310043,0.442,null,487,"",3,"Y"]
["Outlands Wood Solar Park 33kV S Stn","OutlandsWoodSolarPark33kVSStn",438092,0.434,null,500,"Y",3,"Y"]
["Padstow 33/11kV S Stn","Padstow33/11kVSStn",437430,1.21,null,975,"",3,"Y"]
["Paignton 132/33kV S Stn","Paignton132/33kVSStn",340002,0.42799999999999999,null,823,"",3,"Y"]
["Paignton 33/11kV S Stn","Paignton33/11kVSStn",340042,0.42799999999999999,null,823,"",3,"Y"]
["Par Harbour 33/11kV S Stn","ParHarbour33/11kVSStn",437670,0.22800000000000001,null,350,"",3,"Y"]
["Park Lane 33/11kV S Stn","ParkLane33/11kVSStn",350017,7.3999999999999996E-2,null,83,"",3,"Y"]
["Park Street 33/6.6kV S Stn","ParkStreet33/6.6kVSStn",160060,3.1E-2,null,21,"",3,"Y"]
["Parkview Solar Park 33kV S Stn","ParkviewSolarPark33kVSStn",348134,0.63,null,500,"Y",3,"Y"]
["Park Wall Solar Park 33kV S Stn","ParkWallSolarPark33kVSStn",218002,9.4E-2,null,500,"Y",3,"Y"]
["Parsonage Barn Solar Park 33kV S Stn","ParsonageBarnSolarPark33kVSStn",258065,0.16,null,500,"Y",3,"Y"]
["Patchway 33/11kV S Stn","Patchway33/11kVSStn",114741,0.62,null,500,"Y",3,"Y"]
["Paulton 33/11kV S Stn","Paulton33/11kVSStn",161315,0.19700000000000001,null,127,"",3,"Y"]
["Peasedown 33/11kV S Stn","Peasedown33/11kVSStn",162406,0.10199999999999999,null,113,"",3,"Y"]
["Penare Farm Solar Farm 33kV S Stn","PenareFarmSolarFarm33kVSStn",418069,0.41,null,500,"Y",3,"Y"]
["Pencoose Solar Park 33kV S Stn","PencooseSolarPark33kVSStn",418125,1.26,null,500,"Y",3,"Y"]
["Penhale Solar Farm 33kV S Stn","PenhaleSolarFarm33kVSStn",438039,0.8,null,500,"Y",3,"Y"]
["Penn Cross 33/11kV S Stn","PennCross33/11kVSStn",250320,0.29199999999999998,null,455,"",3,"Y"]
["Penryn 33/11kV S Stn","Penryn33/11kVSStn",417170,0.99399999999999999,null,1552,"",3,"Y"]
["Pensilva 33/11kV S Stn","Pensilva33/11kVSStn",457470,5.0110000000000001,null,3403,"",3,"Y"]
["Penzance Causewayhead 33/11kV S Stn","PenzanceCausewayhead33/11kVSStn",417580,0.112,null,149,"",3,"Y"]
["Penzance Heamoor 33/11kV S Stn","PenzanceHeamoor33/11kVSStn",417080,0.32300000000000001,null,627,"",3,"Y"]
["Periton 33/11kV S Stn","Periton33/11kVSStn",210180,0.255,null,172,"",3,"Y"]
["Perranporth 33/11kV S Stn","Perranporth33/11kVSStn",417100,4.29,null,3693,"",3,"Y"]
["Pinhoe 33/11kV S Stn","Pinhoe33/11kVSStn",310026,5.0999999999999997E-2,null,31,"",3,"Y"]
["Pitts Farm Solar Park 33kV S Stn","PittsFarmSolarPark33kVSStn",168105,0.65600000000000003,null,500,"Y",3,"Y"]
["Pitworthy Solar Park 33kV S Stn","PitworthySolarPark33kVSStn",358074,0.33700000000000002,null,500,"Y",3,"Y"]
["Place Barton Farm Solar Park 33kV S Stn","PlaceBartonFarmSolarPark33kVSStn",348176,0.89551000000000003,null,500,"Y",3,"Y"]
["Plymouth 132/33kV S Stn","Plymouth132/33kVSStn",330003,8.5999999999999993E-2,null,43,"",3,"Y"]
["Plymouth BSP 33kV S Stn","PlymouthBSP33kVSStn",330045,8.5999999999999993E-2,null,43,"",3,"Y"]
["Plympton 132/33kV S Stn","Plympton132/33kVSStn",330006,0.67900000000000005,null,764,"",3,"Y"]
["Plymstock South 33/11kV S Stn","PlymstockSouth33/11kVSStn",330037,0.157,null,229,"",3,"Y"]
["Polzeath 33/11kV S Stn","Polzeath33/11kVSStn",437550,2.573,null,2560,"",3,"Y"]
["Portishead 132/33kV S Stn","Portishead132/33kVSStn",182800,5.8999999999999997E-2,null,118,"",3,"Y"]
["Portishead Ashlands 33/11kV S Stn","PortisheadAshlands33/11kVSStn",182983,5.8999999999999997E-2,null,423,"",3,"Y"]
["Portworthy Dams Solar Park 33kV S Stn","PortworthyDamsSolarPark33kVSStn",338151,0.31,null,500,"Y",3,"Y"]
["Prince Rock 33/11kV S Stn","PrinceRock33/11kVSStn",330027,0.7,"Y",500,"Y",3,"Y"]
["Priorswood 33/11kV S Stn","Priorswood33/11kVSStn",210040,7.4999999999999997E-2,null,112,"",3,"Y"]
["Probus 33/11kV S Stn","Probus33/11kVSStn",417560,2.69,null,1783,"",3,"Y"]
["Puriton Landfill Solar Park 33kV S Stn","PuritonLandfillSolarPark33kVSStn",218025,0.115,null,500,"Y",3,"Y"]
["Pylle Solar Park 33kV S Stn","PylleSolarPark33kVSStn",168138,0.17699999999999999,null,500,"Y",3,"Y"]
["Pyworthy 132/33kV S Stn","Pyworthy132/33kVSStn",350001,0.57199999999999995,null,904,"",3,"Y"]
["Quartley 33kV S Stn","Quartley33kVSStn",210540,3.95,null,2386,"",3,"Y"]
["R.O.F. Power House 33kV S Stn","R.O.F.PowerHouse33kVSStn",210999,6.2E-2,null,93,"",3,"Y"]
["Radstock 132/33kV S Stn","Radstock132/33kVSStn",162633,0.25700000000000001,null,247,"",3,"Y"]
["Rame132/33kV S Stn","Rame132/33kVSStn",417500,1.7230000000000001,null,2340,"",3,"Y"]
["Red Hill Solar Park 33kV S Stn","RedHillSolarPark33kVSStn",318155,0.27100000000000002,null,500,"Y",3,"Y"]
["Redlands Farm Solar Park 33kV S Stn","RedlandsFarmSolarPark33kVSStn",218017,0.13,null,500,"Y",3,"Y"]
["Redruth 33/11kV S Stn","Redruth33/11kVSStn",417110,0.42599999999999999,null,849,"",3,"Y"]
["Rew Farm Solar Park 33kV S Stn","RewFarmSolarPark33kVSStn",438037,0.57999999999999996,null,500,"Y",3,"Y"]
["Rexon Cross Farm Solar Park 33kV S Stn","RexonCrossFarmSolarPark33kVSStn",358064,0.45800000000000002,null,500,"Y",3,"Y"]
["Roadford 33kV S Stn","Roadford33kVSStn",350023,0.41,null,406,"",3,"Y"]
["Rockhead Wind Farm 33kV S Stn","RockheadWindFarm33kVSStn",438018,1.133,null,1176,"",3,"Y"]
["Rockingham 33kV S Stn","Rockingham33kVSStn",118183,0.23,null,500,"Y",3,"Y"]
["Rock Park 132/33/11kV S Stn","RockPark132/33/11kVSStn",260590,6.2E-2,null,116,"",3,"Y"]
["Rolls Royce Filton 132kV S Stn","RollsRoyceFilton132kVSStn",114059,0.13300000000000001,null,291,"",1,"Y"]
["Rookery Farm Solar Park 33kV S Stn","RookeryFarmSolarPark33kVSStn",188139,0.254,null,500,"Y",3,"Y"]
["Roseland 33/11kV S Stn","Roseland33/11kVSStn",417120,3.1789999999999998,null,2241,"",3,"Y"]
["Roskrow Barton Solar Park 33kV S Stn","RoskrowBartonSolarPark33kVSStn",418135,0.7,null,500,"Y",3,"Y"]
["Roundswell 33/11kV S Stn","Roundswell33/11kVSStn",260240,0.14000000000000001,null,133,"",3,"Y"]
["Royal Portbury Dock 33/11kV S Stn","RoyalPortburyDock33/11kVSStn",182150,5.0999999999999997E-2,null,20,"",3,"Y"]
["Rydon Farm Solar Park 33kV S Stn","RydonFarmSolarPark33kVSStn",348121,8.5999999999999993E-2,null,500,"Y",3,"Y"]
["Salcombe 33/11kV S Stn","Salcombe33/11kVSStn",340038,0.20100000000000001,null,270,"",3,"Y"]
["Saltash Dunheved Rd 33/11kV S Stn","SaltashDunhevedRd33/11kVSStn",457520,0.27500000000000002,null,271,"",3,"Y"]
["Saltash Whity Cross 33/11kV S Stn","SaltashWhityCross33/11kVSStn",457280,3.0339999999999998,null,3501,"",3,"Y"]
["Sawles Road 33/11kV S Stn","SawlesRoad33/11kVSStn",437640,0.28899999999999998,null,252,"",3,"Y"]
["Seabank 132/33kV S Stn","Seabank132/33kVSStn",114259,8.5999999999999993E-2,null,695,"",3,"Y"]
["Seabank 400/132kV S Stn","Seabank400/132kVSStn",114023,8.5999999999999993E-2,null,1274,"",1,"Y"]
["Severnside Energy Recovery Centre 132kV S Stn","SevernsideEnergyRecoveryCentre132kVSStn",114756,0.125,null,1400,"Y",1,"Y"]
["Shapwick 33/11kV S Stn","Shapwick33/11kVSStn",210460,0.61399999999999999,null,1166,"",3,"Y"]
["Sharland Farm Solar Park 33kV S Stn","SharlandFarmSolarPark33kVSStn",318172,0.219,null,500,"Y",3,"Y"]
["Shebbear 33/11kV S Stn","Shebbear33/11kVSStn",350013,2.5,null,1853,"",3,"Y"]
["Shepton Mallet 33/11kV S Stn","SheptonMallet33/11kVSStn",161641,0.192,null,251,"",3,"Y"]
["Sherford IDNO Connection 33kV S Stn","SherfordIDNOConnection33kVSStn",338181,0.51800000000000002,null,500,"Y",3,"Y"]
["Shooters Bottom Solar Park 33kV S Stn","ShootersBottomSolarPark33kVSStn",168001,0.90400000000000003,null,500,"Y",3,"Y"]
["Shooters Bottom W/F 33kV S Stn","ShootersBottomW/F33kVSStn",162888,1.2,null,1464,"",3,"Y"]
["Sidmouth Town 33/11kV S Stn","SidmouthTown33/11kVSStn",310046,0.124,null,110,"",3,"Y"]
["Slade Farm Solar Park 33kV S Stn","SladeFarmSolarPark33kVSStn",348033,0.498,null,500,"Y",3,"Y"]
["Somerton 33/11kV S Stn","Somerton33/11kVSStn",210080,0.06,null,69,"",3,"Y"]
["Somerton Door Solar Park 33kV S Stn","SomertonDoorSolarPark33kVSStn",218019,7.8E-2,null,500,"Y",3,"Y"]
["South Brent 33/11kV S Stn","SouthBrent33/11kVSStn",340015,0.5,null,671,"",3,"Y"]
["South Molton 33/11kV S Stn","SouthMolton33/11kVSStn",260260,1.1100000000000001,null,1095,"",3,"Y"]
["Southway 33/11kV S Stn","Southway33/11kVSStn",330023,0.245,null,70,"",3,"Y"]
["Sowton 132/33/11kV S Stn","Sowton132/33/11kVSStn",310005,0.1,null,643,"",3,"Y"]
["Sowton 33/11kV S Stn","Sowton33/11kVSStn",310028,0.1,null,20,"",3,"Y"]
["Sowton B 33/11kV S Stn","SowtonB33/11kVSStn",310059,0.1,null,500,"Y",3,"Y"]
["St Agnes 33/11kV S Stn","StAgnes33/11kVSStn",417590,4.59,null,2528,"",3,"Y"]
["Stancombe Quarry 33kV S Stn","StancombeQuarry33kVSStn",182768,1.0840000000000001,null,1444,"",3,"Y"]
["Staplegrove 33/11kV S Stn","Staplegrove33/11kVSStn",210500,0.14799999999999999,null,183,"",3,"Y"]
["Staplehill 33kV S Stn","Staplehill33kVSStn",114393,0.43,null,132,"",3,"Y"]
["St Austell  33/11kV S Stn","StAustell33/11kVSStn",437190,0.77,null,1482,"",3,"Y"]
["St Austell BSP 132/33kV S Stn","StAustellBSP132/33kVSStn",437730,0.629,null,775,"",3,"Y"]
["St Blazey 33kV S Stn","StBlazey33kVSStn",437200,0.443,null,678,"",3,"Y"]
["St Breock 33kV S Stn","StBreock33kVSStn",437790,0.83,null,425,"",3,"Y"]
["St Buryan 33/11kV S Stn","StBuryan33/11kVSStn",417090,6.9039999999999999,null,4163,"",3,"Y"]
["St Columb Major 33/11kV S Stn","StColumbMajor33/11kVSStn",437490,1.591,null,1632,"",3,"Y"]
["St Day Landfill 33kV S Stn","StDayLandfill33kVSStn",417670,0.63,null,419,"",3,"Y"]
["Stentaway 33/11kV S Stn","Stentaway33/11kVSStn",330031,8.6999999999999994E-2,null,73,"",3,"Y"]
["St Germans 132/33kV S Stn","StGermans132/33kVSStn",457510,0.95299999999999996,null,3810,"",3,"Y"]
["St Ives 33/11kV S Stn","StIves33/11kVSStn",417130,3.37,null,5220,"",3,"Y"]
["St Keverne 33/11kV S Stn","StKeverne33/11kVSStn",417330,4.3120000000000003,null,4271,"",3,"Y"]
["St Levan Road 33/11kV S Stn","StLevanRoad33/11kVSStn",330013,8.7999999999999995E-2,null,130,"",3,"Y"]
["St Mawgan 33/11kV S Stn","StMawgan33/11kVSStn",437440,0.76800000000000002,null,658,"",3,"Y"]
["St Neot 33/11kV S Stn","StNeot33/11kVSStn",457480,3.91,null,2491,"",3,"Y"]
["Stoke Bishop 33/11kV S Stn","StokeBishop33/11kVSStn",112389,0.12,null,500,"Y",3,"Y"]
["Stokenham 33/11kV S Stn","Stokenham33/11kVSStn",340041,0.45500000000000002,null,348,"",3,"Y"]
["Stonebarrow Farm Solar Farm 33kV S Stn","StonebarrowFarmSolarFarm33kVSStn",258073,0.151,null,500,"Y",3,"Y"]
["Stoneshill Solar Park 33kV S Stn","StoneshillSolarPark33kVSStn",318173,0.19600000000000001,null,500,"Y",3,"Y"]
["St Pauls 132/11kV S Stn","StPauls132/11kVSStn",113450,0.06,null,314,"",1,"Y"]
["St Pauls BSP 132/11kV S Stn","StPaulsBSP132/11kVSStn",110804,0.06,null,43,"",1,"Y"]
["Stratton 33/11kV S Stn","Stratton33/11kVSStn",350012,0.36699999999999999,null,595,"",3,"Y"]
["Street 132/33kV S Stn","Street132/33kVSStn",210448,0.28000000000000003,null,580,"",3,"Y"]
["St Stephen Solar Park 33kV S Stn","StStephenSolarPark33kVSStn",438094,0.36199999999999999,null,500,"Y",3,"Y"]
["St Thomas 33/11kV S Stn","StThomas33/11kVSStn",310017,3.4000000000000002E-2,null,11,"",3,"Y"]
["St Tudy 132/33kV S Stn","StTudy132/33kVSStn",407450,1.069,null,1110,"",3,"Y"]
["St Tudy 33/11kV S Stn","StTudy33/11kVSStn",437450,1.069,null,2071,"",3,"Y"]
["Tamar Pumping Station 33kV S Stn","TamarPumpingStation33kVSStn",330044,1.46,null,1508,"",3,"Y"]
["Tamerton Bridge STOR Generator 33kV S Stn","TamertonBridgeSTORGenerator33kVSStn",338169,1.2949999999999999,null,500,"Y",3,"Y"]
["Taunton Local 33/11kV S Stn","TauntonLocal33/11kVSStn",210010,4.7E-2,null,24,"",3,"Y"]
["Taunton Main 132/33kV S Stn","TauntonMain132/33kVSStn",210612,0.08,null,3500,"",3,"Y"]
["Taunton Main 400/132kV S Stn","TauntonMain400/132kVSStn",206007,0.2,"Y",3500,"",1,"Y"]
["Tavistock 33/11kV S Stn","Tavistock33/11kVSStn",330011,0.53400000000000003,null,737,"",3,"Y"]
["Teignmouth Gas Works 33/11kV S Stn","TeignmouthGasWorks33/11kVSStn",340017,6.7000000000000004E-2,null,36,"",3,"Y"]
["Tengore Lane Solar Park 33kV S Stn","TengoreLaneSolarPark33kVSStn",218018,0.1,null,500,"Y",3,"Y"]
["Till House Solar Park 33kV S Stn","TillHouseSolarPark33kVSStn",318090,0.17699999999999999,null,500,"Y",3,"Y"]
["Tinkers Cross 33/11kV S Stn","TinkersCross33/11kVSStn",260440,1.593,null,1284,"",3,"Y"]
["Tiverton 132/33/11kV S Stn","Tiverton132/33/11kVSStn",310002,0.187,null,257,"",3,"Y"]
["Tiverton Junction 132/33/11kV S Stn","TivertonJunction132/33/11kVSStn",310032,0.187,null,257,"",3,"Y"]
["Tiverton Moorhayes 33/11kV S Stn","TivertonMoorhayes33/11kVSStn",310023,0.19900000000000001,null,220,"",3,"Y"]
["Tiverton South 33/11kV S Stn","TivertonSouth33/11kVSStn",310025,7.9000000000000001E-2,null,87,"",3,"Y"]
["Tonedale Farm Solar Park 33kV S Stn","TonedaleFarmSolarPark33kVSStn",218032,0.23100000000000001,null,500,"Y",3,"Y"]
["Topsham 33/11kV S Stn","Topsham33/11kVSStn",310031,0.32400000000000001,null,302,"",3,"Y"]
["Torpoint Antony 33/11kV S Stn","TorpointAntony33/11kVSStn",457240,1.39,null,1936,"",3,"Y"]
["Torpoint Town 33/11kV S Stn","TorpointTown33/11kVSStn",457530,0.245,null,290,"",3,"Y"]
["Torquay 132/33kV S Stn","Torquay132/33kVSStn",340003,0.11799999999999999,null,38,"",3,"Y"]
["Torwood 33/11kV S Stn","Torwood33/11kVSStn",340032,8.3000000000000004E-2,null,37,"",3,"Y"]
["Torycombe 33/11kV S Stn","Torycombe33/11kVSStn",330028,0.32200000000000001,null,284,"",3,"Y"]
["Totnes 33/11kV S Stn","Totnes33/11kVSStn",340021,0.04,null,46,"",3,"Y"]
["Totnes BSP 132/33kV S Stn","TotnesBSP132/33kVSStn",340004,0.59599999999999997,null,3699,"",3,"Y"]
["Towerhead Farm Solar Park 33kV S Stn","TowerheadFarmSolarPark33kVSStn",188140,0.1,null,500,"Y",3,"Y"]
["Trebal 33/11kV S Stn","Trebal33/11kVSStn",437720,1.7050000000000001,null,1755,"",3,"Y"]
["Trefinnick Farm Solar Farm 33kV S Stn","TrefinnickFarmSolarFarm33kVSStn",458058,0.39,null,500,"Y",3,"Y"]
["Tregarrick Farm Solar Park 33kV S Stn","TregarrickFarmSolarPark33kVSStn",438088,0.7,"Y",500,"Y",3,"Y"]
["Tregassow Solar Farm 33kV S Stn","TregassowSolarFarm33kVSStn",418070,0.71,null,500,"Y",3,"Y"]
["Trehawke Farm Solar Park 33kV S Stn","TrehawkeFarmSolarPark33kVSStn",458082,0.308,null,500,"Y",3,"Y"]
["Trekenning Farm Solar Park 33kV S Stn","TrekenningFarmSolarPark33kVSStn",438040,0.39,null,500,"Y",3,"Y"]
["Treningle 33kV S Stn","Treningle33kVSStn",437750,2.0699999999999998,null,1888,"",3,"Y"]
["Trenouth Farm Solar Park 33kV S Stn","TrenouthFarmSolarPark33kVSStn",438010,0.8,null,735,"",3,"Y"]
["Trequite Solar Farm 33kV S Stn","TrequiteSolarFarm33kVSStn",458052,0.57899999999999996,null,500,"Y",3,"Y"]
["Trerule Solar Park 33kV S Stn","TreruleSolarPark33kVSStn",458162,0.29699999999999999,null,500,"",3,"Y"]
["Trewidland Farm Solar Park 33kV S Stn","TrewidlandFarmSolarPark33kVSStn",458095,0.34799999999999998,null,500,"Y",3,"Y"]
["Tricky Warren 33kV S Stn","TrickyWarren33kVSStn",218039,0.25,null,500,"Y",3,"Y"]
["Tricky Warren Solar Park 33kV S Stn","TrickyWarrenSolarPark33kVSStn",218020,0.25,null,500,"Y",3,"Y"]
["Trull 33/11kV S Stn","Trull33/11kVSStn",210020,0.06,null,46,"",3,"Y"]
["Truro 132/33kV S Stn","Truro132/33kVSStn",417740,0.99,null,946,"",3,"Y"]
["Truro Shortlanesend 33/11kV S Stn","TruroShortlanesend33/11kVSStn",417140,3.4020000000000001,null,3742,"",3,"Y"]
["Truro Treyew Road 33/11kV S Stn","TruroTreyewRoad33/11kVSStn",417600,0.224,null,343,"",3,"Y"]
["Twelveheads 33/11kV S Stn","Twelveheads33/11kVSStn",417680,7.48,null,5739,"",3,"Y"]
["Twerton 33/6.6kV S Stn","Twerton33/6.6kVSStn",160390,0.08,null,119,"",3,"Y"]
["University Of Bath 33/11kV S Stn","UniversityOfBath33/11kVSStn",164210,0.11700000000000001,null,500,"Y",3,"Y"]
["Upton Valley 33/11kV S Stn","UptonValley33/11kVSStn",340026,6.9000000000000006E-2,null,20,"",3,"Y"]
["Victoria Wind Farm 33kV S Stn","VictoriaWindFarm33kVSStn",438107,1.121,null,500,"Y",3,"Y"]
["Viridor Waste To Energy 33kV S Stn","ViridorWasteToEnergy33kVSStn",118184,9.2999999999999999E-2,null,500,"Y",3,"Y"]
["Wadebridge 33/11kV S Stn","Wadebridge33/11kVSStn",437210,3.92,null,3775,"",3,"Y"]
["Walland Farm Solar Park 33kV S Stn","WallandFarmSolarPark33kVSStn",358129,0.3,null,500,"Y",3,"Y"]
["Wansbrough Paper Mill 33kV S Stn","WansbroughPaperMill33kVSStn",210670,7.8E-2,null,105,"",3,"Y"]
["Warleigh Barton Solar Park 33kV S Stn","WarleighBartonSolarPark33kVSStn",338028,0.63400000000000001,null,500,"Y",3,"Y"]
["Watchfield 33/11kV S Stn","Watchfield33/11kVSStn",210150,0.09,null,263,"",3,"Y"]
["Watchfield Lawn Solar Park 33kV S Stn","WatchfieldLawnSolarPark33kVSStn",218016,0.7,"Y",500,"Y",3,"Y"]
["Waterlake 33/11kV S Stn","Waterlake33/11kVSStn",250330,0.15,null,220,"",3,"Y"]
["Water Lane STOR Generator 33kV S Stn","WaterLaneSTORGenerator33kVSStn",318165,0.49,null,500,"Y",3,"Y"]
["Wedmore 33/11kV S Stn","Wedmore33/11kVSStn",181817,0.123,null,217,"",3,"Y"]
["Week Farm Solar Park 33kV S Stn","WeekFarmSolarPark33kVSStn",268008,0.43,null,500,"Y",3,"Y"]
["Wellington 33/11kV S Stn","Wellington33/11kVSStn",210200,0.44,null,903,"",3,"Y"]
["Wellington Town 33/11kV S Stn","WellingtonTown33/11kVSStn",210380,0.28799999999999998,null,166,"",3,"Y"]
["Wells 33/11kV S Stn","Wells33/11kVSStn",160824,0.14799999999999999,null,129,"",3,"Y"]
["West Carclaze Solar Park 33kV S Stn","WestCarclazeSolarPark33kVSStn",438156,0.78,null,500,"Y",3,"Y"]
["Western Approach 33/11kV S Stn","WesternApproach33/11kVSStn",114434,0.1,null,200,"",3,"Y"]
["West Hill Solar Farm 33kV S Stn","WestHillSolarFarm33kVSStn",268002,0.66,null,500,"Y",3,"Y"]
["Weston 132/33kV S Stn","Weston132/33kVSStn",182372,6.2E-2,null,174,"",3,"Y"]
["Weston Central 33/11kV S Stn","WestonCentral33/11kVSStn",181360,0.30299999999999999,null,135,"",3,"Y"]
["Weston-In-Gordano 33/11kV S Stn","Weston-In-Gordano33/11kVSStn",180820,0.17199999999999999,null,351,"",3,"Y"]
["Weston Locking Road 33/11kV S Stn","WestonLockingRoad33/11kVSStn",180092,6.2E-2,null,128,"",3,"Y"]
["Weston Mill 33/11kV S Stn","WestonMill33/11kVSStn",330012,0.14799999999999999,null,205,"",3,"Y"]
["West Wick 33/11kV S Stn","WestWick33/11kVSStn",182982,0.158,null,316,"",3,"Y"]
["Whatley Quarry 33/11kV S Stn","WhatleyQuarry33/11kVSStn",160739,0.91700000000000004,null,569,"",3,"Y"]
["Wheal Reeth 33/11kV S Stn","WhealReeth33/11kVSStn",417060,4.51,null,2500,"",3,"Y"]
["Whiddon Down 33/11kV S Stn","WhiddonDown33/11kVSStn",350021,2.2200000000000002,null,1725,"",3,"Y"]
["Whitchurch 33/11kV S Stn","Whitchurch33/11kVSStn",112272,4.2000000000000003E-2,null,13,"",3,"Y"]
["Whitchurch Farm Solar Park 33kV S Stn","WhitchurchFarmSolarPark33kVSStn",168000,0.20300000000000001,null,500,"Y",3,"Y"]
["Whitley Farm Solar Farm 33kV S Stn","WhitleyFarmSolarFarm33kVSStn",218075,0.7,"Y",500,"Y",3,"Y"]
["Wick Farm Solar Park 33kV S Stn","WickFarmSolarPark33kVSStn",188150,7.0000000000000007E-2,null,500,"Y",3,"Y"]
["Wick Farm West Solar Park 33kV S Stn","WickFarmWestSolarPark33kVSStn",188168,0.11,null,500,"Y",3,"Y"]
["Willsland Solar Park 33kV S Stn","WillslandSolarPark33kVSStn",358067,0.7,"Y",500,"Y",3,"Y"]
["Wilton 33kV S Stn","Wilton33kVSStn",458145,0.95299999999999996,null,500,"Y",3,"Y"]
["Wilton Farm Solar Park 33kV S Stn","WiltonFarmSolarPark33kVSStn",458142,1.0369999999999999,null,500,"Y",3,"Y"]
["Wilton Farm Wind Farm 33kV S Stn","WiltonFarmWindFarm33kVSStn",458147,1.01,null,500,"Y",3,"Y"]
["Winnards Perch Solar Farm 33kV S Stn","WinnardsPerchSolarFarm33kVSStn",438038,0.38,null,500,"Y",3,"Y"]
["Winscombe 33/11kV S Stn","Winscombe33/11kVSStn",180952,0.21199999999999999,null,428,"",3,"Y"]
["Winslakefoot 33kV S Stn","Winslakefoot33kVSStn",310047,0.55000000000000004,null,553,"",3,"Y"]
["Winterbourne 33/11kV S Stn","Winterbourne33/11kVSStn",112130,0.30099999999999999,null,474,"",3,"Y"]
["Winterbourne Abbas 33kV S Stn","WinterbourneAbbas33kVSStn",200433,0.7,"Y",500,"Y",3,"Y"]
["Witheridge 33/11kV S Stn","Witheridge33/11kVSStn",310011,3.806,null,3342,"",3,"Y"]
["Withycombe Raleigh 33/11kV S Stn","WithycombeRaleigh33/11kVSStn",310037,4.4999999999999998E-2,null,14,"",3,"Y"]
["Withy Drove Solar Park 33kV S Stn","WithyDroveSolarPark33kVSStn",218040,6.3E-2,null,500,"Y",3,"Y"]
["Wiveliscombe 33/11kV S Stn","Wiveliscombe33/11kVSStn",210070,2.06,null,2616,"",3,"Y"]
["Woodbury 33/11kV S Stn","Woodbury33/11kVSStn",310035,0.74,null,842,"",3,"Y"]
["Woodcote 132/33kV S Stn","Woodcote132/33kVSStn",250437,0.17699999999999999,null,283,"",3,"Y"]
["Woodland Barton Solar Park 33kV S Stn","WoodlandBartonSolarPark33kVSStn",438024,0.71,null,500,"Y",3,"Y"]
["Woodland Way 33/11kV S Stn","WoodlandWay33/11kVSStn",110375,8.7999999999999995E-2,null,151,"",3,"Y"]
["Woolavington Solar Park 33kV S Stn","WoolavingtonSolarPark33kVSStn",218005,4.2999999999999997E-2,null,500,"Y",3,"Y"]
["Wyld Meadow Solar Park 33kV S Stn","WyldMeadowSolarPark33kVSStn",258023,0.15,null,500,"Y",3,"Y"]
["Yelverton 33/11kV S Stn","Yelverton33/11kVSStn",330016,0.42699999999999999,null,445,"",3,"Y"]
["Yeovil 33kV S Stn","Yeovil33kVSStn",200435,0.7,"Y",500,"Y",3,"Y"]
["Yonder Netherton 33kV Solar Farm 33/11kV S Stn","YonderNetherton33kVSolarFarm33/11kVSStn",458053,0.7,"Y",500,"Y",3,"Y"]
["Yonder Parks Solar Park 33kV S Stn","YonderParksSolarPark33kVSStn",348111,0.86,null,500,"Y",3,"Y"]

{"sheet":"Source-SWA-Num","index":16,"n_rows":350,"n_cols":8,"rows_kept":350,"cut":false,"hidden":true,"merged":[]}
[1,2,3,4,5,6,7,8]
["SUBSTATION_NUMBER_SWA","SUBSTATION_NAME","ZE","Assumed ZE","UE","Assumed UE","t","Assumed t"]
[510006,"Cardiff Central Grid 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
[510007,"Cardiff East Grid 275/132/33/11kV S Stn",0.2,"Y",1480,"",3,"Y"]
[510008,"Cardiff North Grid 132/33kV S Stn",8.1000000000000003E-2,null,1000,"Y",3,"Y"]
[510009,"Cardiff West Grid 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
[510049,"Aberthaw Power Station 275/132kV S Stn",0.2,"Y",2152,"",1,"Y"]
[510059,"East Aberthaw 132/33kV S Stn",0.16,null,1000,"Y",3,"Y"]
[510064,"Ashgrove 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510069,"Birchgrove 33/11kV S Stn",6.7000000000000004E-2,null,500,"Y",3,"Y"]
[510086,"Broad St. Barry 33/11kV S Stn",0.26300000000000001,null,500,"Y",3,"Y"]
[510088,"Brynhill Barry Grid 132/33/11kV S Stn",0.08,null,1000,"Y",3,"Y"]
[510096,"Canton 33/11kV S Stn",0.19700000000000001,null,500,"Y",3,"Y"]
[510104,"Court Rd. Barry 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510108,"Crwys Rd. 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510115,"Cyncoed 33/11kV S Stn",0.23,null,500,"Y",3,"Y"]
[510119,"Ely 33/11kV S Stn",7.3999999999999996E-2,null,500,"Y",3,"Y"]
[510121,"Fairwater 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510141,"Heath 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510144,"Highmead 33/11kV S Stn",4.5999999999999999E-2,null,96,"",3,"Y"]
[510148,"Ironbridge 33/11kV S Stn",7.3999999999999996E-2,null,163,"",3,"Y"]
[510152,"Llandough 33/11kV S Stn",7.0000000000000007E-2,null,500,"Y",3,"Y"]
[510160,"Llanishen 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510178,"Morlanga Farm 33/11kV S Stn",1.214,null,500,"Y",3,"Y"]
[510190,"Northcote St. 33/11kV S Stn",6.8000000000000005E-2,null,500,"Y",3,"Y"]
[510198,"Park Lane 33/11kV S Stn",8.2000000000000003E-2,null,500,"Y",3,"Y"]
[510199,"Penarth 33/11kV S Stn",0.14199999999999999,null,500,"Y",3,"Y"]
[510218,"Sanatorium 33/11kV S Stn",5.5E-2,null,500,"Y",3,"Y"]
[510219,"Sandon St. 33/11kV S Stn",0.14000000000000001,null,500,"Y",3,"Y"]
[510223,"Ship Hill Barry 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510230,"St Mellons 33/11kV S Stn",0.13600000000000001,null,500,"Y",3,"Y"]
[510238,"Taff Bank 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510310,"Wood Street 33/11kV S Stn",0.61,null,500,"Y",3,"Y"]
[510327,"Heath Hospital Primary 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510356,"Trident Park Generation 33kV S Stn",0.09,null,500,"Y",3,"Y"]
[510362,"Sutton Farm Solar Park 33kV S Stn",0.109,null,500,"Y",3,"Y"]
[510366,"Peakgen Barry STOR 33kV S Stn",0.23,null,500,"Y",3,"Y"]
[510398,"Jesus College P V Generation 33kV S Stn",0.16200000000000001,null,500,"Y",3,"Y"]
[510399,"Sully Moors Power Station 33kV S Stn",0.15,null,500,"Y",3,"Y"]
[510401,"Llancadle Solar Farm 33kV S Stn",0.16,null,500,"Y",3,"Y"]
[510407,"Derwyn Solar Farm 33kV S Stn",0.14000000000000001,null,500,"Y",3,"Y"]
[510428,false,0.20599999999999999,null,405,"",3,"Y"]
[510429,"Barry Dock Biomass 33kV S Stn",0.10299999999999999,null,500,"Y",3,"Y"]
[510439,"Broad Street Swg Site 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510447,"Trident Park 33kv Waste Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[510902,"Trowbridge 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[510905,"Cardiff South Grid 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[510908,"Grangetown Grid Primary 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[510909,"Sully Grid Primary 132/11kV S Stn",0.13400000000000001,null,1000,"Y",1,"Y"]
[510911,"Rover Way 132/11kV S Stn",8.6999999999999994E-2,null,1000,"Y",1,"Y"]
[510928,"GKN Rod Mill 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[520002,"Ammanford Grid 132/33kV S Stn",0.41699999999999998,null,1000,"Y",3,"Y"]
[520022,"Llanelli Grid 132/11kV S Stn",8.5000000000000006E-2,null,1000,"Y",1,"Y"]
[520035,"Swansea North Grid 132/33kV S Stn",0.17,null,4216,"",3,"Y"]
[520036,"Swansea West Grid 132/33kV S Stn",0.17599999999999999,null,1000,"Y",3,"Y"]
[520037,"Tir John Primary 132/33/6.6kV S Stn",8.4000000000000005E-2,null,1000,"Y",3,"Y"]
[520038,"Trostre Grid 132/33kV S Stn",0.14000000000000001,null,1000,"Y",3,"Y"]
[520041,"Travellers Rest 33/11kV S Stn",0.32800000000000001,null,500,"Y",3,"Y"]
[520045,"Gowerton East Grid 132/33kV S Stn",0.156,null,1000,"Y",3,"Y"]
[520070,"Bishopston 33/11kV S Stn",0.434,null,500,"Y",3,"Y"]
[520100,"Clase 33/11kV S Stn",0.20399999999999999,null,500,"Y",3,"Y"]
[520118,"Westfa 33/11kV S Stn",2.04,null,500,"Y",3,"Y"]
[520127,"Garngoch 33/11kV S Stn",0.29199999999999998,null,743,"",3,"Y"]
[520129,"Gethin Street Swansea 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[520137,"Gwaun Cae Gurwen 33/11kV S Stn",1.82,null,500,"Y",3,"Y"]
[520142,"Hendy 33/11kV S Stn",0.29299999999999998,null,500,"Y",3,"Y"]
[520145,"Waunarlwyd 33kV S Stn",0.39300000000000002,null,500,"Y",3,"Y"]
[520147,"Inco Europe South 33kV S Stn",0.21,null,500,"Y",3,"Y"]
[520162,"Llanrhidian 33/11kV S Stn",1.4319999999999999,null,500,"Y",3,"Y"]
[520172,"Meinciau 33/11kV S Stn",3.44,null,500,"Y",3,"Y"]
[520187,"New Lodge 33/11kV S Stn",0.18,null,500,"Y",3,"Y"]
[520197,"Pantyffynon 33/11kV S Stn",0.20699999999999999,null,500,"Y",3,"Y"]
[520207,"Pontardawe 33/11kV S Stn",0.3,null,500,"Y",3,"Y"]
[520209,"Pontyates 33/11kV S Stn",0.93600000000000005,null,500,"Y",3,"Y"]
[520211,"Ravenhill 33/11kV S Stn",5.6259999999999998E-2,null,161,"",3,"Y"]
[520217,"Lime Street Gorseinon 33/11kV S Stn",0.28000000000000003,null,500,"Y",3,"Y"]
[520225,"Sketty Park 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[520233,"Strand Swansea 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[520248,"Tumble 33/11kV S Stn",0.154,null,500,"Y",3,"Y"]
[520250,"Uplands Swansea 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[520251,"Upper Bank 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[520258,"West Cross 33/11kV S Stn",0.184,null,500,"Y",3,"Y"]
[520259,"Westfa 33/11kV S Stn",0.10100000000000001,null,500,"Y",3,"Y"]
[520274,"Swansea Trading Estate 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[520284,"Jersey Marine 33/11kV S Stn",9.2999999999999999E-2,null,500,"Y",3,"Y"]
[520286,"Kidwelly 33/11kV S Stn",0.748,null,500,"Y",3,"Y"]
[520291,"Morriston 132/11kV S Stn",0.127,null,1000,"Y",1,"Y"]
[520299,"Maes Ar Dafen 33/11kV S Stn",0.16400000000000001,null,500,"Y",3,"Y"]
[520307,"Cross Hands 33/11kV S Stn",0.248,null,500,"Y",3,"Y"]
[520312,"Crymlyn Burrows 33kV S Stn",0.3,null,500,"Y",3,"Y"]
[520316,"Swansea University 33/11kV S Stn",1.9504999999999999,null,500,"Y",3,"Y"]
[520317,"Swansea Waterfront 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[520318,"Pwllfa Gwatkin 33kV S Stn",1.6819999999999999,null,500,"Y",3,"Y"]
[520326,"Felindre Pumping Station 33kV S Stn",0.26900000000000002,null,500,"Y",3,"Y"]
[520334,"Western Coal 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[520339,"Cefn Betingau Solar PV 33kV S Stn",0.34100000000000003,null,500,"Y",3,"Y"]
[520340,"Clawdd Ddu Solar Farm 33kV S Stn",0.34,null,500,"Y",3,"Y"]
[520341,"Betws Wind Farm Grid 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[520344,"Waunarlwydd STOR Generation 33kV S Stn",0.39300000000000002,null,500,"Y",3,"Y"]
[520345,"Ffos Las PV Generation 33kV S Stn",0.32400000000000001,null,500,"Y",3,"Y"]
[520346,"Pont Andrew PV Generation 33kV S Stn",0.68100000000000005,null,500,"Y",3,"Y"]
[520348,"Tir John STOR Generation 33kV S Stn",8.4000000000000005E-2,null,500,"Y",3,"Y"]
[520360,"Swansea North Local 33/11kV S Stn",0.3,null,500,"Y",3,"Y"]
[520365,"Pentre Solar Farm Generation 33kV S Stn",0.8,null,500,"Y",3,"Y"]
[520371,"Pen Y Cae Solar 33kV S Stn",0.2,null,500,"Y",3,"Y"]
[520373,"Saron Solar Farm 33kV S Stn",0.18,null,500,"Y",3,"Y"]
[520374,"Brynteg Solar Farm 33kV S Stn",0.34,null,500,"Y",3,"Y"]
[520381,"Abergelli PV Generation Site 33kV S Stn",0.36,null,500,"Y",3,"Y"]
[520386,"Rhyd Y Pandy Solar Park 33kV S Stn",0.25,null,500,"Y",3,"Y"]
[520388,"Blaenlleidi Wind Farm 33kV S Stn",2.2000000000000002,null,500,"Y",3,"Y"]
[520392,"Gelliwern Isaf Pv Gen 33kV S Stn",0.42,null,500,"Y",3,"Y"]
[520396,"Brynwhilach Solar Park 33kV S Stn",0.13200000000000001,null,500,"Y",3,"Y"]
[520410,"Mynydd Y Gwrhyd Wind Generation 33kV S Stn",0.92,null,500,"Y",3,"Y"]
[520423,"Cockett Valley Solar Park 33kV S Stn",0.41199999999999998,null,500,"Y",3,"Y"]
[520427,"Gowerton STOR 33kV S Stn",0.27300000000000002,null,479,"",3,"Y"]
[520435,"Brechfa Forest West Wind Farm 132kV S Stn",1.45,null,1000,"Y",1,"Y"]
[520438,"Mynydd Y Gwair Wind Farm 132kV S Stn",0.61599999999999999,null,3000,"",1,"Y"]
[520445,"Mynydd Uchaf Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[520446,"Brynhenllys Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[530001,"Abergavenny 132/66kV S Stn",7.8E-2,null,271,null,1,"Y"]
[530023,"Llantarnam 132/66kV S Stn",0.10299999999999999,null,460,null,1,"Y"]
[530027,"Newport East 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[530028,"Newport South 132/33kV S Stn",1.7999999999999999E-2,null,148,null,1,"Y"]
[530034,"Sudbrook 132/33kV S Stn",0.11,null,440,null,1,"Y"]
[530046,"Uskmouth 275/132kV S Stn",0.2,"Y",901,"",1,"Y"]
[530056,"Abersychan 66/11kV S Stn",0.20599999999999999,null,244,null,3,"Y"]
[530071,"Blaenavon 66/11kV S Stn",0.11,null,146,"",3,"Y"]
[530095,"Caldicot 33/11kV S Stn",0.11600000000000001,null,102,null,3,"Y"]
[530099,"Chepstow 33/11kV S Stn",0.36499999999999999,null,341,null,3,"Y"]
[530110,"Cwmbran Primary 132/11kV S Stn",6.3E-2,null,287,null,1,"Y"]
[530177,"Monmouth 66/11kV S Stn",7.3999999999999996E-2,null,85,null,3,"Y"]
[530195,"Orb Works 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[530196,"Panteg 132/11kV S Stn",5.7000000000000002E-2,null,260,null,1,"Y"]
[530214,"Ringland Newport 33/11kV S Stn",6.8000000000000005E-2,null,98,null,3,"Y"]
[530226,"St Arvans 33/11kV S Stn",1.1020000000000001,null,905,null,3,"Y"]
[530252,"Usk 66/11kV S Stn",0.248,null,294,null,3,"Y"]
[530294,"Newhouse 33/11kV S Stn",0.32,null,341,null,3,"Y"]
[530316,"British Energy Newport South 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[530333,"Rogerstone 66/11kV S Stn",0.20399999999999999,null,157,null,3,"Y"]
[530404,"Oak Grove Farm Solar Generation 33kV S Stn",0.43,null,309,"",3,"Y"]
[530406,"Lower House P V Generation 66kV S Stn",0.23,null,500,"Y",3,"Y"]
[530413,"Traston Road Stor Generation 33kV S Stn",0.17,null,500,"Y",3,"Y"]
[530414,"Rhewl Farm Solar Park 33kV S Stn",0.29599999999999999,null,500,"Y",3,"Y"]
[530415,"Manor Farm Solar Park 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[530900,"Newport West 132/11kV S Stn",9.1999999999999998E-2,null,672,null,1,"Y"]
[530907,"Pontypool North 132/11kV S Stn",7.0999999999999994E-2,null,307,null,1,"Y"]
[530914,"Simms Metals 132kV S Stn",0.17299999999999999,null,1000,"Y",1,"Y"]
[530941,"Magor BSP 132/11kV S Stn",0.105,null,484,null,1,"Y"]
[540039,"Upper Boat 132/11kV S Stn",0.2,"Y",2629,"",1,"Y"]
[540094,"Caerphilly Primary 33/11kV S Stn",0.13300000000000001,null,500,"Y",3,"Y"]
[540106,"Creigiau 33/11kV S Stn",0.78400000000000003,null,500,"Y",3,"Y"]
[540120,"Energlyn Primary 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[540128,"Gas Yard 33/11kV S Stn",0.24199999999999999,null,500,"Y",3,"Y"]
[540174,"Middle Fan 33/11kV S Stn",0.247,null,500,"Y",3,"Y"]
[540234,"Trethomas 33/11kV S Stn",0.32200000000000001,null,500,"Y",3,"Y"]
[540240,"Tonypandy 33/11kV S Stn",0.22,null,500,"Y",3,"Y"]
[540241,"Mill St. Tonyrefail 33/11kV S Stn",0.7,"Y",384,"",3,"Y"]
[540255,"Wattstown 33/11kV S Stn",0.35199999999999998,null,700,"",3,"Y"]
[540263,"Ynysfeio 33/11kV S Stn",0.20399999999999999,null,500,"Y",3,"Y"]
[540270,"Talbot Green 132/11kV S Stn",0.29399999999999998,null,1000,"Y",1,"Y"]
[540295,"Taff Ely Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[540306,"Maerdy 33/11kV S Stn",0.378,null,500,"Y",3,"Y"]
[540332,"Ferndale Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[540335,"Mynydd Portref Wind Farm 33kV S Stn",1.48,null,500,"Y",3,"Y"]
[540338,"Maerdy Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[540412,"Tonypandy Stor 33kv Generation 33kV S Stn",3.87,null,500,"Y",3,"Y"]
[540425,"St Peters Church Wind Farm 33kV S Stn",0.92300000000000004,null,500,"Y",3,"Y"]
[540426,"Berthllwyd Solar Park Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[540903,"Nantgarw BSP 132/11kV S Stn",0.29299999999999998,null,1000,"Y",1,"Y"]
[540910,"Energlyn BSP 132/11kV S Stn",0.13800000000000001,null,1000,"Y",1,"Y"]
[540913,"Pontyclun 132/11kV S Stn",0.16200000000000001,null,1000,"Y",1,"Y"]
[550011,"Crumlin 132/11kV S Stn",0.219,null,1000,"Y",1,"Y"]
[550012,"Dowlais Grid 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
[550013,"Ebbw Vale 132/11kV S Stn",0.159,null,1000,"Y",1,"Y"]
[550018,"Hirwaun 132/33kV S Stn",0.21299999999999999,null,1000,"Y",3,"Y"]
[550026,"Mountain Ash Grid 132/33kV S Stn",1.03,null,1000,"Y",3,"Y"]
[550060,"Abertillery 33/11kV S Stn",0.16400000000000001,null,500,"Y",3,"Y"]
[550061,"Abertysswg 33/11kV S Stn",0.1111,null,500,"Y",3,"Y"]
[550090,"Brynmawr 33/11kV S Stn",0.10100000000000001,null,500,"Y",3,"Y"]
[550111,"Cwmfelinfach 33/11kV S Stn",0.34399999999999997,null,500,"Y",3,"Y"]
[550149,"Lady Windsor 33/11kV S Stn",0.53700000000000003,null,500,"Y",3,"Y"]
[550179,"Mountain Ash 33/11kV S Stn",0.14099999999999999,null,500,"Y",3,"Y"]
[550182,"Nantwen 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[550183,"Nelson 33/11kV S Stn",0.5,null,500,"Y",3,"Y"]
[550202,"Pengam Grid 132/11kV S Stn",0.13100000000000001,null,1000,"Y",1,"Y"]
[550203,"Pentrebach 33/11kV S Stn",0.15,null,500,"Y",3,"Y"]
[550208,"Pontllanffraith 33/11kV S Stn",0.126,null,500,"Y",3,"Y"]
[550244,"Tredegar 33/11kV S Stn",6.6000000000000003E-2,null,500,"Y",3,"Y"]
[550267,"Aberdare 33/11kV S Stn",0.13,null,500,"Y",3,"Y"]
[550287,"Swansea Road Merthyr 33/11kV S Stn",0.10299999999999999,null,500,"Y",3,"Y"]
[550288,"Rassau West 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[550313,"Aberaman Park 33kV S Stn",0.63700000000000001,null,500,"Y",3,"Y"]
[550321,"Trecatti Generation 33kV S Stn",0.34,null,500,"Y",3,"Y"]
[550343,"Hirwaun STOR Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[550354,"Dowlais STOR Generation West 33kV S Stn",0.52,null,500,"Y",3,"Y"]
[550375,"Hendre Fawr Solar Farm 33/11kV S Stn",0.16,null,500,"Y",3,"Y"]
[550376,"Mynydd Y Bwllfa Wind Farm 132kV S Stn",1.05,null,1000,"Y",1,"Y"]
[550377,"Cwm Cae Singrug Solar Park 33kV S Stn",0.5,null,500,"Y",3,"Y"]
[550378,"Hendai Solar Farm 33kV S Stn",0.39,null,500,"Y",3,"Y"]
[550384,"Aberaman Industrial No.1 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[550389,"Cwmbargoed Coal Washery (Load) 33kV S Stn",0.30199999999999999,null,500,"Y",3,"Y"]
[550390,"Hill Solar Farm 33kV S Stn",0.95,null,500,"Y",3,"Y"]
[550400,"Pen Y Cymoedd Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[550402,"Hafod Y Dafal Solar Park 33kV S Stn",0.59799999999999998,null,500,"Y",3,"Y"]
[550403,"Dowlais Stor Generation East 33kV S Stn",0.3347,null,500,"Y",3,"Y"]
[550409,"Pen Rhiw Caradog Pv Generation 33kV S Stn",0.751,null,500,"Y",3,"Y"]
[550416,"Bargoed Solar Park 33kV S Stn",0.44,null,500,"Y",3,"Y"]
[550418,"Rassau Industrial Estate Stor Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[550422,"Waun Y Pound Gas Stor 33kV S Stn",1.31,null,500,"Y",3,"Y"]
[550433,"Rhigos Road Gas Generation 33kV S Stn",1.573,null,500,"Y",3,"Y"]
[550434,"Manmoel Solar Park 33kV S Stn",0.84,null,832,"",3,"Y"]
[550436,"Crumlin STOR 33kV S Stn",0.84399999999999997,null,710,"",3,"Y"]
[550437,"Pen Bryn Oer Windfarm 33kV S Stn",0.55400000000000005,null,680,"",3,"Y"]
[550441,"Beaufort Power Stor 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[550442,"Brecon Power Stor 33kV S Stn",0.434,null,240,"",3,"Y"]
[550901,"Merthyr East Primary 132/11kV S Stn",0.23599999999999999,null,1000,"Y",1,"Y"]
[550906,"Rassau Supergrid 400/132kV S Stn",7.9000000000000001E-2,null,4870,"",1,"Y"]
[560004,"Bridgend Grid 132/33kV S Stn",0.127,null,1000,"Y",3,"Y"]
[560005,"Briton Ferry 132/33kV S Stn",5.8999999999999997E-2,null,1000,"Y",3,"Y"]
[560015,"Grange 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[560024,"Llynfi 66/11kV S Stn",0.26500000000000001,null,500,"Y",3,"Y"]
[560025,"Cefn Gwrgan 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[560030,"Pyle Grid 132/33/11kV S Stn",0.14299999999999999,null,2159,"",3,"Y"]
[560047,"Margam Grid 132/66kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
[560050,"Fords Bridgend 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[560053,"Abercrave 33/11kV S Stn",0.92,null,500,"Y",3,"Y"]
[560055,"Aberpergwm 33/11kV S Stn",0.30199999999999999,null,500,"Y",3,"Y"]
[560075,"Boverton 33/11kV S Stn",0.32200000000000001,null,500,"Y",3,"Y"]
[560079,"Bridgend Trading Estate 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[560093,"Caerau Road 66/11kV S Stn",0.34,null,500,"Y",3,"Y"]
[560103,"Commercial St. Neath 33/11kV S Stn",0.22500000000000001,null,500,"Y",3,"Y"]
[560105,"Cowbridge 33/11kV S Stn",0.21,null,500,"Y",3,"Y"]
[560150,"Litchard 33/11kV S Stn",0.151,null,500,"Y",3,"Y"]
[560158,"Llangewydd 33/11kV S Stn",0.22600000000000001,null,500,"Y",3,"Y"]
[560191,"Nottage 33/11kV S Stn",0.23599999999999999,null,500,"Y",3,"Y"]
[560193,"Ogmore Vale 66/11kV S Stn",0.30099999999999999,null,500,"Y",3,"Y"]
[560220,"Schwyll 33/11kV S Stn",0.61599999999999999,null,500,"Y",3,"Y"]
[560253,"Victoria Road 33/11kV S Stn",0.12,null,500,"Y",3,"Y"]
[560256,"Wern 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[560265,"Ynys Street 33/11kV S Stn",0.106,null,500,"Y",3,"Y"]
[560290,"Boc Margam Grid 132kV S Stn",0.115,null,1000,"Y",1,"Y"]
[560292,"Waterton Industrial Primary 132/11kV S Stn",0.16,null,1000,"Y",1,"Y"]
[560311,"South Cornelly 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[560320,"Ffynnon Oer Wind Farm 66kV S Stn",2.2170000000000001,null,500,"Y",3,"Y"]
[560322,"Llandarcy 33/11kV S Stn",0.28100000000000003,null,500,"Y",3,"Y"]
[560324,"Margam BOC Biomass 33kV S Stn",0.27,null,500,"Y",3,"Y"]
[560331,"Maesgwyne Wind Farm 132kV S Stn",0.14299999999999999,null,1000,"Y",1,"Y"]
[560336,"Baglan Bay PV Generation 33kV S Stn",0.44,null,500,"Y",3,"Y"]
[560342,"Pant Y Wal Wind Farm 66kV S Stn",0.86199999999999999,null,500,"Y",3,"Y"]
[560347,"Briton Ferry STOR Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[560358,"Llandarcy STOR Generation 33kV S Stn",0.63,null,500,"Y",3,"Y"]
[560359,"Garn Farm Solar Park 33kV S Stn",0.34,null,500,"Y",3,"Y"]
[560361,"Treguff Farm PV Generation 33kV S Stn",0.35899999999999999,null,500,"Y",3,"Y"]
[560363,"Loughor Solar Park 33kV S Stn",0.14499999999999999,null,500,"Y",3,"Y"]
[560372,"Margam Biomass Generation 132kV S Stn",0.11700000000000001,null,822,"",1,"Y"]
[560379,"Court Coleman PV Generation 33/11kV S Stn",0.28000000000000003,null,500,"Y",3,"Y"]
[560382,"Cenin Energy Park 33kV S Stn",1.5740000000000001,null,500,"Y",3,"Y"]
[560397,"Pant Y Moch Solar Farm 33kV S Stn",0.81,null,500,"Y",3,"Y"]
[560405,"Stormy Down Pv Generation 33kV S Stn",1,null,1331,"",3,"Y"]
[560408,"Rosedew Solar  Farm 33kV S Stn",0.34899999999999998,null,500,"Y",3,"Y"]
[560411,"Maesgwyn Wind Farm 33kV S Stn",0.47,null,500,"Y",3,"Y"]
[560417,"Mynydd Brombil Windfarm 33kV S Stn",1.5309999999999999,null,500,"Y",3,"Y"]
[560419,"Newton Down Wind Farm 33kV S Stn",1.6759999999999999,null,1240,"",3,"Y"]
[560420,"Llynfi Afan Wind Farm 66kV S Stn",0.78,null,325,"",3,"Y"]
[560421,"Mynydd Yr Aber Wind Farm 66kV S Stn",0.86199999999999999,null,500,"Y",3,"Y"]
[560440,"Afan Way Stor Generation 33kV S Stn",0.11700000000000001,null,500,"Y",3,"Y"]
[560912,"Pencoed BSP 132/11kV S Stn",0.189,null,1000,"Y",1,"Y"]
[580010,"Carmarthen 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
[580031,"Rhos 132/33/11kV S Stn",1.21,null,1000,"Y",3,"Y"]
[580072,"Blaenporth 33/11kV S Stn",1.18,null,500,"Y",3,"Y"]
[580078,"Bridell 33/11kV S Stn",0.24299999999999999,null,500,"Y",3,"Y"]
[580201,"Pendine 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[580228,"St Clears 33/11kV S Stn",1.1970000000000001,null,1161,"",3,"Y"]
[580247,"Trevaughan 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[580262,"Whitland 33/11kV S Stn",0.75,null,500,"Y",3,"Y"]
[580272,"Cardigan 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[580276,"Newcastle Emlyn South 33/11kV S Stn",0.66900000000000004,null,500,"Y",3,"Y"]
[580296,"Cwmffrwd 33/11kV S Stn",0.65,null,500,"Y",3,"Y"]
[580308,"Llanfyrnach 33/11kV S Stn",3.843,null,500,"Y",3,"Y"]
[580314,"Parc Cynog Wind Farm 33kV S Stn",0.37,null,500,"Y",3,"Y"]
[580315,"Blaen Bowi Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[580328,"Blaengwen Wind Farm 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[580337,"Whitland Solar Park 33kV S Stn",0.152,null,500,"Y",3,"Y"]
[580380,"Llwyndu Solar Farm 33kV S Stn",0.54,null,500,"Y",3,"Y"]
[580383,"Crugmore Solar Park 33kV S Stn",0.23,null,500,"Y",3,"Y"]
[580394,"Red Court Solar Farm 33kV S Stn",0.16900000000000001,null,500,"Y",3,"Y"]
[580432,"Bryncyrnau Isaf Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[590020,"Lampeter Primary 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
[590021,"Llanarth Primary 132/33kV S Stn",1.1419999999999999,null,1000,"Y",3,"Y"]
[590052,"Aberaeron 33/11kV S Stn",0.59,null,500,"Y",3,"Y"]
[590151,"Llandeilo 33/11kV S Stn",0.85799999999999998,null,500,"Y",3,"Y"]
[590153,"Llandovery 33/11kV S Stn",0.32300000000000001,null,500,"Y",3,"Y"]
[590156,"Llanfihangel Ystrad 33/11kV S Stn",1.0109999999999999,null,500,"Y",3,"Y"]
[590157,"Llangadog 33/11kV S Stn",0.74,null,500,"Y",3,"Y"]
[590161,"Llanllwni 33/11kV S Stn",3.76,null,500,"Y",3,"Y"]
[590170,"Manoravon Pumping Station 33kV S Stn",0.72799999999999998,null,1421,"",3,"Y"]
[590180,"Nantgaredig 33/11kV S Stn",4.0490000000000004,null,500,"Y",3,"Y"]
[590206,"Pont Ar Annell 33/11kV S Stn",1.28,null,500,"Y",3,"Y"]
[590246,"Argoed Tregaron 33/11kV S Stn",3.3,null,500,"Y",3,"Y"]
[590282,"W G W B Towy Intake 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[590298,"Duffryn Brodyn 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[590304,"Llyn Brianne 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[590424,"Nathenfoel Solar Park 33kV S Stn",0.39500000000000002,null,500,"Y",3,"Y"]
[600003,"Texaco Grid 132/11kV S Stn",0.27100000000000002,null,1000,"Y",1,"Y"]
[600014,"Golden Hill 132/33kV S Stn",0.24299999999999999,null,1000,"Y",3,"Y"]
[600016,"Haverfordwest Grid 132/33kV S Stn",0.45900000000000002,null,1000,"Y",3,"Y"]
[600017,"Haverfordwest 33/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[600029,"Pembroke Power Station 400/132kV S Stn",0.2,"Y",2300,"",1,"Y"]
[600040,"Waterston 132/11kV S Stn",0.42,null,1000,"Y",1,"Y"]
[600042,"Milford Haven Grid 132/33kV S Stn",1.07,null,1000,"Y",3,"Y"]
[600043,"Robeston 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[600076,"Brawdy 33/11kV S Stn",2.0630000000000002,null,500,"Y",3,"Y"]
[600085,"Broadfield 33/11kV S Stn",0.23799999999999999,null,500,"Y",3,"Y"]
[600124,"Fishguard 33/11kV S Stn",1.895,null,500,"Y",3,"Y"]
[600173,"Merlins Bridge 33/11kV S Stn",0.2,null,500,"Y",3,"Y"]
[600184,"Nevern 33/11kV S Stn",2.6,null,500,"Y",3,"Y"]
[600188,"Neyland 33/11kV S Stn",0.66100000000000003,null,500,"Y",3,"Y"]
[600200,"Penblewin 33/11kV S Stn",0.80200000000000005,null,500,"Y",3,"Y"]
[600229,"St Florence 33/11kV S Stn",2.0499999999999998,null,500,"Y",3,"Y"]
[600231,"St Twynnells 33/11kV S Stn",1.4179999999999999,null,500,"Y",3,"Y"]
[600232,"Steynton 33/11kV S Stn",0.19,null,500,"Y",3,"Y"]
[600271,"St Davids 33/11kV S Stn",2.3860000000000001,null,500,"Y",3,"Y"]
[600273,"Tenby 33/11kV S Stn",0.248,null,500,"Y",3,"Y"]
[600279,"Milford Haven 33/11kV S Stn",0.22,null,500,"Y",3,"Y"]
[600319,"South Hook 132/33kV S Stn",0.15,null,1000,"Y",3,"Y"]
[600323,"Withyhedges 33kV S Stn",0.27,null,500,"Y",3,"Y"]
[600349,"Wear Point Wind Farm 33kV S Stn",0.8,null,500,"Y",3,"Y"]
[600350,"Jordanston Farm PV Generation 33kV S Stn",0.5,null,500,"Y",3,"Y"]
[600351,"West Farm PV Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[600352,"Rudbaxton PV Farm 33kV S Stn",0.20200000000000001,null,500,"Y",3,"Y"]
[600353,"Little Neath Solar Farm 33kV S Stn",0.59,null,500,"Y",3,"Y"]
[600355,"Hoplass Solar Farm PV Generation 33kV S Stn",0.32,null,500,"Y",3,"Y"]
[600357,"Liddlestone Ridge PV Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[600364,"Tiers Cross Solar Park 132kV S Stn",0.26,null,1000,"Y",1,"Y"]
[600367,"Fenton Farm PV Generation 33kV S Stn",0.16,null,500,"Y",3,"Y"]
[600370,"Yerbeston Solar Farm 33kV S Stn",0.252,null,500,"Y",3,"Y"]
[600385,"Yerbeston Chapel Hill Solar Farm 33kV S Stn",0.39,null,500,"Y",3,"Y"]
[600387,"Haverfordwest Solar Park 33kV S Stn",0.28000000000000003,null,83,"",3,"Y"]
[600391,"Little Neath Solar Farm 33kV S Stn",0.44,null,500,"Y",3,"Y"]
[600393,"Oak Cottage Solar Farm 33kV S Stn",0.27,null,500,"Y",3,"Y"]
[600431,"North Tenement Solar Park 33kV S Stn",0.28399999999999997,null,616,"",3,"Y"]
[600448,"Rhoscrowther 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[610077,"Brecon 66/11kV S Stn",0.13700000000000001,null,210,null,3,"Y"]
[610092,"Builth Wells 66/11kV S Stn",1.39,null,1215,null,3,"Y"]
[610107,"Crickhowell 66/11kV S Stn",0.497,null,561,null,3,"Y"]
[610133,"Glasbury 66/11kV S Stn",1.099,null,1044,null,3,"Y"]
[610154,"Llandrindod Wells 66/11kV S Stn",0.191,null,144,null,3,"Y"]
[610277,"Rhayader 66/11kV S Stn",0.439,null,285,null,3,"Y"]
[610297,"Bryn Titli Wind Farm 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[610443,"Bryn Blaen Wind Farm 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]

{"sheet":"Source-SWA-Name","index":17,"n_rows":350,"n_cols":9,"rows_kept":350,"cut":false,"hidden":true,"merged":[]}
[null,1,2,3,4,5,6,7,8]
["SUBSTATION_NAME_SWA","SUBSTATION_NAME_TRUNC_SWA","SUBSTATION_NUMBER_SWA","ZE","Assumed ZE","UE","Assumed UE","t","Assumed t"]
["Aberaeron 33/11kV S Stn","Aberaeron33/11kVSStn",590052,0.59,null,500,"Y",3,"Y"]
["Aberaman Industrial No.1 33kV S Stn","AberamanIndustrialNo.133kVSStn",550384,0.7,"Y",500,"Y",3,"Y"]
["Aberaman Park 33kV S Stn","AberamanPark33kVSStn",550313,0.63700000000000001,null,500,"Y",3,"Y"]
["Abercrave 33/11kV S Stn","Abercrave33/11kVSStn",560053,0.92,null,500,"Y",3,"Y"]
["Aberdare 33/11kV S Stn","Aberdare33/11kVSStn",550267,0.13,null,500,"Y",3,"Y"]
["Abergavenny 132/66kV S Stn","Abergavenny132/66kVSStn",530001,7.8E-2,null,271,null,1,"Y"]
["Abergelli PV Generation Site 33kV S Stn","AbergelliPVGenerationSite33kVSStn",520381,0.36,null,500,"Y",3,"Y"]
["Aberpergwm 33/11kV S Stn","Aberpergwm33/11kVSStn",560055,0.30199999999999999,null,500,"Y",3,"Y"]
["Abersychan 66/11kV S Stn","Abersychan66/11kVSStn",530056,0.20599999999999999,null,244,null,3,"Y"]
["Aberthaw Power Station 275/132kV S Stn","AberthawPowerStation275/132kVSStn",510049,0.2,"Y",2152,"",1,"Y"]
["Abertillery 33/11kV S Stn","Abertillery33/11kVSStn",550060,0.16400000000000001,null,500,"Y",3,"Y"]
["Abertysswg 33/11kV S Stn","Abertysswg33/11kVSStn",550061,0.1111,null,500,"Y",3,"Y"]
["Afan Way Stor Generation 33kV S Stn","AfanWayStorGeneration33kVSStn",560440,0.11700000000000001,null,500,"Y",3,"Y"]
["Ammanford Grid 132/33kV S Stn","AmmanfordGrid132/33kVSStn",520002,0.41699999999999998,null,1000,"Y",3,"Y"]
["Argoed Tregaron 33/11kV S Stn","ArgoedTregaron33/11kVSStn",590246,3.3,null,500,"Y",3,"Y"]
["Ashgrove 33/11kV S Stn","Ashgrove33/11kVSStn",510064,0.7,"Y",500,"Y",3,"Y"]
["Baglan Bay PV Generation 33kV S Stn","BaglanBayPVGeneration33kVSStn",560336,0.44,null,500,"Y",3,"Y"]
["Bargoed Solar Park 33kV S Stn","BargoedSolarPark33kVSStn",550416,0.44,null,500,"Y",3,"Y"]
["Barry Dock Biomass 33kV S Stn","BarryDockBiomass33kVSStn",510429,0.10299999999999999,null,500,"Y",3,"Y"]
["Beaufort Power Stor 33/11kV S Stn","BeaufortPowerStor33/11kVSStn",550441,0.7,"Y",500,"Y",3,"Y"]
["Berthllwyd Solar Park Generation 33kV S Stn","BerthllwydSolarParkGeneration33kVSStn",540426,0.7,"Y",500,"Y",3,"Y"]
["Betws Wind Farm Grid 132kV S Stn","BetwsWindFarmGrid132kVSStn",520341,0.2,"Y",1000,"Y",1,"Y"]
["Birchgrove 33/11kV S Stn","Birchgrove33/11kVSStn",510069,6.7000000000000004E-2,null,500,"Y",3,"Y"]
["Bishopston 33/11kV S Stn","Bishopston33/11kVSStn",520070,0.434,null,500,"Y",3,"Y"]
["Blaenavon 66/11kV S Stn","Blaenavon66/11kVSStn",530071,0.11,null,146,"",3,"Y"]
["Blaen Bowi Wind Farm 33kV S Stn","BlaenBowiWindFarm33kVSStn",580315,0.7,"Y",500,"Y",3,"Y"]
["Blaengwen Wind Farm 132kV S Stn","BlaengwenWindFarm132kVSStn",580328,0.2,"Y",1000,"Y",1,"Y"]
["Blaenlleidi Wind Farm 33kV S Stn","BlaenlleidiWindFarm33kVSStn",520388,2.2000000000000002,null,500,"Y",3,"Y"]
["Blaenporth 33/11kV S Stn","Blaenporth33/11kVSStn",580072,1.18,null,500,"Y",3,"Y"]
["Boc Margam Grid 132kV S Stn","BocMargamGrid132kVSStn",560290,0.115,null,1000,"Y",1,"Y"]
["Boverton 33/11kV S Stn","Boverton33/11kVSStn",560075,0.32200000000000001,null,500,"Y",3,"Y"]
["Brawdy 33/11kV S Stn","Brawdy33/11kVSStn",600076,2.0630000000000002,null,500,"Y",3,"Y"]
["Brechfa Forest West Wind Farm 132kV S Stn","BrechfaForestWestWindFarm132kVSStn",520435,1.45,null,1000,"Y",1,"Y"]
["Brecon 66/11kV S Stn","Brecon66/11kVSStn",610077,0.13700000000000001,null,210,null,3,"Y"]
["Brecon Power Stor 33kV S Stn","BreconPowerStor33kVSStn",550442,0.434,null,240,"",3,"Y"]
["Bridell 33/11kV S Stn","Bridell33/11kVSStn",580078,0.24299999999999999,null,500,"Y",3,"Y"]
["Bridgend Grid 132/33kV S Stn","BridgendGrid132/33kVSStn",560004,0.127,null,1000,"Y",3,"Y"]
["Bridgend Trading Estate 33/11kV S Stn","BridgendTradingEstate33/11kVSStn",560079,0.7,"Y",500,"Y",3,"Y"]
["British Energy Newport South 33kV S Stn","BritishEnergyNewportSouth33kVSStn",530316,0.7,"Y",500,"Y",3,"Y"]
["Briton Ferry 132/33kV S Stn","BritonFerry132/33kVSStn",560005,5.8999999999999997E-2,null,1000,"Y",3,"Y"]
["Briton Ferry STOR Generation 33kV S Stn","BritonFerrySTORGeneration33kVSStn",560347,0.7,"Y",500,"Y",3,"Y"]
["Broadfield 33/11kV S Stn","Broadfield33/11kVSStn",600085,0.23799999999999999,null,500,"Y",3,"Y"]
["Broad St. Barry 33/11kV S Stn","BroadSt.Barry33/11kVSStn",510086,0.26300000000000001,null,500,"Y",3,"Y"]
["Broad Street Swg Site 33kV S Stn","BroadStreetSwgSite33kVSStn",510439,0.7,"Y",500,"Y",3,"Y"]
["Bryn Blaen Wind Farm 66kV S Stn","BrynBlaenWindFarm66kVSStn",610443,0.7,"Y",500,"Y",3,"Y"]
["Bryncyrnau Isaf Solar Park 33kV S Stn","BryncyrnauIsafSolarPark33kVSStn",580432,0.7,"Y",500,"Y",3,"Y"]
["Brynhenllys Solar Park 33kV S Stn","BrynhenllysSolarPark33kVSStn",520446,0.7,"Y",500,"Y",3,"Y"]
["Brynhill Barry Grid 132/33/11kV S Stn","BrynhillBarryGrid132/33/11kVSStn",510088,0.08,null,1000,"Y",3,"Y"]
["Brynmawr 33/11kV S Stn","Brynmawr33/11kVSStn",550090,0.10100000000000001,null,500,"Y",3,"Y"]
["Brynteg Solar Farm 33kV S Stn","BryntegSolarFarm33kVSStn",520374,0.34,null,500,"Y",3,"Y"]
["Bryn Titli Wind Farm 66kV S Stn","BrynTitliWindFarm66kVSStn",610297,0.7,"Y",500,"Y",3,"Y"]
["Brynwhilach Solar Park 33kV S Stn","BrynwhilachSolarPark33kVSStn",520396,0.13200000000000001,null,500,"Y",3,"Y"]
["Builth Wells 66/11kV S Stn","BuilthWells66/11kVSStn",610092,1.39,null,1215,null,3,"Y"]
["Caerau Road 66/11kV S Stn","CaerauRoad66/11kVSStn",560093,0.34,null,500,"Y",3,"Y"]
["Caerphilly Primary 33/11kV S Stn","CaerphillyPrimary33/11kVSStn",540094,0.13300000000000001,null,500,"Y",3,"Y"]
["Caldicot 33/11kV S Stn","Caldicot33/11kVSStn",530095,0.11600000000000001,null,102,null,3,"Y"]
["Canton 33/11kV S Stn","Canton33/11kVSStn",510096,0.19700000000000001,null,500,"Y",3,"Y"]
["Cardiff Central Grid 132/33kV S Stn","CardiffCentralGrid132/33kVSStn",510006,0.2,"Y",1000,"Y",3,"Y"]
["Cardiff East Grid 275/132/33/11kV S Stn","CardiffEastGrid275/132/33/11kVSStn",510007,0.2,"Y",1480,"",3,"Y"]
["Cardiff North Grid 132/33kV S Stn","CardiffNorthGrid132/33kVSStn",510008,8.1000000000000003E-2,null,1000,"Y",3,"Y"]
["Cardiff South Grid 132/11kV S Stn","CardiffSouthGrid132/11kVSStn",510905,0.2,"Y",1000,"Y",1,"Y"]
["Cardiff West Grid 132/33kV S Stn","CardiffWestGrid132/33kVSStn",510009,0.2,"Y",1000,"Y",3,"Y"]
["Cardigan 33/11kV S Stn","Cardigan33/11kVSStn",580272,0.7,"Y",500,"Y",3,"Y"]
["Carmarthen 132/33kV S Stn","Carmarthen132/33kVSStn",580010,0.2,"Y",1000,"Y",3,"Y"]
["Cefn Betingau Solar PV 33kV S Stn","CefnBetingauSolarPV33kVSStn",520339,0.34100000000000003,null,500,"Y",3,"Y"]
["Cefn Gwrgan 66kV S Stn","CefnGwrgan66kVSStn",560025,0.7,"Y",500,"Y",3,"Y"]
["Cenin Energy Park 33kV S Stn","CeninEnergyPark33kVSStn",560382,1.5740000000000001,null,500,"Y",3,"Y"]
["Chepstow 33/11kV S Stn","Chepstow33/11kVSStn",530099,0.36499999999999999,null,341,null,3,"Y"]
["Clase 33/11kV S Stn","Clase33/11kVSStn",520100,0.20399999999999999,null,500,"Y",3,"Y"]
["Clawdd Ddu Solar Farm 33kV S Stn","ClawddDduSolarFarm33kVSStn",520340,0.34,null,500,"Y",3,"Y"]
["Cockett Valley Solar Park 33kV S Stn","CockettValleySolarPark33kVSStn",520423,0.41199999999999998,null,500,"Y",3,"Y"]
["Commercial St. Neath 33/11kV S Stn","CommercialSt.Neath33/11kVSStn",560103,0.22500000000000001,null,500,"Y",3,"Y"]
["Court Coleman PV Generation 33/11kV S Stn","CourtColemanPVGeneration33/11kVSStn",560379,0.28000000000000003,null,500,"Y",3,"Y"]
["Court Rd. Barry 33/11kV S Stn","CourtRd.Barry33/11kVSStn",510104,0.7,"Y",500,"Y",3,"Y"]
["Cowbridge 33/11kV S Stn","Cowbridge33/11kVSStn",560105,0.21,null,500,"Y",3,"Y"]
["Creigiau 33/11kV S Stn","Creigiau33/11kVSStn",540106,0.78400000000000003,null,500,"Y",3,"Y"]
["Crickhowell 66/11kV S Stn","Crickhowell66/11kVSStn",610107,0.497,null,561,null,3,"Y"]
["Cross Hands 33/11kV S Stn","CrossHands33/11kVSStn",520307,0.248,null,500,"Y",3,"Y"]
["Crugmore Solar Park 33kV S Stn","CrugmoreSolarPark33kVSStn",580383,0.23,null,500,"Y",3,"Y"]
["Crumlin 132/11kV S Stn","Crumlin132/11kVSStn",550011,0.219,null,1000,"Y",1,"Y"]
["Crumlin STOR 33kV S Stn","CrumlinSTOR33kVSStn",550436,0.84399999999999997,null,710,"",3,"Y"]
["Crwys Rd. 33/11kV S Stn","CrwysRd.33/11kVSStn",510108,0.7,"Y",500,"Y",3,"Y"]
["Crymlyn Burrows 33kV S Stn","CrymlynBurrows33kVSStn",520312,0.3,null,500,"Y",3,"Y"]
["Cwmbargoed Coal Washery (Load) 33kV S Stn","CwmbargoedCoalWashery(Load)33kVSStn",550389,0.30199999999999999,null,500,"Y",3,"Y"]
["Cwmbran Primary 132/11kV S Stn","CwmbranPrimary132/11kVSStn",530110,6.3E-2,null,287,null,1,"Y"]
["Cwm Cae Singrug Solar Park 33kV S Stn","CwmCaeSingrugSolarPark33kVSStn",550377,0.5,null,500,"Y",3,"Y"]
["Cwmfelinfach 33/11kV S Stn","Cwmfelinfach33/11kVSStn",550111,0.34399999999999997,null,500,"Y",3,"Y"]
["Cwmffrwd 33/11kV S Stn","Cwmffrwd33/11kVSStn",580296,0.65,null,500,"Y",3,"Y"]
["Cyncoed 33/11kV S Stn","Cyncoed33/11kVSStn",510115,0.23,null,500,"Y",3,"Y"]
["Derwyn Solar Farm 33kV S Stn","DerwynSolarFarm33kVSStn",510407,0.14000000000000001,null,500,"Y",3,"Y"]
["Dowlais Grid 132/33kV S Stn","DowlaisGrid132/33kVSStn",550012,0.2,"Y",1000,"Y",3,"Y"]
["Dowlais Stor Generation East 33kV S Stn","DowlaisStorGenerationEast33kVSStn",550403,0.3347,null,500,"Y",3,"Y"]
["Dowlais STOR Generation West 33kV S Stn","DowlaisSTORGenerationWest33kVSStn",550354,0.52,null,500,"Y",3,"Y"]
["Duffryn Brodyn 33kV S Stn","DuffrynBrodyn33kVSStn",590298,0.7,"Y",500,"Y",3,"Y"]
["East Aberthaw 132/33kV S Stn","EastAberthaw132/33kVSStn",510059,0.16,null,1000,"Y",3,"Y"]
["Ebbw Vale 132/11kV S Stn","EbbwVale132/11kVSStn",550013,0.159,null,1000,"Y",1,"Y"]
["Ely 33/11kV S Stn","Ely33/11kVSStn",510119,7.3999999999999996E-2,null,500,"Y",3,"Y"]
["Energlyn BSP 132/11kV S Stn","EnerglynBSP132/11kVSStn",540910,0.13800000000000001,null,1000,"Y",1,"Y"]
["Energlyn Primary 33/11kV S Stn","EnerglynPrimary33/11kVSStn",540120,0.7,"Y",500,"Y",3,"Y"]
["Fairwater 33/11kV S Stn","Fairwater33/11kVSStn",510121,0.7,"Y",500,"Y",3,"Y"]
["Felindre Pumping Station 33kV S Stn","FelindrePumpingStation33kVSStn",520326,0.26900000000000002,null,500,"Y",3,"Y"]
["Fenton Farm PV Generation 33kV S Stn","FentonFarmPVGeneration33kVSStn",600367,0.16,null,500,"Y",3,"Y"]
["Ferndale Wind Farm 33kV S Stn","FerndaleWindFarm33kVSStn",540332,0.7,"Y",500,"Y",3,"Y"]
["Ffos Las PV Generation 33kV S Stn","FfosLasPVGeneration33kVSStn",520345,0.32400000000000001,null,500,"Y",3,"Y"]
["Ffynnon Oer Wind Farm 66kV S Stn","FfynnonOerWindFarm66kVSStn",560320,2.2170000000000001,null,500,"Y",3,"Y"]
["Fishguard 33/11kV S Stn","Fishguard33/11kVSStn",600124,1.895,null,500,"Y",3,"Y"]
["Fords Bridgend 132kV S Stn","FordsBridgend132kVSStn",560050,0.2,"Y",1000,"Y",1,"Y"]
["Garn Farm Solar Park 33kV S Stn","GarnFarmSolarPark33kVSStn",560359,0.34,null,500,"Y",3,"Y"]
["Garngoch 33/11kV S Stn","Garngoch33/11kVSStn",520127,0.29199999999999998,null,743,"",3,"Y"]
["Gas Yard 33/11kV S Stn","GasYard33/11kVSStn",540128,0.24199999999999999,null,500,"Y",3,"Y"]
["Gelliwern Isaf Pv Gen 33kV S Stn","GelliwernIsafPvGen33kVSStn",520392,0.42,null,500,"Y",3,"Y"]
["Gethin Street Swansea 33/11kV S Stn","GethinStreetSwansea33/11kVSStn",520129,0.7,"Y",500,"Y",3,"Y"]
["GKN Rod Mill 33kV S Stn","GKNRodMill33kVSStn",510928,0.7,"Y",500,"Y",3,"Y"]
["Glasbury 66/11kV S Stn","Glasbury66/11kVSStn",610133,1.099,null,1044,null,3,"Y"]
["Golden Hill 132/33kV S Stn","GoldenHill132/33kVSStn",600014,0.24299999999999999,null,1000,"Y",3,"Y"]
["Gowerton East Grid 132/33kV S Stn","GowertonEastGrid132/33kVSStn",520045,0.156,null,1000,"Y",3,"Y"]
["Gowerton STOR 33kV S Stn","GowertonSTOR33kVSStn",520427,0.27300000000000002,null,479,"",3,"Y"]
["Grange 66kV S Stn","Grange66kVSStn",560015,0.7,"Y",500,"Y",3,"Y"]
["Grangetown Grid Primary 132/11kV S Stn","GrangetownGridPrimary132/11kVSStn",510908,0.2,"Y",1000,"Y",1,"Y"]
["Gwaun Cae Gurwen 33/11kV S Stn","GwaunCaeGurwen33/11kVSStn",520137,1.82,null,500,"Y",3,"Y"]
["Hafod Y Dafal Solar Park 33kV S Stn","HafodYDafalSolarPark33kVSStn",550402,0.59799999999999998,null,500,"Y",3,"Y"]
["Haverfordwest 33/11kV S Stn","Haverfordwest33/11kVSStn",600017,0.7,"Y",500,"Y",3,"Y"]
["Haverfordwest Grid 132/33kV S Stn","HaverfordwestGrid132/33kVSStn",600016,0.45900000000000002,null,1000,"Y",3,"Y"]
["Haverfordwest Solar Park 33kV S Stn","HaverfordwestSolarPark33kVSStn",600387,0.28000000000000003,null,83,"",3,"Y"]
["Heath 33/11kV S Stn","Heath33/11kVSStn",510141,0.7,"Y",500,"Y",3,"Y"]
["Heath Hospital Primary 33/11kV S Stn","HeathHospitalPrimary33/11kVSStn",510327,0.7,"Y",500,"Y",3,"Y"]
["Hendai Solar Farm 33kV S Stn","HendaiSolarFarm33kVSStn",550378,0.39,null,500,"Y",3,"Y"]
["Hendre Fawr Solar Farm 33/11kV S Stn","HendreFawrSolarFarm33/11kVSStn",550375,0.16,null,500,"Y",3,"Y"]
["Hendy 33/11kV S Stn","Hendy33/11kVSStn",520142,0.29299999999999998,null,500,"Y",3,"Y"]
["Highmead 33/11kV S Stn","Highmead33/11kVSStn",510144,4.5999999999999999E-2,null,96,"",3,"Y"]
["Hill Solar Farm 33kV S Stn","HillSolarFarm33kVSStn",550390,0.95,null,500,"Y",3,"Y"]
["Hirwaun 132/33kV S Stn","Hirwaun132/33kVSStn",550018,0.21299999999999999,null,1000,"Y",3,"Y"]
["Hirwaun STOR Generation 33kV S Stn","HirwaunSTORGeneration33kVSStn",550343,0.7,"Y",500,"Y",3,"Y"]
["Hoplass Solar Farm PV Generation 33kV S Stn","HoplassSolarFarmPVGeneration33kVSStn",600355,0.32,null,500,"Y",3,"Y"]
["Inco Europe South 33kV S Stn","IncoEuropeSouth33kVSStn",520147,0.21,null,500,"Y",3,"Y"]
["Ironbridge 33/11kV S Stn","Ironbridge33/11kVSStn",510148,7.3999999999999996E-2,null,163,"",3,"Y"]
["Jersey Marine 33/11kV S Stn","JerseyMarine33/11kVSStn",520284,9.2999999999999999E-2,null,500,"Y",3,"Y"]
["Jesus College P V Generation 33kV S Stn","JesusCollegePVGeneration33kVSStn",510398,0.16200000000000001,null,500,"Y",3,"Y"]
["Jordanston Farm PV Generation 33kV S Stn","JordanstonFarmPVGeneration33kVSStn",600350,0.5,null,500,"Y",3,"Y"]
["Kidwelly 33/11kV S Stn","Kidwelly33/11kVSStn",520286,0.748,null,500,"Y",3,"Y"]
["Lady Windsor 33/11kV S Stn","LadyWindsor33/11kVSStn",550149,0.53700000000000003,null,500,"Y",3,"Y"]
["Lampeter Primary 132/33kV S Stn","LampeterPrimary132/33kVSStn",590020,0.2,"Y",1000,"Y",3,"Y"]
["Liddlestone Ridge PV Generation 33kV S Stn","LiddlestoneRidgePVGeneration33kVSStn",600357,0.7,"Y",500,"Y",3,"Y"]
["Lime Street Gorseinon 33/11kV S Stn","LimeStreetGorseinon33/11kVSStn",520217,0.28000000000000003,null,500,"Y",3,"Y"]
["Litchard 33/11kV S Stn","Litchard33/11kVSStn",560150,0.151,null,500,"Y",3,"Y"]
["Little Neath Solar Farm 33kV S Stn","LittleNeathSolarFarm33kVSStn",600353,0.59,null,500,"Y",3,"Y"]
["Little Neath Solar Farm 33kV S Stn","LittleNeathSolarFarm33kVSStn",600391,0.44,null,500,"Y",3,"Y"]
["Llanarth Primary 132/33kV S Stn","LlanarthPrimary132/33kVSStn",590021,1.1419999999999999,null,1000,"Y",3,"Y"]
["Llancadle Solar Farm 33kV S Stn","LlancadleSolarFarm33kVSStn",510401,0.16,null,500,"Y",3,"Y"]
["Llandarcy 33/11kV S Stn","Llandarcy33/11kVSStn",560322,0.28100000000000003,null,500,"Y",3,"Y"]
["Llandarcy STOR Generation 33kV S Stn","LlandarcySTORGeneration33kVSStn",560358,0.63,null,500,"Y",3,"Y"]
["Llandeilo 33/11kV S Stn","Llandeilo33/11kVSStn",590151,0.85799999999999998,null,500,"Y",3,"Y"]
["Llandough 33/11kV S Stn","Llandough33/11kVSStn",510152,7.0000000000000007E-2,null,500,"Y",3,"Y"]
["Llandovery 33/11kV S Stn","Llandovery33/11kVSStn",590153,0.32300000000000001,null,500,"Y",3,"Y"]
["Llandrindod Wells 66/11kV S Stn","LlandrindodWells66/11kVSStn",610154,0.191,null,144,null,3,"Y"]
["Llanelli Grid 132/11kV S Stn","LlanelliGrid132/11kVSStn",520022,8.5000000000000006E-2,null,1000,"Y",1,"Y"]
["Llanfihangel Ystrad 33/11kV S Stn","LlanfihangelYstrad33/11kVSStn",590156,1.0109999999999999,null,500,"Y",3,"Y"]
["Llanfyrnach 33/11kV S Stn","Llanfyrnach33/11kVSStn",580308,3.843,null,500,"Y",3,"Y"]
["Llangadog 33/11kV S Stn","Llangadog33/11kVSStn",590157,0.74,null,500,"Y",3,"Y"]
["Llangewydd 33/11kV S Stn","Llangewydd33/11kVSStn",560158,0.22600000000000001,null,500,"Y",3,"Y"]
["Llanishen 33/11kV S Stn","Llanishen33/11kVSStn",510160,0.7,"Y",500,"Y",3,"Y"]
["Llanllwni 33/11kV S Stn","Llanllwni33/11kVSStn",590161,3.76,null,500,"Y",3,"Y"]
["Llanrhidian 33/11kV S Stn","Llanrhidian33/11kVSStn",520162,1.4319999999999999,null,500,"Y",3,"Y"]
["Llantarnam 132/66kV S Stn","Llantarnam132/66kVSStn",530023,0.10299999999999999,null,460,null,1,"Y"]
["Llwyndu Solar Farm 33kV S Stn","LlwynduSolarFarm33kVSStn",580380,0.54,null,500,"Y",3,"Y"]
["Llyn Brianne 33kV S Stn","LlynBrianne33kVSStn",590304,0.7,"Y",500,"Y",3,"Y"]
["Llynfi 66/11kV S Stn","Llynfi66/11kVSStn",560024,0.26500000000000001,null,500,"Y",3,"Y"]
["Llynfi Afan Wind Farm 66kV S Stn","LlynfiAfanWindFarm66kVSStn",560420,0.78,null,325,"",3,"Y"]
["Loughor Solar Park 33kV S Stn","LoughorSolarPark33kVSStn",560363,0.14499999999999999,null,500,"Y",3,"Y"]
["Lower House P V Generation 66kV S Stn","LowerHousePVGeneration66kVSStn",530406,0.23,null,500,"Y",3,"Y"]
["Maerdy 33/11kV S Stn","Maerdy33/11kVSStn",540306,0.378,null,500,"Y",3,"Y"]
["Maerdy Wind Farm 33kV S Stn","MaerdyWindFarm33kVSStn",540338,0.7,"Y",500,"Y",3,"Y"]
["Maes Ar Dafen 33/11kV S Stn","MaesArDafen33/11kVSStn",520299,0.16400000000000001,null,500,"Y",3,"Y"]
["Maesgwyne Wind Farm 132kV S Stn","MaesgwyneWindFarm132kVSStn",560331,0.14299999999999999,null,1000,"Y",1,"Y"]
["Maesgwyn Wind Farm 33kV S Stn","MaesgwynWindFarm33kVSStn",560411,0.47,null,500,"Y",3,"Y"]
["Magor BSP 132/11kV S Stn","MagorBSP132/11kVSStn",530941,0.105,null,484,null,1,"Y"]
["Manmoel Solar Park 33kV S Stn","ManmoelSolarPark33kVSStn",550434,0.84,null,832,"",3,"Y"]
["Manoravon Pumping Station 33kV S Stn","ManoravonPumpingStation33kVSStn",590170,0.72799999999999998,null,1421,"",3,"Y"]
["Manor Farm Solar Park 66kV S Stn","ManorFarmSolarPark66kVSStn",530415,0.7,"Y",500,"Y",3,"Y"]
["Margam Biomass Generation 132kV S Stn","MargamBiomassGeneration132kVSStn",560372,0.11700000000000001,null,822,"",1,"Y"]
["Margam BOC Biomass 33kV S Stn","MargamBOCBiomass33kVSStn",560324,0.27,null,500,"Y",3,"Y"]
["Margam Grid 132/66kV S Stn","MargamGrid132/66kVSStn",560047,0.2,"Y",1000,"Y",3,"Y"]
["Meinciau 33/11kV S Stn","Meinciau33/11kVSStn",520172,3.44,null,500,"Y",3,"Y"]
["Merlins Bridge 33/11kV S Stn","MerlinsBridge33/11kVSStn",600173,0.2,null,500,"Y",3,"Y"]
["Merthyr East Primary 132/11kV S Stn","MerthyrEastPrimary132/11kVSStn",550901,0.23599999999999999,null,1000,"Y",1,"Y"]
["Middle Fan 33/11kV S Stn","MiddleFan33/11kVSStn",540174,0.247,null,500,"Y",3,"Y"]
["Milford Haven 33/11kV S Stn","MilfordHaven33/11kVSStn",600279,0.22,null,500,"Y",3,"Y"]
["Milford Haven Grid 132/33kV S Stn","MilfordHavenGrid132/33kVSStn",600042,1.07,null,1000,"Y",3,"Y"]
["Mill St. Tonyrefail 33/11kV S Stn","MillSt.Tonyrefail33/11kVSStn",540241,0.7,"Y",384,"",3,"Y"]
["Monmouth 66/11kV S Stn","Monmouth66/11kVSStn",530177,7.3999999999999996E-2,null,85,null,3,"Y"]
["Morlanga Farm 33/11kV S Stn","MorlangaFarm33/11kVSStn",510178,1.214,null,500,"Y",3,"Y"]
["Morriston 132/11kV S Stn","Morriston132/11kVSStn",520291,0.127,null,1000,"Y",1,"Y"]
["Mountain Ash 33/11kV S Stn","MountainAsh33/11kVSStn",550179,0.14099999999999999,null,500,"Y",3,"Y"]
["Mountain Ash Grid 132/33kV S Stn","MountainAshGrid132/33kVSStn",550026,1.03,null,1000,"Y",3,"Y"]
["Mynydd Brombil Windfarm 33kV S Stn","MynyddBrombilWindfarm33kVSStn",560417,1.5309999999999999,null,500,"Y",3,"Y"]
["Mynydd Portref Wind Farm 33kV S Stn","MynyddPortrefWindFarm33kVSStn",540335,1.48,null,500,"Y",3,"Y"]
["Mynydd Uchaf Wind Farm 33kV S Stn","MynyddUchafWindFarm33kVSStn",520445,0.7,"Y",500,"Y",3,"Y"]
["Mynydd Y Bwllfa Wind Farm 132kV S Stn","MynyddYBwllfaWindFarm132kVSStn",550376,1.05,null,1000,"Y",1,"Y"]
["Mynydd Y Gwair Wind Farm 132kV S Stn","MynyddYGwairWindFarm132kVSStn",520438,0.61599999999999999,null,3000,"",1,"Y"]
["Mynydd Y Gwrhyd Wind Generation 33kV S Stn","MynyddYGwrhydWindGeneration33kVSStn",520410,0.92,null,500,"Y",3,"Y"]
["Mynydd Yr Aber Wind Farm 66kV S Stn","MynyddYrAberWindFarm66kVSStn",560421,0.86199999999999999,null,500,"Y",3,"Y"]
["Nantgaredig 33/11kV S Stn","Nantgaredig33/11kVSStn",590180,4.0490000000000004,null,500,"Y",3,"Y"]
["Nantgarw BSP 132/11kV S Stn","NantgarwBSP132/11kVSStn",540903,0.29299999999999998,null,1000,"Y",1,"Y"]
["Nantwen 33/11kV S Stn","Nantwen33/11kVSStn",550182,0.7,"Y",500,"Y",3,"Y"]
["Nathenfoel Solar Park 33kV S Stn","NathenfoelSolarPark33kVSStn",590424,0.39500000000000002,null,500,"Y",3,"Y"]
["Nelson 33/11kV S Stn","Nelson33/11kVSStn",550183,0.5,null,500,"Y",3,"Y"]
["Nevern 33/11kV S Stn","Nevern33/11kVSStn",600184,2.6,null,500,"Y",3,"Y"]
["Newcastle Emlyn South 33/11kV S Stn","NewcastleEmlynSouth33/11kVSStn",580276,0.66900000000000004,null,500,"Y",3,"Y"]
["Newhouse 33/11kV S Stn","Newhouse33/11kVSStn",530294,0.32,null,341,null,3,"Y"]
["New Lodge 33/11kV S Stn","NewLodge33/11kVSStn",520187,0.18,null,500,"Y",3,"Y"]
["Newport East 132/11kV S Stn","NewportEast132/11kVSStn",530027,0.2,"Y",1000,"Y",1,"Y"]
["Newport South 132/33kV S Stn","NewportSouth132/33kVSStn",530028,1.7999999999999999E-2,null,148,null,1,"Y"]
["Newport West 132/11kV S Stn","NewportWest132/11kVSStn",530900,9.1999999999999998E-2,null,672,null,1,"Y"]
["Newton Down Wind Farm 33kV S Stn","NewtonDownWindFarm33kVSStn",560419,1.6759999999999999,null,1240,"",3,"Y"]
["Neyland 33/11kV S Stn","Neyland33/11kVSStn",600188,0.66100000000000003,null,500,"Y",3,"Y"]
["Northcote St. 33/11kV S Stn","NorthcoteSt.33/11kVSStn",510190,6.8000000000000005E-2,null,500,"Y",3,"Y"]
["North Tenement Solar Park 33kV S Stn","NorthTenementSolarPark33kVSStn",600431,0.28399999999999997,null,616,"",3,"Y"]
["Nottage 33/11kV S Stn","Nottage33/11kVSStn",560191,0.23599999999999999,null,500,"Y",3,"Y"]
["Oak Cottage Solar Farm 33kV S Stn","OakCottageSolarFarm33kVSStn",600393,0.27,null,500,"Y",3,"Y"]
["Oak Grove Farm Solar Generation 33kV S Stn","OakGroveFarmSolarGeneration33kVSStn",530404,0.43,null,309,"",3,"Y"]
["Ogmore Vale 66/11kV S Stn","OgmoreVale66/11kVSStn",560193,0.30099999999999999,null,500,"Y",3,"Y"]
["Orb Works 33kV S Stn","OrbWorks33kVSStn",530195,0.7,"Y",500,"Y",3,"Y"]
["Panteg 132/11kV S Stn","Panteg132/11kVSStn",530196,5.7000000000000002E-2,null,260,null,1,"Y"]
["Pantyffynon 33/11kV S Stn","Pantyffynon33/11kVSStn",520197,0.20699999999999999,null,500,"Y",3,"Y"]
["Pant Y Moch Solar Farm 33kV S Stn","PantYMochSolarFarm33kVSStn",560397,0.81,null,500,"Y",3,"Y"]
["Pant Y Wal Wind Farm 66kV S Stn","PantYWalWindFarm66kVSStn",560342,0.86199999999999999,null,500,"Y",3,"Y"]
["Parc Cynog Wind Farm 33kV S Stn","ParcCynogWindFarm33kVSStn",580314,0.37,null,500,"Y",3,"Y"]
["Park Lane 33/11kV S Stn","ParkLane33/11kVSStn",510198,8.2000000000000003E-2,null,500,"Y",3,"Y"]
["Peakgen Barry STOR 33kV S Stn","PeakgenBarrySTOR33kVSStn",510366,0.23,null,500,"Y",3,"Y"]
["Pembroke Power Station 400/132kV S Stn","PembrokePowerStation400/132kVSStn",600029,0.2,"Y",2300,"",1,"Y"]
["Penarth 33/11kV S Stn","Penarth33/11kVSStn",510199,0.14199999999999999,null,500,"Y",3,"Y"]
["Penblewin 33/11kV S Stn","Penblewin33/11kVSStn",600200,0.80200000000000005,null,500,"Y",3,"Y"]
["Pen Bryn Oer Windfarm 33kV S Stn","PenBrynOerWindfarm33kVSStn",550437,0.55400000000000005,null,680,"",3,"Y"]
["Pencoed BSP 132/11kV S Stn","PencoedBSP132/11kVSStn",560912,0.189,null,1000,"Y",1,"Y"]
["Pendine 33/11kV S Stn","Pendine33/11kVSStn",580201,0.7,"Y",500,"Y",3,"Y"]
["Pengam Grid 132/11kV S Stn","PengamGrid132/11kVSStn",550202,0.13100000000000001,null,1000,"Y",1,"Y"]
["Pen Rhiw Caradog Pv Generation 33kV S Stn","PenRhiwCaradogPvGeneration33kVSStn",550409,0.751,null,500,"Y",3,"Y"]
["Pentrebach 33/11kV S Stn","Pentrebach33/11kVSStn",550203,0.15,null,500,"Y",3,"Y"]
["Pentre Solar Farm Generation 33kV S Stn","PentreSolarFarmGeneration33kVSStn",520365,0.8,null,500,"Y",3,"Y"]
["Pen Y Cae Solar 33kV S Stn","PenYCaeSolar33kVSStn",520371,0.2,null,500,"Y",3,"Y"]
["Pen Y Cymoedd Wind Farm 33kV S Stn","PenYCymoeddWindFarm33kVSStn",550400,0.7,"Y",500,"Y",3,"Y"]
["Pont Andrew PV Generation 33kV S Stn","PontAndrewPVGeneration33kVSStn",520346,0.68100000000000005,null,500,"Y",3,"Y"]
["Pont Ar Annell 33/11kV S Stn","PontArAnnell33/11kVSStn",590206,1.28,null,500,"Y",3,"Y"]
["Pontardawe 33/11kV S Stn","Pontardawe33/11kVSStn",520207,0.3,null,500,"Y",3,"Y"]
["Pontllanffraith 33/11kV S Stn","Pontllanffraith33/11kVSStn",550208,0.126,null,500,"Y",3,"Y"]
["Pontyates 33/11kV S Stn","Pontyates33/11kVSStn",520209,0.93600000000000005,null,500,"Y",3,"Y"]
["Pontyclun 132/11kV S Stn","Pontyclun132/11kVSStn",540913,0.16200000000000001,null,1000,"Y",1,"Y"]
["Pontypool North 132/11kV S Stn","PontypoolNorth132/11kVSStn",530907,7.0999999999999994E-2,null,307,null,1,"Y"]
["Pwllfa Gwatkin 33kV S Stn","PwllfaGwatkin33kVSStn",520318,1.6819999999999999,null,500,"Y",3,"Y"]
["Pyle Grid 132/33/11kV S Stn","PyleGrid132/33/11kVSStn",560030,0.14299999999999999,null,2159,"",3,"Y"]
["Rassau Industrial Estate Stor Generation 33kV S Stn","RassauIndustrialEstateStorGeneration33kVSStn",550418,0.7,"Y",500,"Y",3,"Y"]
["Rassau Supergrid 400/132kV S Stn","RassauSupergrid400/132kVSStn",550906,7.9000000000000001E-2,null,4870,"",1,"Y"]
["Rassau West 132/11kV S Stn","RassauWest132/11kVSStn",550288,0.2,"Y",1000,"Y",1,"Y"]
["Ravenhill 33/11kV S Stn","Ravenhill33/11kVSStn",520211,5.6259999999999998E-2,null,161,"",3,"Y"]
["Red Court Solar Farm 33kV S Stn","RedCourtSolarFarm33kVSStn",580394,0.16900000000000001,null,500,"Y",3,"Y"]
["Rhayader 66/11kV S Stn","Rhayader66/11kVSStn",610277,0.439,null,285,null,3,"Y"]
["Rhewl Farm Solar Park 33kV S Stn","RhewlFarmSolarPark33kVSStn",530414,0.29599999999999999,null,500,"Y",3,"Y"]
["Rhigos Road Gas Generation 33kV S Stn","RhigosRoadGasGeneration33kVSStn",550433,1.573,null,500,"Y",3,"Y"]
["Rhos 132/33/11kV S Stn","Rhos132/33/11kVSStn",580031,1.21,null,1000,"Y",3,"Y"]
["Rhoscrowther 132kV S Stn","Rhoscrowther132kVSStn",600448,0.2,"Y",1000,"Y",1,"Y"]
["Rhyd Y Pandy Solar Park 33kV S Stn","RhydYPandySolarPark33kVSStn",520386,0.25,null,500,"Y",3,"Y"]
["Ringland Newport 33/11kV S Stn","RinglandNewport33/11kVSStn",530214,6.8000000000000005E-2,null,98,null,3,"Y"]
["Robeston 132/11kV S Stn","Robeston132/11kVSStn",600043,0.2,"Y",1000,"Y",1,"Y"]
["Rogerstone 66/11kV S Stn","Rogerstone66/11kVSStn",530333,0.20399999999999999,null,157,null,3,"Y"]
["Rosedew Solar  Farm 33kV S Stn","RosedewSolarFarm33kVSStn",560408,0.34899999999999998,null,500,"Y",3,"Y"]
["Rover Way 132/11kV S Stn","RoverWay132/11kVSStn",510911,8.6999999999999994E-2,null,1000,"Y",1,"Y"]
["Rudbaxton PV Farm 33kV S Stn","RudbaxtonPVFarm33kVSStn",600352,0.20200000000000001,null,500,"Y",3,"Y"]
["Sanatorium 33/11kV S Stn","Sanatorium33/11kVSStn",510218,5.5E-2,null,500,"Y",3,"Y"]
["Sandon St. 33/11kV S Stn","SandonSt.33/11kVSStn",510219,0.14000000000000001,null,500,"Y",3,"Y"]
["Saron Solar Farm 33kV S Stn","SaronSolarFarm33kVSStn",520373,0.18,null,500,"Y",3,"Y"]
["Schwyll 33/11kV S Stn","Schwyll33/11kVSStn",560220,0.61599999999999999,null,500,"Y",3,"Y"]
["Ship Hill Barry 33/11kV S Stn","ShipHillBarry33/11kVSStn",510223,0.7,"Y",500,"Y",3,"Y"]
["Simms Metals 132kV S Stn","SimmsMetals132kVSStn",530914,0.17299999999999999,null,1000,"Y",1,"Y"]
["Sketty Park 33/11kV S Stn","SkettyPark33/11kVSStn",520225,0.7,"Y",500,"Y",3,"Y"]
["South Cornelly 33kV S Stn","SouthCornelly33kVSStn",560311,0.7,"Y",500,"Y",3,"Y"]
["South Hook 132/33kV S Stn","SouthHook132/33kVSStn",600319,0.15,null,1000,"Y",3,"Y"]
["St Arvans 33/11kV S Stn","StArvans33/11kVSStn",530226,1.1020000000000001,null,905,null,3,"Y"]
["St Clears 33/11kV S Stn","StClears33/11kVSStn",580228,1.1970000000000001,null,1161,"",3,"Y"]
["St Davids 33/11kV S Stn","StDavids33/11kVSStn",600271,2.3860000000000001,null,500,"Y",3,"Y"]
["Steynton 33/11kV S Stn","Steynton33/11kVSStn",600232,0.19,null,500,"Y",3,"Y"]
["St Florence 33/11kV S Stn","StFlorence33/11kVSStn",600229,2.0499999999999998,null,500,"Y",3,"Y"]
["St Mellons 33/11kV S Stn","StMellons33/11kVSStn",510230,0.13600000000000001,null,500,"Y",3,"Y"]
["Stormy Down Pv Generation 33kV S Stn","StormyDownPvGeneration33kVSStn",560405,1,null,1331,"",3,"Y"]
["St Peters Church Wind Farm 33kV S Stn","StPetersChurchWindFarm33kVSStn",540425,0.92300000000000004,null,500,"Y",3,"Y"]
["Strand Swansea 33/11kV S Stn","StrandSwansea33/11kVSStn",520233,0.7,"Y",500,"Y",3,"Y"]
["St Twynnells 33/11kV S Stn","StTwynnells33/11kVSStn",600231,1.4179999999999999,null,500,"Y",3,"Y"]
["Sudbrook 132/33kV S Stn","Sudbrook132/33kVSStn",530034,0.11,null,440,null,1,"Y"]
["Sully Grid Primary 132/11kV S Stn","SullyGridPrimary132/11kVSStn",510909,0.13400000000000001,null,1000,"Y",1,"Y"]
["Sully Moors Power Station 33kV S Stn","SullyMoorsPowerStation33kVSStn",510399,0.15,null,500,"Y",3,"Y"]
["Sutton Farm Solar Park 33kV S Stn","SuttonFarmSolarPark33kVSStn",510362,0.109,null,500,"Y",3,"Y"]
["Swansea North Grid 132/33kV S Stn","SwanseaNorthGrid132/33kVSStn",520035,0.17,null,4216,"",3,"Y"]
["Swansea North Local 33/11kV S Stn","SwanseaNorthLocal33/11kVSStn",520360,0.3,null,500,"Y",3,"Y"]
["Swansea Road Merthyr 33/11kV S Stn","SwanseaRoadMerthyr33/11kVSStn",550287,0.10299999999999999,null,500,"Y",3,"Y"]
["Swansea Trading Estate 33/11kV S Stn","SwanseaTradingEstate33/11kVSStn",520274,0.7,"Y",500,"Y",3,"Y"]
["Swansea University 33/11kV S Stn","SwanseaUniversity33/11kVSStn",520316,1.9504999999999999,null,500,"Y",3,"Y"]
["Swansea Waterfront 33/11kV S Stn","SwanseaWaterfront33/11kVSStn",520317,0.7,"Y",500,"Y",3,"Y"]
["Swansea West Grid 132/33kV S Stn","SwanseaWestGrid132/33kVSStn",520036,0.17599999999999999,null,1000,"Y",3,"Y"]
["Taff Bank 33/11kV S Stn","TaffBank33/11kVSStn",510238,0.7,"Y",500,"Y",3,"Y"]
["Taff Ely Wind Farm 33kV S Stn","TaffElyWindFarm33kVSStn",540295,0.7,"Y",500,"Y",3,"Y"]
["Talbot Green 132/11kV S Stn","TalbotGreen132/11kVSStn",540270,0.29399999999999998,null,1000,"Y",1,"Y"]
["Tenby 33/11kV S Stn","Tenby33/11kVSStn",600273,0.248,null,500,"Y",3,"Y"]
["Texaco Grid 132/11kV S Stn","TexacoGrid132/11kVSStn",600003,0.27100000000000002,null,1000,"Y",1,"Y"]
["Tiers Cross Solar Park 132kV S Stn","TiersCrossSolarPark132kVSStn",600364,0.26,null,1000,"Y",1,"Y"]
["Tir John Primary 132/33/6.6kV S Stn","TirJohnPrimary132/33/6.6kVSStn",520037,8.4000000000000005E-2,null,1000,"Y",3,"Y"]
["Tir John STOR Generation 33kV S Stn","TirJohnSTORGeneration33kVSStn",520348,8.4000000000000005E-2,null,500,"Y",3,"Y"]
["Tonypandy 33/11kV S Stn","Tonypandy33/11kVSStn",540240,0.22,null,500,"Y",3,"Y"]
["Tonypandy Stor 33kv Generation 33kV S Stn","TonypandyStor33kvGeneration33kVSStn",540412,3.87,null,500,"Y",3,"Y"]
["Traston Road Stor Generation 33kV S Stn","TrastonRoadStorGeneration33kVSStn",530413,0.17,null,500,"Y",3,"Y"]
["Travellers Rest 33/11kV S Stn","TravellersRest33/11kVSStn",520041,0.32800000000000001,null,500,"Y",3,"Y"]
["Trecatti Generation 33kV S Stn","TrecattiGeneration33kVSStn",550321,0.34,null,500,"Y",3,"Y"]
["Tredegar 33/11kV S Stn","Tredegar33/11kVSStn",550244,6.6000000000000003E-2,null,500,"Y",3,"Y"]
["Treguff Farm PV Generation 33kV S Stn","TreguffFarmPVGeneration33kVSStn",560361,0.35899999999999999,null,500,"Y",3,"Y"]
["Trethomas 33/11kV S Stn","Trethomas33/11kVSStn",540234,0.32200000000000001,null,500,"Y",3,"Y"]
["Trevaughan 33/11kV S Stn","Trevaughan33/11kVSStn",580247,0.7,"Y",500,"Y",3,"Y"]
["Trident Park 33kv Waste Generation 33kV S Stn","TridentPark33kvWasteGeneration33kVSStn",510447,0.7,"Y",500,"Y",3,"Y"]
["Trident Park Generation 33kV S Stn","TridentParkGeneration33kVSStn",510356,0.09,null,500,"Y",3,"Y"]
["Trostre Grid 132/33kV S Stn","TrostreGrid132/33kVSStn",520038,0.14000000000000001,null,1000,"Y",3,"Y"]
["Trowbridge 132/11kV S Stn","Trowbridge132/11kVSStn",510902,0.2,"Y",1000,"Y",1,"Y"]
["Tumble 33/11kV S Stn","Tumble33/11kVSStn",520248,0.154,null,500,"Y",3,"Y"]
["Uplands Swansea 33/11kV S Stn","UplandsSwansea33/11kVSStn",520250,0.7,"Y",500,"Y",3,"Y"]
["Upper Bank 33/11kV S Stn","UpperBank33/11kVSStn",520251,0.7,"Y",500,"Y",3,"Y"]
["Upper Boat 132/11kV S Stn","UpperBoat132/11kVSStn",540039,0.2,"Y",2629,"",1,"Y"]
["Usk 66/11kV S Stn","Usk66/11kVSStn",530252,0.248,null,294,null,3,"Y"]
["Uskmouth 275/132kV S Stn","Uskmouth275/132kVSStn",530046,0.2,"Y",901,"",1,"Y"]
["Victoria Road 33/11kV S Stn","VictoriaRoad33/11kVSStn",560253,0.12,null,500,"Y",3,"Y"]
["Waterston 132/11kV S Stn","Waterston132/11kVSStn",600040,0.42,null,1000,"Y",1,"Y"]
["Waterton Industrial Primary 132/11kV S Stn","WatertonIndustrialPrimary132/11kVSStn",560292,0.16,null,1000,"Y",1,"Y"]
["Wattstown 33/11kV S Stn","Wattstown33/11kVSStn",540255,0.35199999999999998,null,700,"",3,"Y"]
["Waunarlwyd 33kV S Stn","Waunarlwyd33kVSStn",520145,0.39300000000000002,null,500,"Y",3,"Y"]
["Waunarlwydd STOR Generation 33kV S Stn","WaunarlwyddSTORGeneration33kVSStn",520344,0.39300000000000002,null,500,"Y",3,"Y"]
["Waun Y Pound Gas Stor 33kV S Stn","WaunYPoundGasStor33kVSStn",550422,1.31,null,500,"Y",3,"Y"]
["Wear Point Wind Farm 33kV S Stn","WearPointWindFarm33kVSStn",600349,0.8,null,500,"Y",3,"Y"]
["Wern 33/11kV S Stn","Wern33/11kVSStn",560256,0.7,"Y",500,"Y",3,"Y"]
["West Cross 33/11kV S Stn","WestCross33/11kVSStn",520258,0.184,null,500,"Y",3,"Y"]
["Western Coal 33/11kV S Stn","WesternCoal33/11kVSStn",520334,0.7,"Y",500,"Y",3,"Y"]
["Westfa 33/11kV S Stn","Westfa33/11kVSStn",520118,2.04,null,500,"Y",3,"Y"]
["Westfa 33/11kV S Stn","Westfa33/11kVSStn",520259,0.10100000000000001,null,500,"Y",3,"Y"]
["West Farm PV Generation 33kV S Stn","WestFarmPVGeneration33kVSStn",600351,0.7,"Y",500,"Y",3,"Y"]
["W G W B Towy Intake 33kV S Stn","WGWBTowyIntake33kVSStn",590282,0.7,"Y",500,"Y",3,"Y"]
["Whitland 33/11kV S Stn","Whitland33/11kVSStn",580262,0.75,null,500,"Y",3,"Y"]
["Whitland Solar Park 33kV S Stn","WhitlandSolarPark33kVSStn",580337,0.152,null,500,"Y",3,"Y"]
["Whitton Mawr Solar Park 33kV S Stn","WhittonMawrSolarPark33kVSStn",510428,0.20599999999999999,null,405,"",3,"Y"]
["Withyhedges 33kV S Stn","Withyhedges33kVSStn",600323,0.27,null,500,"Y",3,"Y"]
["Wood Street 33/11kV S Stn","WoodStreet33/11kVSStn",510310,0.61,null,500,"Y",3,"Y"]
["Yerbeston Chapel Hill Solar Farm 33kV S Stn","YerbestonChapelHillSolarFarm33kVSStn",600385,0.39,null,500,"Y",3,"Y"]
["Yerbeston Solar Farm 33kV S Stn","YerbestonSolarFarm33kVSStn",600370,0.252,null,500,"Y",3,"Y"]
["Ynysfeio 33/11kV S Stn","Ynysfeio33/11kVSStn",540263,0.20399999999999999,null,500,"Y",3,"Y"]
["Ynys Street 33/11kV S Stn","YnysStreet33/11kVSStn",560265,0.106,null,500,"Y",3,"Y"]

{"sheet":"Source-EM-Num","index":18,"n_rows":739,"n_cols":8,"rows_kept":739,"cut":false,"hidden":true,"merged":[]}
[1,2,3,4,5,6,7,8]
["SUBSTATION_NUMBER_EM","SUBSTATION_NAME","ZE","Assumed ZE","UE","Assumed UE","t","Assumed t"]
[680001,"Staythorpe C 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
[680002,"Ratcliffe 400/132kV S Stn",6.4399999999999999E-2,null,1269,"",1,"Y"]
[680005,"Drakelow 275/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
[680006,"Willington 400/275/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
[680007,"Chesterfield 275/132/33kV S Stn",5.6000000000000001E-2,null,1070,"",3,"Y"]
[680009,"Burton South 132/33kV S Stn",0.1,null,2006,"",3,"Y"]
[680010,"Pinxton 132kV S Stn",0.13400000000000001,null,601,"",1,"Y"]
[680011,"Annesley 132/33kV S Stn",8.2000000000000003E-2,null,370,"",3,"Y"]
[680012,"Clipstone 132/33kV S Stn",0.18,null,477,"",3,"Y"]
[680013,"Checkerhouse 132/33kV S Stn",0.21,null,685,"",3,"Y"]
[680014,"Willoughby 132/33kV S Stn",7.9000000000000001E-2,null,329,"",3,"Y"]
[680015,"Nottingham East 132/33kV S Stn",3.2000000000000001E-2,null,275,"",3,"Y"]
[680016,"Whitwell 132/33kV S Stn",0.42699999999999999,null,1320,"",3,"Y"]
[680017,"Worksop 132/33kV S Stn",0.14399999999999999,null,586,"",3,"Y"]
[680018,"Mansfield 132/33kV S Stn",0.1,null,383,"",3,"Y"]
[680019,"Toton 132/33kV S Stn",9.6000000000000002E-2,null,567,"",3,"Y"]
[680020,"Staythorpe B 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[680021,"Retford 132/25kV S Stn",0.253,null,1204,"",1,"Y"]
[680022,"Nottingham North 132/33/11kV S Stn",1.7999999999999999E-2,null,160,"",3,"Y"]
[680023,"Nottingham 132/33kV S Stn",7.6999999999999999E-2,null,601,"",3,"Y"]
[680028,"Buxton 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[680029,"Derby South 132/33kV S Stn",0.05,null,481,"",3,"Y"]
[680030,"Spondon A 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[680031,"Spondon 'B' 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
[680032,"Chesterfield 33kV S Stn",5.6000000000000001E-2,null,1070,"",3,"Y"]
[680033,"Burton 132/33/11kV S Stn",1.9E-2,null,141,"",3,"Y"]
[680034,"Burnaston 132/11kV S Stn",9.0999999999999998E-2,null,1237,"",1,"Y"]
[680035,"Gresley 132/33kV S Stn",0.11700000000000001,null,671,"",3,"Y"]
[680036,"Heanor 132/33kV S Stn",9.5000000000000001E-2,null,522,"",3,"Y"]
[680037,"Alfreton 132/33kV S Stn",0.193,null,752,"",3,"Y"]
[680038,"Goitside 132/33kV S Stn",9.1999999999999998E-2,null,88,"",3,"Y"]
[680039,"Staveley 132/33kV S Stn",4.8599999999999997E-2,null,372,"",3,"Y"]
[680040,"Winster 132/33kV S Stn",0.2,"Y",565,"",3,"Y"]
[680041,"Derby 132/33/11kV S Stn",8.4000000000000005E-2,null,375,"",3,"Y"]
[680042,"Stanton 132/33kV S Stn",7.3200000000000001E-2,null,457,"",3,"Y"]
[680043,"Uttoxeter 132/33kV S Stn",0.156,null,569,"",3,"Y"]
[680068,"Stoke Bardolph 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
[680069,"Loscoe 132kV S Stn",0.11,null,576,"",1,"Y"]
[690001,"Berkswell 275/132kV S Stn",0.2,"Y",350,"",1,"Y"]
[690002,"Coventry 275/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
[690003,"Bicker Fen 400/132kV S Stn",0.04,null,710,"",1,"Y"]
[690004,"Enderby 400/132kV S Stn",6.5000000000000002E-2,null,849,"",1,"Y"]
[690005,"Walpole 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
[690006,"Bradwell Abbey 132/33kV S Stn",9.4E-2,null,486,"",3,"Y"]
[690007,"Grendon 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
[690008,"Corby 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
[690010,"Harbury 132/33kV S Stn",0.06,null,281,"",3,"Y"]
[690011,"Tamworth Town 132/33/11kV S Stn",3.4000000000000002E-2,null,217,"",3,"Y"]
[690012,"Coventry North 132/33kV S Stn",7.2999999999999995E-2,null,752,"",3,"Y"]
[690013,"Coventry Central 132/33kV S Stn",9.2999999999999999E-2,null,331,"",3,"Y"]
[690014,"Coventry South 132/33kV S Stn",5.7000000000000002E-2,null,553,"",3,"Y"]
[690015,"Coventry West 132/33kV S Stn",0.12,null,1161,"",3,"Y"]
[690016,"Tamworth 132/33kV S Stn",4.7E-2,null,301,"",3,"Y"]
[690017,"Rugby 132/33/25/11kV S Stn",4.2000000000000003E-2,null,361,"",3,"Y"]
[690018,"Nuneaton 132/33kV S Stn",8.5000000000000006E-2,null,632,"",3,"Y"]
[690020,"Warwick 132/33/11kV S Stn",4.1000000000000002E-2,null,274,"",3,"Y"]
[690021,"Middlemarsh 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[690022,"Loughborough 132/33/11kV S Stn",9.1999999999999998E-2,null,436,"",3,"Y"]
[690023,"Leicester North 132/33kV S Stn",0.1,null,113,"",3,"Y"]
[690024,"Coalville 132/33kV S Stn",0.109,null,382,"",3,"Y"]
[690025,"Leicester East 132/33kV S Stn",3.6999999999999998E-2,null,68,"",3,"Y"]
[690026,"Leicester 132/33kV S Stn",4.2999999999999997E-2,null,524,"",1,"Y"]
[690027,"Wigston 132/33/11kV S Stn",0.2,"Y",393,"",3,"Y"]
[690028,"Kibworth 132/33kV S Stn",9.5000000000000001E-2,null,319,"",3,"Y"]
[690029,"Hinckley 132/33/11kV S Stn",0.159,null,872,"",3,"Y"]
[690030,"Skegness 132/33kV S Stn",5.0999999999999997E-2,null,192,"",3,"Y"]
[690031,"Grantham North 132/25/11kV S Stn",0.104,null,376,"",1,"Y"]
[690032,"Grantham South 132kV S Stn",0.2,null,700,"",1,"Y"]
[690033,"Melton Mowbray 132/33kV S Stn",4.2999999999999997E-2,null,242,"",3,"Y"]
[690034,"Asfordby 132kV S Stn",9.5000000000000001E-2,null,185,"",1,"Y"]
[690035,"Stamford 132/33kV S Stn",5.6000000000000001E-2,null,222,"",3,"Y"]
[690036,"Spalding 132/33kV S Stn",3.4000000000000002E-2,null,147,"",3,"Y"]
[690037,"Sleaford 132/33kV S Stn",0.13700000000000001,null,349,"",3,"Y"]
[690038,"Oakham 132/33kV S Stn",8.6999999999999994E-2,null,413,"",3,"Y"]
[690039,"Bourne West 132/25kV S Stn",0.17399999999999999,null,1366,"",1,"Y"]
[690040,"South Holland 132/33kV S Stn",3.9E-2,null,359,"",3,"Y"]
[690041,"Grantham 132/33kV S Stn",0.3,null,1096,"",3,"Y"]
[690042,"Hawton 132/33kV S Stn",7.0000000000000007E-2,null,469,"",3,"Y"]
[690043,"Boston 132/33kV S Stn",3.9E-2,null,257,"",3,"Y"]
[690044,"Bourne 132/33kV S Stn",0.09,null,844,"",3,"Y"]
[690045,"Stony Stratford 132/33kV S Stn",9.1999999999999998E-2,null,1074,"",3,"Y"]
[690046,"Bletchley 132/33kV S Stn",2.7E-2,null,166,"",3,"Y"]
[690047,"Brackley 132/33kV S Stn",0.1,null,637,"",3,"Y"]
[690048,"Corby North 132kV S Stn",6.5000000000000002E-2,null,1049,"",1,"Y"]
[690049,"Irthlingborough 132/33kV S Stn",6.5000000000000002E-2,null,131,"",3,"Y"]
[690050,"Kettering 132/33kV S Stn",0.02,null,168,"",3,"Y"]
[690051,"Wellingborough 132/33kV S Stn",4.4999999999999998E-2,null,217,"",3,"Y"]
[690052,"Daventry 132/33kV S Stn",4.4999999999999998E-2,null,147,"",3,"Y"]
[690053,"Northampton East 132/33kV S Stn",0.09,null,637,"",3,"Y"]
[690054,"Northampton West 132/33kV S Stn",5.2999999999999999E-2,null,1000,"Y",3,"Y"]
[690055,"Northampton 132/33kV S Stn",5.2999999999999999E-2,null,570,"",3,"Y"]
[690057,"Lincoln Main 132/33/11kV S Stn",0.04,null,236,"",3,"Y"]
[690058,"Lincoln Local 132kV S Stn",7.0000000000000007E-2,null,261,"",1,"Y"]
[690059,"Warwick Grid 132/11kV S Stn",4.1000000000000002E-2,null,274,"",1,"Y"]
[690060,"Willesley 33/11kV S Stn",0.23200000000000001,null,220,"",3,"Y"]
[690061,"East Claydon 400/132kV S Stn",3.9E-2,null,936,"",1,"Y"]
[690063,"North Greetwell 132kV S Stn",0.23200000000000001,null,1392,"",1,"Y"]
[690064,"Hatton Gas Compressor 132kV S Stn",0.15,null,480,"",1,"Y"]
[690067,"Pailton 33kV S Stn",0.19,null,807,"",3,"Y"]
[690068,"Sleaford REP 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[690069,"Clay Lake Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[690070,"Bowbridge STOR Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[690071,"Old Dalby Lodge Wind Farm 33kV S Stn",0.13900000000000001,null,285,"",3,"Y"]
[690073,"Lincoln No 2 33kV S Stn",0.04,null,236,"",3,"Y"]
[690074,"Raunds 33kV S Stn",0.12,null,190,"",3,"Y"]
[690075,"East Claydon 132/33kV S Stn",3.9E-2,null,936,"",3,"Y"]
[720004,"Lea Marston 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
[870004,"Burton South 33kV S Stn",0.1,null,843,"",3,"Y"]
[870005,"Derby South 33kV S Stn",0.05,null,134,"",3,"Y"]
[870006,"Spondon 33kV S Stn",7.1999999999999995E-2,null,984,"",3,"Y"]
[870007,"Heanor 33kV S Stn",9.5000000000000001E-2,null,522,"",3,"Y"]
[870009,"Uttoxeter 33kV S Stn",0.156,null,569,"",3,"Y"]
[870010,"Gresley 33kV S Stn",0.11700000000000001,null,671,"",3,"Y"]
[870011,"Stanton 33kV S Stn",7.3200000000000001E-2,null,457,"",3,"Y"]
[870012,"Derby 33kV S Stn",8.4000000000000005E-2,null,375,"",3,"Y"]
[870013,"Barton Under Needwood 33/11kV S Stn",0.16500000000000001,null,185,"",3,"Y"]
[870014,"Trent Lane 33/11kV S Stn",0.22600000000000001,null,339,"",3,"Y"]
[870015,"Eagle Centre 33/11kV S Stn",0.1,null,95,"",3,"Y"]
[870016,"Bombardier 33kV S Stn",5.3999999999999999E-2,null,127,"",3,"Y"]
[870017,"Melbourne 33/11kV S Stn",0.129,null,249,"",3,"Y"]
[870019,"Sinfin C 33kV S Stn",8.1000000000000003E-2,null,148,"",3,"Y"]
[870022,"Heanor 33/11kV S Stn",9.5000000000000001E-2,null,522,"",3,"Y"]
[870026,"Rocester 33/11kV S Stn",0.13100000000000001,null,197,"",3,"Y"]
[870027,"Church Street 33/11kV S Stn",1.4999999999999999E-2,null,206,"",3,"Y"]
[870028,"Marchington 33/11kV S Stn",0.215,null,338,"",3,"Y"]
[870029,"Wellington Street 33/11kV S Stn",8.5000000000000006E-2,null,172,"",3,"Y"]
[870030,"Ashbourne 33/11kV S Stn",0.125,null,230,"",3,"Y"]
[870031,"Hatton 33/11kV S Stn",4.3999999999999997E-2,null,88,"",3,"Y"]
[870032,"Station Street 33/11kV S Stn",0.26,null,248,"",3,"Y"]
[870033,"Ravensdale Park 33/11kV S Stn",0.20200000000000001,null,290,"",3,"Y"]
[870034,"Bretby 33/11kV S Stn",8.8999999999999996E-2,null,130,"",3,"Y"]
[870035,"Trent Alloys 33/11kV S Stn",0.17399999999999999,null,216,"",3,"Y"]
[870036,"Derby 132/11kV S Stn",8.4000000000000005E-2,null,375,"",1,"Y"]
[870037,"Woodville 33/11kV S Stn",0.28199999999999997,null,333,"",3,"Y"]
[870038,"Mackworth 33/11kV S Stn",9.8000000000000004E-2,null,200,"",3,"Y"]
[870039,"Darley Abbey 33/11kV S Stn",0.09,null,132,"",3,"Y"]
[870040,"Normanton 33/11kV S Stn",0.11899999999999999,null,238,"",3,"Y"]
[870041,"Sinfin Lane 33/11kV S Stn",8.1000000000000003E-2,null,148,"",3,"Y"]
[870042,"Morley 33/11kV S Stn",0.104,null,208,"",3,"Y"]
[870043,"Allenton 33/11kV S Stn",8.1000000000000003E-2,null,229,"",3,"Y"]
[870044,"Chaddesden 33/11kV S Stn",8.7999999999999995E-2,null,205,"",3,"Y"]
[870045,"Osmaston Road 33/6.6kv S Stn",0.7,"Y",500,"Y",3,"Y"]
[870046,"Spondon 33/11kV S Stn",7.1999999999999995E-2,null,984,"",3,"Y"]
[870047,"Castle Donington 33/11kV S Stn",0.13600000000000001,null,171,"",3,"Y"]
[870048,"Ilkeston 33/11kV S Stn",0.17,null,276,"",3,"Y"]
[870049,"Little Hallam 33/11kV S Stn",0.17499999999999999,null,315,"",3,"Y"]
[870050,"Long Eaton 33/11kV S Stn",6.4000000000000001E-2,null,115,"",3,"Y"]
[870051,"Sandiacre 33/11kV S Stn",9.8000000000000004E-2,null,190,"",3,"Y"]
[870053,"Gresley 33/11kV S Stn",0.11700000000000001,null,671,"",3,"Y"]
[874558,"Burton 132/11kV S Stn",1.9E-2,null,141,"",1,"Y"]
[874972,"Smith Hall Farm Solar Plant 33kV S Stn",0.28999999999999998,null,235,"",3,"Y"]
[874987,"Aston House Solar Farm 33kV S Stn",0.23499999999999999,null,291,"",3,"Y"]
[874992,"Rolleston Park Solar Farm 33kV S Stn",0.16,null,255,"",3,"Y"]
[875000,"Burton 33kV S Stn",1.9E-2,null,141,"",3,"Y"]
[875036,"Green Lane Marchinton PV 33kV S Stn",0.24,null,411,"",3,"Y"]
[875043,"Moat Farm Draycott-In-The-Clay Solar Site 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[875065,"Holtwood Farm Solar Park 33kV S Stn",0.22,null,274,"",3,"Y"]
[875067,"Drakelow Solar Farm 33kV S Stn",0.18,null,119,"",3,"Y"]
[875073,"Derby Waste Sinfin Lane 33kV S Stn",0.125,null,334,"",3,"Y"]
[875086,"Trafalgar Park Gas Peaking S15 33kV S Stn",0.23,null,406,"",3,"Y"]
[875119,"Dayfields Farm PV 33kV S Stn",0.24,null,278,"",3,"Y"]
[875136,"Infinity Park 33/11kv S Stn",0.14799999999999999,null,410,"",3,"Y"]
[875141,"Taylor Lane STOR 33kV S Stn",2,null,522,"",3,"Y"]
[875155,"Nottingham Road STOR 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[875157,"Breach Farm 33kv S Stn",0.747,null,1141,"",3,"Y"]
[875166,"Twin Oaks STOR 33kV S Stn",0.56999999999999995,null,816,"",3,"Y"]
[880002,"Nottingham East 33kV S Stn",3.2000000000000001E-2,null,275,"",3,"Y"]
[880003,"Nottingham 33kV S Stn",7.6999999999999999E-2,null,601,"",3,"Y"]
[880004,"Toton 33kV S Stn",9.6000000000000002E-2,null,567,"",3,"Y"]
[880005,"Nottingham North 33kV S Stn",1.7999999999999999E-2,null,160,"",3,"Y"]
[880006,"Willoughby 33kV S Stn",7.9000000000000001E-2,null,329,"",3,"Y"]
[880009,"Toton 33/11kV S Stn",9.6000000000000002E-2,null,567,"",3,"Y"]
[880010,"Chilwell 33/11kV S Stn",0.106,null,190,"",3,"Y"]
[880011,"Hucknall 33/11kV S Stn",0.191,null,285,"",3,"Y"]
[880012,"Beeston 33/11kV S Stn",0.1,null,216,"",3,"Y"]
[880013,"Bilborough 33/11kV S Stn",0.13100000000000001,null,277,"",3,"Y"]
[880014,"Lenton 33/11kV S Stn",0.17599999999999999,null,412,"",3,"Y"]
[880015,"Cinderhill 33/11kV S Stn",0.09,null,136,"",3,"Y"]
[880016,"Boots 33/11kV S Stn",0.153,null,384,"",3,"Y"]
[880017,"North Wilford 33/11kV S Stn",6.6000000000000003E-2,null,193,"",3,"Y"]
[880018,"Ratcliffe On Soar 33/11kV S Stn",6.4399999999999999E-2,null,1269,"",3,"Y"]
[880019,"Bulwell 33/11kV S Stn",7.5999999999999998E-2,null,176,"",3,"Y"]
[880020,"Wollaton Road 33/11kV S Stn",6.5000000000000002E-2,null,130,"",3,"Y"]
[880021,"Nottingham North 132/11kV S Stn",1.7999999999999999E-2,null,160,"",1,"Y"]
[880022,"Talbot Street 33/11kV S Stn",0.13500000000000001,null,204,"",3,"Y"]
[880023,"East Leake 33/11kV S Stn",0.14399999999999999,null,215,"",3,"Y"]
[880024,"Clifton 33/11kV S Stn",9.7000000000000003E-2,null,363,"",3,"Y"]
[880025,"Castle Road 33/11kV S Stn",7.2999999999999995E-2,null,194,"",3,"Y"]
[880026,"Marlborough Road 33/11kV S Stn",0.161,null,243,"",3,"Y"]
[880027,"Arnold 33/11kV S Stn",0.16700000000000001,null,326,"",3,"Y"]
[880028,"West Bridgford 33/11kV S Stn",7.8E-2,null,118,"",3,"Y"]
[880029,"Mapperley 33/11kV S Stn",9.6000000000000002E-2,null,145,"",3,"Y"]
[880030,"Sneinton 33/11kV S Stn",9.1999999999999998E-2,null,141,"",3,"Y"]
[880031,"Calverton 33/11kV S Stn",0.27700000000000002,null,300,"",3,"Y"]
[880032,"Willoughby 33/11kV S Stn",7.9000000000000001E-2,null,329,"",3,"Y"]
[880033,"Keyworth 33/11kV S Stn",0.105,null,211,"",3,"Y"]
[880034,"Gedling 33/11kV S Stn",8.7999999999999995E-2,null,215,"",3,"Y"]
[880035,"Colwick 33/11kV S Stn",2.1999999999999999E-2,null,175,"",3,"Y"]
[880036,"Cotgrave 33/11kV S Stn",0.126,null,177,"",3,"Y"]
[880037,"Caythorpe 33/11kV S Stn",0.30499999999999999,null,573,"",3,"Y"]
[880038,"Sibthorpe 33/11kV S Stn",0.23,null,414,"",3,"Y"]
[880039,"Bingham 33/11kV S Stn",6.0999999999999999E-2,null,73,"",3,"Y"]
[880040,"St Anns 33/11kV S Stn",0.218,null,294,"",3,"Y"]
[880042,"London Road Heat Station 33kV S Stn",3.1E-2,null,47,"",3,"Y"]
[883330,"Willoughby STOR 33kV S Stn",7.9000000000000001E-2,null,500,"Y",3,"Y"]
[883349,"Lodge Farm Solar Park 33kV S Stn",0.09,null,132,"",3,"Y"]
[883362,"Watnall Primary 33/11kV S Stn",1.04,null,592,"",3,"Y"]
[883446,"Langar Solar Switch Room 33kV S Stn",0.16400000000000001,null,198,"",3,"Y"]
[883447,"Redfield Road 1 STOR 33kV S Stn",0.42,null,593,"",3,"Y"]
[883456,"Shelton Lodge Solar Generation 33kV S Stn",0.20300000000000001,null,285,"",3,"Y"]
[883465,"Stragglethorpe Road Pv Solar Park 33kv S Stn",0.128,null,236,"",3,"Y"]
[883503,"Redfield Road 2 STOR 33kV S Stn",0.36,null,683,"",3,"Y"]
[883570,"Private Road No 5 Colwick STOR 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[890003,"West Burton 400/132kV S Stn",3.7199999999999997E-2,null,599,"",1,"Y"]
[890006,"Clipstone 33kV S Stn",0.18,null,477,"",3,"Y"]
[890007,"Annesley 33kV S Stn",8.2000000000000003E-2,null,370,"",3,"Y"]
[890008,"Mansfield 33kV S Stn",0.1,null,383,"",3,"Y"]
[890009,"Whitwell 33kV S Stn",0.42699999999999999,null,1320,"",3,"Y"]
[890010,"Checkerhouse 33/11kV S Stn",0.21,null,685,"",3,"Y"]
[890011,"Worksop 33kV S Stn",0.14399999999999999,null,586,"",3,"Y"]
[890013,"Winster 33kV S Stn",0.17899999999999999,null,565,"",3,"Y"]
[890014,"Alfreton 33kV S Stn",0.193,null,752,"",3,"Y"]
[890015,"Staveley 33kV S Stn",4.8599999999999997E-2,null,372,"",3,"Y"]
[890016,"Goitside 33kV S Stn",9.1999999999999998E-2,null,88,"",3,"Y"]
[890017,"Daneshill Generation 33kV S Stn",0.28999999999999998,null,335,"",3,"Y"]
[890021,"Pinxton 132/11kV S Stn",0.13400000000000001,null,601,"",1,"Y"]
[890022,"Lindhurst Wind Farm 33kV S Stn",0.40400000000000003,null,553,"",3,"Y"]
[890023,"Sheepbridge 33/11kV S Stn",0.112,null,318,"",3,"Y"]
[890025,"Moorgreen 33/11kV S Stn",0.114,null,251,"",3,"Y"]
[890026,"Blackwell 33/11kV S Stn",0.114,null,201,"",3,"Y"]
[890027,"Huthwaite 33/11kV S Stn",7.9000000000000001E-2,null,132,"",3,"Y"]
[890028,"Westwood 33/11kV S Stn",0.219,null,314,"",3,"Y"]
[890029,"Teversal 33/11kV S Stn",0.105,null,205,"",3,"Y"]
[890030,"Skegby Lane 33/11kV S Stn",7.0000000000000007E-2,null,221,"",3,"Y"]
[890031,"Sutton Junction 33/11kV S Stn",0.10100000000000001,null,225,"",3,"Y"]
[890032,"Craggs Lane 33/11kV S Stn",0.156,null,293,"",3,"Y"]
[890033,"Annesley 33/11kV S Stn",8.2000000000000003E-2,null,370,"",3,"Y"]
[890034,"Shirebrook 33/11kV S Stn",0.23699999999999999,null,332,"",3,"Y"]
[890035,"Acreage Lane 33/11kV S Stn",0.59599999999999997,null,1173,"",3,"Y"]
[890036,"Mansfield 33/11kV S Stn",0.1,null,383,"",3,"Y"]
[890037,"Crown Farm 33/11kV S Stn",2.5999999999999999E-2,null,487,"",3,"Y"]
[890038,"Worksop West 33/11kV S Stn",0.157,null,308,"",3,"Y"]
[890039,"Lime Tree Place 33/11kV S Stn",0.154,null,233,"",3,"Y"]
[890040,"Clipstone 33/11kV S Stn",0.18,null,477,"",3,"Y"]
[890041,"Blidworth 33/11kV S Stn",0.64400000000000002,null,1173,"",3,"Y"]
[890042,"Holme Carr 33/11kV S Stn",0.314,null,566,"",3,"Y"]
[890043,"Kilton Road 33/11kV S Stn",0.23799999999999999,null,395,"",3,"Y"]
[890044,"Manton 33/11kV S Stn",0.27,null,385,"",3,"Y"]
[890045,"Budby 33/11kV S Stn",0.51200000000000001,null,737,"",3,"Y"]
[890046,"Warsop 33/11kV S Stn",0.25600000000000001,null,536,"",3,"Y"]
[890047,"Rufford 33/11kV S Stn",0.79200000000000004,null,1052,"",3,"Y"]
[890048,"Thoresby 33/11kV S Stn",0.31,null,2814,"",3,"Y"]
[890049,"Misson 33/11kV S Stn",0.17799999999999999,null,343,"",3,"Y"]
[890050,"Checkerhouse 33kV S Stn",0.21,null,685,"",3,"Y"]
[890051,"Ollerton 33/11kV S Stn",0.19,null,376,"",3,"Y"]
[890052,"Hallcroft Road 33/11kV S Stn",0.20599999999999999,null,225,"",3,"Y"]
[890053,"Ordsall Road 33/11kV S Stn",0.19400000000000001,null,360,"",3,"Y"]
[890054,"Bilsthorpe 33/11kV S Stn",0.2,null,396,"",3,"Y"]
[890055,"Bevercotes 33/11kV S Stn",0.17100000000000001,null,171,"",3,"Y"]
[890056,"Farnsfield 33/11kV S Stn",0.38700000000000001,null,766,"",3,"Y"]
[890057,"North Wheatley 33/11kV S Stn",0.53400000000000003,null,555,"",3,"Y"]
[890058,"Tuxford 33/11kV S Stn",0.23400000000000001,null,185,"",3,"Y"]
[890059,"Southwell 33/11kV S Stn",0.153,null,289,"",3,"Y"]
[890060,"Misterton 33/11kV S Stn",0.30099999999999999,null,286,"",3,"Y"]
[890061,"Carlton On Trent 33/11kV S Stn",0.67500000000000004,null,989,"",3,"Y"]
[890062,"Woodbeck 33/11kV S Stn",0.499,null,528,"",3,"Y"]
[890063,"Hindlow 33/11kV S Stn",1.3,null,2200,"",3,"Y"]
[890064,"Flagg 33/11kV S Stn",2.2000000000000002,null,2640,"",3,"Y"]
[890065,"Bakewell 33/11kV S Stn",0.3,null,268,"",3,"Y"]
[890066,"Eyam 33/11kV S Stn",0.5,null,685,"",3,"Y"]
[890067,"Longcliffe 33/11kV S Stn",0.65,null,1276,"",3,"Y"]
[890068,"Millclose 33/11kV S Stn",0.16400000000000001,null,273,"",3,"Y"]
[890069,"Robin Hood 33/11kV S Stn",0.26800000000000002,null,359,"",3,"Y"]
[890070,"Sheffield Road 33/11/6.6kV S Stn",0.13500000000000001,null,266,"",3,"Y"]
[890071,"Hopton 33/11kV S Stn",1.1970000000000001,null,1831,"",3,"Y"]
[890072,"Wingerworth 33/11kV S Stn",4.2999999999999997E-2,null,117,"",3,"Y"]
[890073,"Cromford 33/11kV S Stn",0.21,null,422,"",3,"Y"]
[890074,"Matlock 33/11kV S Stn",0.106,null,165,"",3,"Y"]
[890075,"Goitside 33/6.6kV S Stn",9.1999999999999998E-2,null,88,"",3,"Y"]
[890076,"Belper 33/11kV S Stn",8.3000000000000004E-2,null,120,"",3,"Y"]
[890077,"Ambergate 33/11kV S Stn",6.5000000000000002E-2,null,75,"",3,"Y"]
[890078,"Walton 33/11kV S Stn",0.16300000000000001,null,199,"",3,"Y"]
[890079,"Queens Park 33/11kV S Stn",0.1,null,159,"",3,"Y"]
[890080,"Staveley 33/11kV S Stn",4.8599999999999997E-2,null,372,"",3,"Y"]
[890081,"Robert Hyde 33/11kV S Stn",0.17699999999999999,null,350,"",3,"Y"]
[890082,"Denby 33/11kV S Stn",0.11799999999999999,null,250,"",3,"Y"]
[890083,"Eckington 33/11kV S Stn",0.122,null,262,"",3,"Y"]
[890084,"Grassmoor 33/11kV S Stn",0.08,null,182,"",3,"Y"]
[890085,"Clowne 33/11kV S Stn",0.5,null,884,"",3,"Y"]
[890086,"Somercotes 33/11kV S Stn",9.2999999999999999E-2,null,147,"",3,"Y"]
[890087,"Wessington 33/11kV S Stn",0.219,null,350,"",3,"Y"]
[890088,"Ripley 33/11kV S Stn",0.16300000000000001,null,319,"",3,"Y"]
[890089,"Halfway 33/11kV S Stn",0.11799999999999999,null,184,"",3,"Y"]
[890090,"Meadow Lane 33/11kV S Stn",0.215,null,424,"",3,"Y"]
[890091,"Westhorpe 33/11kV S Stn",6.5000000000000002E-2,null,205,"",3,"Y"]
[890093,"Bolsover 33/11kV S Stn",0.15,null,225,"",3,"Y"]
[890094,"Danesmoor 33/11kV S Stn",0.26300000000000001,null,108,"",3,"Y"]
[890095,"Biwaters 33/11kV S Stn",0.26200000000000001,null,349,"",3,"Y"]
[890098,"Staveley Works 33kV S Stn",6.3E-2,null,156,"",3,"Y"]
[890099,"Sherwood Park 33/11kV S Stn",0.14099999999999999,null,190,"",3,"Y"]
[897792,"Low Farm AD 33kV S Stn",0.27300000000000002,null,355,"",3,"Y"]
[898163,"Bentinck Generating Station 33kV S Stn",1.3,null,2275,"",3,"Y"]
[898181,"Stonish Hill Windfarm 33kV S Stn",0.14000000000000001,null,278,"",3,"Y"]
[898284,"Little Morton Solar Farm 33kV S Stn",8.5000000000000006E-2,null,134,"",3,"Y"]
[898308,"Welbeck Colliery Solar Generation 33kV S Stn",0.15,null,420,"",3,"Y"]
[898324,"Moat Farm Solar Farm 33kV S Stn",0.43,null,305,"",3,"Y"]
[898326,"Bilsthorpe Solar 33kV S Stn",0.27,null,208,"",3,"Y"]
[898340,"Eakring Solar Farm 33kV S Stn",0.22,null,395,"",3,"Y"]
[898344,"Welbeck Solar Farm 33kV S Stn",0.41,null,712,"",3,"Y"]
[898347,"Tiln Farm Solar Generation 33kV S Stn",0.19,null,246,"",3,"Y"]
[898350,"Thoresby Solar Farm 33kV S Stn",0.24,null,432,"",3,"Y"]
[898357,"Walkers Wood Solar Farm 33kV S Stn",0.35,null,581,"",3,"Y"]
[898371,"Cobb Farm Solar Generation 33kV S Stn",0.19600000000000001,null,175,"",3,"Y"]
[898432,"Lodge Farm Solar 33kV S Stn",0.09,null,132,"",3,"Y"]
[898435,"West End Farm Solar Generation 33kV S Stn",0.2,null,235,"",3,"Y"]
[898436,"Arkwright Solar 33kV S Stn",0.49,null,821,"",3,"Y"]
[898444,"Averill Solar Farm 33kV S Stn",0.13,null,150,"",3,"Y"]
[898460,"The Brek Solar 33kv S Stn",0.14199999999999999,null,404,"",3,"Y"]
[898475,"Littlewood Farm PV 33kV S Stn",0.28999999999999998,null,442,"",3,"Y"]
[898478,"Oxcroft Solar Farm 33kV S Stn",0.11899999999999999,null,204,"",3,"Y"]
[898482,"Twin Yards Solar Farm 33kV S Stn",0.23,null,283,"",3,"Y"]
[898483,"Retford Road Solar Generation 33kV S Stn",0.53,null,695,"",3,"Y"]
[898500,"Erin Road 33/11kV S Stn",0.25,null,397,"",3,"Y"]
[898530,"Garnham Close STOR 33kV S Stn",0.2,null,102,"",3,"Y"]
[898541,"Hermitage Lane Generation 33kV S Stn",0.61,null,325,"",3,"Y"]
[898555,"Bilsthorpe P V Generation 33kV S Stn",0.24,null,496,"",3,"Y"]
[898563,"Bolsover Moor Quarry PV Solar Farm 33kV S Stn",0.35,null,487,"",3,"Y"]
[898663,"Asher Lane STOR 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[900002,"Lincoln No 1 33kV S Stn",0.04,null,236,"",3,"Y"]
[900003,"Hawton 33kV S Stn",7.0000000000000007E-2,null,469,"",3,"Y"]
[900004,"Boston 33kV S Stn",3.9E-2,null,257,"",3,"Y"]
[900005,"Skegness 33kV S Stn",5.0999999999999997E-2,null,192,"",3,"Y"]
[900006,"Sleaford Road, Boston 33kV S Stn",0.11,null,330,"",3,"Y"]
[900007,"Marsh Lane 33/11kV S Stn",0.105,null,230,"",3,"Y"]
[900008,"Bambers Farm Wind Generation 33kV S Stn",0.2,null,272,"",3,"Y"]
[900009,"Beevor Street 33/11kV S Stn",0.15,null,300,"",3,"Y"]
[900010,"The Hollies Wind Farm 33kV S Stn",7.0000000000000007E-2,null,165,"",3,"Y"]
[900011,"Fernwood 33/11kV S Stn",0.13200000000000001,null,318,"",3,"Y"]
[900012,"Trusthorpe 33/11kV S Stn",0.115,null,230,"",3,"Y"]
[900013,"Horncastle 33/11kV S Stn",0.127,null,251,"",3,"Y"]
[900014,"Alford 33/11kV S Stn",0.26500000000000001,null,441,"",3,"Y"]
[900015,"Chapel St Leonards 33/11kV S Stn",0.219,null,438,"",3,"Y"]
[900016,"Spilsby 33kV S Stn",0.20300000000000001,null,357,"",3,"Y"]
[900017,"Ingoldmells 33/11kV S Stn",0.105,null,210,"",3,"Y"]
[900018,"Warth Lane 33/11kV S Stn",0.12,null,360,"",3,"Y"]
[900019,"Wrangle 33/11kV S Stn",0.17299999999999999,null,322,"",3,"Y"]
[900020,"Stickney 33kV S Stn",0.27200000000000002,null,310,"",3,"Y"]
[900021,"Langrick 33/11kV S Stn",0.22900000000000001,null,307,"",3,"Y"]
[900022,"Mount Bridge 33/11kV S Stn",0.08,null,151,"",3,"Y"]
[900023,"Great Hale 33/11kV S Stn",0.19600000000000001,null,226,"",3,"Y"]
[900024,"Newark Junction 33/11kV S Stn",0.161,null,240,"",3,"Y"]
[900025,"Swinderby 33/11kV S Stn",0.27200000000000002,null,266,"",3,"Y"]
[900026,"Hawton 33/11kV S Stn",7.0000000000000007E-2,null,469,"",3,"Y"]
[900027,"South Carlton 33kV S Stn",0.129,null,249,"",3,"Y"]
[900028,"Doddington Park 33/11kV S Stn",7.9000000000000001E-2,null,146,"",3,"Y"]
[900029,"North Hykeham 33/11kV S Stn",9.4E-2,null,150,"",3,"Y"]
[900030,"Rookery Lane 33/11kV S Stn",0.13,null,208,"",3,"Y"]
[900031,"Ruston & Hornsby 33/11kV S Stn",6.4000000000000001E-2,null,278,"",3,"Y"]
[900032,"Anderson Lane 33/11kV S Stn",0.121,null,369,"",3,"Y"]
[900033,"Waddington 33/11kV S Stn",0.13300000000000001,null,219,"",3,"Y"]
[900034,"Lincoln Local No 2 132/11kV S Stn",7.0000000000000007E-2,null,260,"",1,"Y"]
[900035,"Fiskerton 33/11kV S Stn",0.19,null,392,"",3,"Y"]
[900036,"Wragby 33/11kV S Stn",6.7000000000000004E-2,null,122,"",3,"Y"]
[900037,"Metheringham 33/11kV S Stn",0.13,null,250,"",3,"Y"]
[900038,"Woodhall Spa 33/11kV S Stn",0.219,null,799,"",3,"Y"]
[900039,"Tattershall 33/11kV S Stn",0.09,null,180,"",3,"Y"]
[900040,"Lincoln No 5 132/11kV S Stn",0.04,null,236,"",1,"Y"]
[904540,"EFW Paving Way 33kV S Stn",7.3999999999999996E-2,null,164,"",3,"Y"]
[905191,"Croft End Solar Farm 33kV S Stn",7.0000000000000007E-2,null,165,"",3,"Y"]
[905663,"Burton Pedwardine Solar Park 1 33kV S Stn",0.17799999999999999,null,267,"",3,"Y"]
[906124,"Whitecross Lane Solar Park Burton Pedwardine 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[906126,"Leverton Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[906387,"Fiskerton Solar Farm 33kV S Stn",8.4000000000000005E-2,null,229,"",3,"Y"]
[906537,"Grange Farm Solar Kirkby On Bain 33kV S Stn",5.1999999999999998E-2,null,46,"",3,"Y"]
[906775,"Canopus Solar Farm 33kV S Stn",5.8000000000000003E-2,null,119,"",3,"Y"]
[906936,"Lincoln Farm Solar 33kV S Stn",0.14799999999999999,null,359,"",3,"Y"]
[906972,"Hawton Wind Farm 33kV S Stn",0.27,null,684,"",3,"Y"]
[907000,"Lincoln Local No 4 132/11kV S Stn",7.0000000000000007E-2,null,261,"",1,"Y"]
[907046,"Leverton Battery Storage 33kV S Stn",0.91200000000000003,null,218,"",3,"Y"]
[907058,"Boston Biomass Generation 33kV S Stn",9.6000000000000002E-2,null,261,"",3,"Y"]
[907556,"Branston South Solar Farm 33kV S Stn",0.22,null,418,"",3,"Y"]
[910003,"Grantham 33kV S Stn",0.3,null,1096,"",3,"Y"]
[910004,"Stamford 33kV S Stn",5.6000000000000001E-2,null,222,"",3,"Y"]
[910005,"Bourne 33kV S Stn",0.09,null,844,"",3,"Y"]
[910006,"Melton Mowbray 33kV S Stn",4.2999999999999997E-2,null,242,"",3,"Y"]
[910007,"Oakham 33kV S Stn",8.6999999999999994E-2,null,413,"",3,"Y"]
[910008,"Sleaford 33kV S Stn",0.13700000000000001,null,349,"",3,"Y"]
[910009,"Spalding Clay Lake 33kV S Stn",3.4000000000000002E-2,null,145,"",3,"Y"]
[910010,"South Holland 33kV S Stn",3.9E-2,null,359,"",3,"Y"]
[910015,"Deeping St Nicholas Wind Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[910016,"Redhouse Farm Wind Farm Gedney 33kV S Stn",4.8000000000000001E-2,null,50,"",3,"Y"]
[910017,"Wardentree Park 33/11kV S Stn",0.18,null,266,"",3,"Y"]
[910018,"Grantham North 132/11kV S Stn",0.104,null,376,"",1,"Y"]
[910019,"Bicker Fen Wind Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[910021,"Sleaford 33/11kV S Stn",0.13700000000000001,null,349,"",3,"Y"]
[910022,"Kirton 33/11kV S Stn",9.6000000000000002E-2,null,192,"",3,"Y"]
[910023,"Spalding Park Road 33/11kV S Stn",0.06,null,90,"",3,"Y"]
[910024,"Donington 33/11kV S Stn",0.128,null,192,"",3,"Y"]
[910025,"Dowsby Fen 33/11kV S Stn",0.154,null,394,"",3,"Y"]
[910026,"Holbeach 33/11kV S Stn",7.5999999999999998E-2,null,111,"",3,"Y"]
[910027,"Long Sutton 33/11kV S Stn",0.13400000000000001,null,257,"",3,"Y"]
[910028,"Spalding Clay Lake 33/11kV S Stn",3.4000000000000002E-2,null,145,"",3,"Y"]
[910029,"Crowland 33/11kV S Stn",0.13800000000000001,null,215,"",3,"Y"]
[910030,"Whaplode Drove 33/11kV S Stn",0.27800000000000002,null,325,"",3,"Y"]
[910031,"Cranwell 33/11kV S Stn",0.11,null,220,"",3,"Y"]
[910032,"Bourne 33/11kV S Stn",0.09,null,844,"",3,"Y"]
[910033,"Ruskington 33/11kV S Stn",0.129,null,235,"",3,"Y"]
[910034,"New Beacon Road 33/11kV S Stn",0.08,null,102,"",3,"Y"]
[910035,"Billingborough 33/11kV S Stn",0.32300000000000001,null,633,"",3,"Y"]
[910036,"Grantham South 132/11kV S Stn",0.2,null,700,"",1,"Y"]
[910037,"Westborough 33/11kV S Stn",0.29699999999999999,null,425,"",3,"Y"]
[910038,"Bottesford 33/11kV S Stn",0.217,null,260,"",3,"Y"]
[910039,"Melton Mowbray 33/11kV S Stn",4.2999999999999997E-2,null,242,"",3,"Y"]
[910040,"Skillington 33/11kV S Stn",0.433,null,550,"",3,"Y"]
[910041,"Easton 33/11kV S Stn",0.113,null,90,"",3,"Y"]
[910042,"Tunnel Bank 33/11kV S Stn",0.17,null,340,"",3,"Y"]
[910043,"Old Dalby 33/11kV S Stn",0.26100000000000001,null,381,"",3,"Y"]
[910044,"Holwell 33/11kV S Stn",7.6999999999999999E-2,null,106,"",3,"Y"]
[910045,"Market Deeping 33/11kV S Stn",0.19,null,258,"",3,"Y"]
[910046,"West Deeping 33/11kV S Stn",0.41499999999999998,null,872,"",3,"Y"]
[910047,"Asfordby 132/11kV S Stn",9.5000000000000001E-2,null,185,"",1,"Y"]
[910048,"Market Overton 33/11kV S Stn",0.23200000000000001,null,282,"",3,"Y"]
[910049,"Regent Street 33/11kV S Stn",0.21,null,414,"",3,"Y"]
[910050,"Stamford 33/11kV S Stn",5.6000000000000001E-2,null,222,"",3,"Y"]
[910051,"Ketton Cement 33/11kV S Stn",0.17299999999999999,null,284,"",3,"Y"]
[910052,"Exton 33/11kV S Stn",0.52800000000000002,null,737,"",3,"Y"]
[910053,"Wittering 33/11kV S Stn",0.08,null,98,"",3,"Y"]
[910054,"Tinwell Road 33/11kV S Stn",0.17299999999999999,null,268,"",3,"Y"]
[910055,"Oakham 33/11kV S Stn",8.6999999999999994E-2,null,413,"",3,"Y"]
[910056,"Empingham 33/11kV S Stn",0.10100000000000001,null,148,"",3,"Y"]
[910057,"Uppingham 33/11kV S Stn",0.24399999999999999,null,435,"",3,"Y"]
[910058,"Leadenham 33/11kV S Stn",8.5999999999999993E-2,null,248,"",3,"Y"]
[916813,"Ermine Farm Solar Farm 33kV S Stn",0.16,null,500,"Y",3,"Y"]
[917435,"Deepdale Solar Farm 33kV S Stn",0.12,null,123,"",3,"Y"]
[917515,"The Grange Windfarm 33kV S Stn",5.1999999999999998E-2,null,81,"",3,"Y"]
[917543,"Nowhere Farm PV 33kV S Stn",0.05,null,60,"",3,"Y"]
[917572,"Decoy Farm Generation 33kV S Stn",0.251,null,314,"",3,"Y"]
[917574,"Horsemoor Drove Solar 33kV S Stn",0.06,null,121,"",3,"Y"]
[917592,"Copley Farm Solar Generation 33kV S Stn",0.15,null,290,"",3,"Y"]
[917647,"Mill Farm Solar Boothby Great Wood 33kV S Stn",0.21299999999999999,null,234,"",3,"Y"]
[917670,"French Farm Wind Farm 33kV S Stn",0.105,null,234,"",3,"Y"]
[917673,"Equitix ESI CHP Notts 33kV S Stn",0.13,null,323,"",3,"Y"]
[917678,"RAF Cranwell High G Facility 33kV S Stn",1.04,null,1372,"",3,"Y"]
[917757,"Mill Farm Battery Storage 33kV S Stn",0.57499999999999996,null,642,"",3,"Y"]
[917778,"North Rauceby 33kV S Stn",0.93,null,252,"",3,"Y"]
[920001,"Kibworth 33kV S Stn",9.5000000000000001E-2,null,319,"",3,"Y"]
[920002,"Loughborough 33kV S Stn",9.1999999999999998E-2,null,436,"",3,"Y"]
[920003,"Leicester North 33kV S Stn",0.1,null,113,"",3,"Y"]
[920004,"Leicester East 33kV S Stn",3.6999999999999998E-2,null,35,"",3,"Y"]
[920005,"Wigston 33kV S Stn",6.0999999999999999E-2,null,393,"",3,"Y"]
[920006,"Leicester 33kV S Stn",4.2999999999999997E-2,null,524,"",1,"Y"]
[920007,"Corby No2 33kV S Stn",7.3999999999999996E-2,null,1221,"",3,"Y"]
[920008,"Kettering 33kV S Stn",0.02,null,168,"",3,"Y"]
[920009,"Pytchley Road 33/11kV S Stn",7.5999999999999998E-2,null,131,"",3,"Y"]
[920010,"Wymington Wykes Generation 33kV S Stn",4.8000000000000001E-2,null,78,"",3,"Y"]
[920011,"Weldon Shanks Generation 33kV S Stn",0.74,null,1110,"",3,"Y"]
[920012,"Burton Wold Wind Farm Generation 33kV S Stn",0.13600000000000001,null,256,"",3,"Y"]
[920013,"Kettering North 33/11kV S Stn",5.8999999999999997E-2,null,142,"",3,"Y"]
[920016,"Wellingborough 132/11kV S Stn",4.4999999999999998E-2,null,217,"",1,"Y"]
[920017,"Wigston Magna 33/11kV S Stn",7.9000000000000001E-2,null,34,"",3,"Y"]
[920018,"British Gypsum 33/11kV S Stn",0.113,null,219,"",3,"Y"]
[920019,"Shepshed 33/11kV S Stn",0.08,null,154,"",3,"Y"]
[920020,"Loughborough 132/11kV S Stn",9.1999999999999998E-2,null,436,"",1,"Y"]
[920021,"Brush 33/11kV S Stn",0.09,null,176,"",3,"Y"]
[920022,"Quorn 33/11kV S Stn",0.20100000000000001,null,390,"",3,"Y"]
[920023,"Lero 33/6.6kV S Stn",0.09,null,166,"",3,"Y"]
[920024,"Mansfield Street 33/11kV S Stn",0.157,null,393,"",3,"Y"]
[920025,"Mountsorrel 33/11kV S Stn",0.192,null,369,"",3,"Y"]
[920026,"Beaumont Leys 33/11kV S Stn",0.13,null,275,"",3,"Y"]
[920027,"Groby Road 33/11kV S Stn",8.4000000000000005E-2,null,164,"",3,"Y"]
[920028,"Jupiter 33/11kV S Stn",7.4999999999999997E-2,null,153,"",3,"Y"]
[920029,"Birstall 33/11kV S Stn",7.6999999999999999E-2,null,182,"",3,"Y"]
[920030,"Leicester North 33/11kV S Stn",0.1,null,113,"",3,"Y"]
[920031,"Braunstone 33/11kV S Stn",9.2999999999999999E-2,null,55,"",3,"Y"]
[920032,"Redcross Street 33/11kV S Stn",9.7000000000000003E-2,null,148,"",3,"Y"]
[920033,"Leicester 33/11kV S Stn",4.2999999999999997E-2,null,524,"",1,"Y"]
[920034,"Thurmaston 33/11kV S Stn",5.6000000000000001E-2,null,110,"",3,"Y"]
[920035,"Syston 33/11kV S Stn",6.5000000000000002E-2,null,70,"",3,"Y"]
[920036,"Highfields 33/11kV S Stn",9.8000000000000004E-2,null,318,"",3,"Y"]
[920037,"Salutation 33/6.6kV S Stn",5.8000000000000003E-2,null,211,"",3,"Y"]
[920038,"Stoneygate 33/6.6kV S Stn",6.9000000000000006E-2,null,111,"",3,"Y"]
[920039,"Wigston 132/11kV S Stn",6.0999999999999999E-2,null,393,"",1,"Y"]
[920040,"Leicester East 33/6.6kV S Stn",3.6999999999999998E-2,null,35,"",3,"Y"]
[920041,"South Croxton 33/11kV S Stn",0.183,null,207,"",3,"Y"]
[920042,"Thurnby 33/11kV S Stn",5.1999999999999998E-2,null,140,"",3,"Y"]
[920043,"Kibworth 33/11kV S Stn",9.5000000000000001E-2,null,319,"",3,"Y"]
[920044,"Hamilton 33/11kV S Stn",7.8E-2,null,204,"",3,"Y"]
[920045,"Field Street 33/11kV S Stn",4.9000000000000002E-2,null,124,"",3,"Y"]
[920046,"Farndon Road 33/11kV S Stn",5.6000000000000001E-2,null,134,"",3,"Y"]
[920047,"Market Harborough 33/11kV S Stn",0.17,null,262,"",3,"Y"]
[920048,"Desborough 33/11kV S Stn",6.4000000000000001E-2,null,100,"",3,"Y"]
[920049,"Corby Central 33/11kV S Stn",0.151,null,313,"",3,"Y"]
[920050,"Hazelwood 33/11kV S Stn",0.13,null,2117,"",3,"Y"]
[920051,"Oakley 33/11kV S Stn",0.05,null,97,"",3,"Y"]
[920052,"Earlstrees 33/11kV S Stn",6.3E-2,null,118,"",3,"Y"]
[920053,"Corby No2 33/11kV S Stn",7.3999999999999996E-2,null,1221,"",3,"Y"]
[920054,"Burton Latimer 33/11kV S Stn",6.2E-2,null,106,"",3,"Y"]
[920055,"Oundle 33/11kV S Stn",0.28000000000000003,null,409,"",3,"Y"]
[920056,"Rushden 33/11kV S Stn",0.13800000000000001,null,236,"",3,"Y"]
[920057,"Sharnbrook 33/11kV S Stn",0.06,null,103,"",3,"Y"]
[920058,"Cannon Street 33/11kV S Stn",4.8000000000000001E-2,null,123,"",3,"Y"]
[920059,"Thrapston 33/11kV S Stn",0.22,null,420,"",3,"Y"]
[920060,"Little Irchester 33/11kV S Stn",0.14000000000000001,null,420,"",3,"Y"]
[920061,"Harrold 33/11kV S Stn",0.156,null,232,"",3,"Y"]
[920062,"Raunds 33/11kV S Stn",0.12,null,190,"",3,"Y"]
[920063,"Corby North 33kV S Stn",6.5000000000000002E-2,null,1049,"",3,"Y"]
[920064,"ABR Foods 33kV S Stn",0.36,null,734,"",3,"Y"]
[920065,"Park Farm 33/11kV S Stn",9.6000000000000002E-2,null,188,"",3,"Y"]
[920066,"Astrazeneca 33/11kV S Stn",9.2999999999999999E-2,null,180,"",3,"Y"]
[921092,"Irthlingborough 33/11kV S Stn",6.5000000000000002E-2,null,131,"",3,"Y"]
[923189,"Burton Wold Wind Farm South 33kV S Stn",0.16600000000000001,null,187,"",3,"Y"]
[925737,"Burton Wold North 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[926096,"Wymeswold Airfield PV Farm 33kV S Stn",0.1,null,148,"",3,"Y"]
[926100,"Rockingham Data Centre 33kV S Stn",0.25,null,408,"",3,"Y"]
[926142,"The Ridge Solar Park 33kV S Stn",8.6999999999999994E-2,null,235,"",3,"Y"]
[926144,"Hockley Farm Road 33/11kV S Stn",0.1,null,331,"",3,"Y"]
[926184,"Airfield Farm Windfarm 33kV S Stn",0.17,null,391,"",3,"Y"]
[926186,"New Albion Wind Farm 33kV S Stn",0.182,null,275,"",3,"Y"]
[926202,"Pipewell Road PV 33kV S Stn",0.13,null,202,"",3,"Y"]
[926220,"Ragdale PV Solar Park 33kV S Stn",9.7000000000000003E-2,null,106,"",3,"Y"]
[926237,"Chelveston Solar Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[926242,"Glebe Farm Solar Park 33kV S Stn",0.08,null,52,"",3,"Y"]
[926263,"Kelmarsh Wind Farm 33kV S Stn",0.15,null,329,"",3,"Y"]
[926264,"Higham Ferrers Switching Station 33kV S Stn",0.27,null,331,"",3,"Y"]
[926300,"Wide Lane Wymeswold Solar Farm 33kV S Stn",7.2999999999999995E-2,null,164,"",3,"Y"]
[926308,"Sywell PV 33kV S Stn",0.193,null,122,"",3,"Y"]
[926349,"Irchester Road Switching Station 33kV S Stn",0.309,null,200,"",3,"Y"]
[926406,"Meadow Farm Solar 33kV S Stn",0.18,null,217,"",3,"Y"]
[926431,"Gypsum Solar Farm 33kV S Stn",0.08,null,112,"",3,"Y"]
[927000,"Chelveston Energy Park 33kV S Stn",0.12,null,211,"",3,"Y"]
[928000,"Irthlingborough 33kV S Stn",6.5000000000000002E-2,null,131,"",3,"Y"]
[930004,"Nuneaton 33kV S Stn",8.5000000000000006E-2,null,632,"",3,"Y"]
[930005,"Tamworth Town 33kV S Stn",3.4000000000000002E-2,null,217,"",3,"Y"]
[930006,"Rugby 33kV S Stn",4.2000000000000003E-2,null,361,"",3,"Y"]
[930007,"Warwick 33kV S Stn",4.1000000000000002E-2,null,274,"",3,"Y"]
[930008,"Whitley 33kV S Stn",7.0000000000000007E-2,null,574,"",3,"Y"]
[930009,"Coventry North 33kV S Stn",7.2999999999999995E-2,null,752,"",3,"Y"]
[930010,"Tamworth 33kV S Stn",4.7E-2,null,301,"",3,"Y"]
[930011,"Harbury 33kV S Stn",0.06,null,281,"",3,"Y"]
[930012,"Coventry South 33kV S Stn",5.7000000000000002E-2,null,553,"",3,"Y"]
[930013,"Coventry Central 33kV S Stn",9.2999999999999999E-2,null,331,"",3,"Y"]
[930014,"Coventry West 33kV S Stn",0.12,null,1161,"",3,"Y"]
[930015,"Tamworth Br 132/25kV S Stn",9.2999999999999999E-2,null,579,"",1,"Y"]
[930016,"Whitley 132/33kV S Stn",7.0000000000000007E-2,null,357,"",3,"Y"]
[930018,"Pailton 132/33kV S Stn",0.19,null,807,"",3,"Y"]
[930019,"Hinckley 33kV S Stn",0.159,null,872,"",3,"Y"]
[930020,"Coalville 33kV S Stn",0.109,null,382,"",3,"Y"]
[930021,"Rugby Portland Cement 33kV S Stn",4.2000000000000003E-2,null,361,"",3,"Y"]
[930025,"Coventry West 33/6.6kV S Stn",0.12,null,1161,"",3,"Y"]
[930027,"London Road 33/6.6kV S Stn",8.4000000000000005E-2,null,82,"",3,"Y"]
[930028,"Hawkesmill Lane 33/6.6kV S Stn",0.152,null,269,"",3,"Y"]
[930029,"Jaguar Browns Lane 33/11kv S Stn",9.2999999999999999E-2,null,160,"",3,"Y"]
[930030,"Torrington Avenue 33/11kV S Stn",8.4000000000000005E-2,null,219,"",3,"Y"]
[930031,"Cox Street 33/6.6 Kv S Stn",9.0999999999999998E-2,null,224,"",3,"Y"]
[930032,"Coventry South 33/11kV S Stn",5.7000000000000002E-2,null,553,"",3,"Y"]
[930033,"Courthouse Green 33/11kV S Stn",0.127,null,70,"",3,"Y"]
[930034,"University Of Warwick 33/11kV S Stn",0.04,null,270,"",3,"Y"]
[930035,"Courthouse Green 33/6.6kV S Stn",0.127,null,70,"",3,"Y"]
[930036,"Coventry Colliery 33/11kV S Stn",0.13300000000000001,null,262,"",3,"Y"]
[930037,"Holyhead Road 33/11kV S Stn",5.1999999999999998E-2,null,90,"",3,"Y"]
[930038,"Holbrook Lane 33/6.6kV S Stn",0.04,null,73,"",3,"Y"]
[930039,"Dunlop 33/6.6kV S Stn",9.8000000000000004E-2,null,218,"",3,"Y"]
[930040,"Sandy Lane 33/6.6kV S Stn",6.4000000000000001E-2,null,100,"",3,"Y"]
[930041,"Spon Street 33/6.6kV S Stn",0.1,null,200,"",3,"Y"]
[930042,"Dillotford Avenue 33/11kV S Stn",6.7000000000000004E-2,null,162,"",3,"Y"]
[930043,"Gulson Road 33/6.6kV S Stn",9.8000000000000004E-2,null,206,"",3,"Y"]
[930044,"Copsewood 33/11kV S Stn",0.104,null,253,"",3,"Y"]
[930045,"Whitley 33/11kV S Stn",7.0000000000000007E-2,null,357,"",3,"Y"]
[930046,"Coventry North 33/11kV S Stn",7.2999999999999995E-2,null,752,"",3,"Y"]
[930047,"Walsgrave 33/11kV S Stn",0.16,null,128,"",3,"Y"]
[930048,"Claverdon 33/11kV S Stn",0.129,null,187,"",3,"Y"]
[930049,"Ryton 33/11kV S Stn",5.0999999999999997E-2,null,82,"",3,"Y"]
[930050,"Kenilworth 33/11kV S Stn",0.08,null,142,"",3,"Y"]
[930051,"Banbury Road 33/11kV S Stn",0.123,null,224,"",3,"Y"]
[930053,"Campion Hills 33/11kV S Stn",0.11700000000000001,null,220,"",3,"Y"]
[930054,"Wise Street 33/11kV S Stn",0.05,null,73,"",3,"Y"]
[930055,"Lawford 33/11kV S Stn",5.1999999999999998E-2,null,134,"",3,"Y"]
[930056,"Lockheed 33/11kV S Stn",0.11700000000000001,null,22,"",3,"Y"]
[930057,"Gaydon 33/11kV S Stn",0.28999999999999998,null,286,"",3,"Y"]
[930058,"Harbury 33/11kV S Stn",0.06,null,281,"",3,"Y"]
[930059,"Princethorpe 33/11kV S Stn",0.2,null,342,"",3,"Y"]
[930060,"Southam 33/11kV S Stn",0.10199999999999999,null,168,"",3,"Y"]
[930061,"Ansty 33/11kV S Stn",9.5000000000000001E-2,null,235,"",3,"Y"]
[930062,"Lutterworth 33/11kV S Stn",7.1999999999999995E-2,null,122,"",3,"Y"]
[930063,"English Electric 33/11kV S Stn",6.4000000000000001E-2,null,170,"",3,"Y"]
[930064,"Rugby 132/11kV S Stn",4.2000000000000003E-2,null,361,"",1,"Y"]
[930065,"Union Street 33/11kV S Stn",5.2999999999999999E-2,null,80,"",3,"Y"]
[930066,"Brownsover 33/11kV S Stn",0.151,null,411,"",3,"Y"]
[930067,"Hillmorton 33/11kV S Stn",7.0000000000000007E-2,null,182,"",3,"Y"]
[930068,"Apollo 33/11kV S Stn",0.107,null,261,"",3,"Y"]
[930069,"Coton Road 33/6.6kV S Stn",0.109,null,222,"",3,"Y"]
[930070,"Tamworth Town 132/11kV S Stn",3.4000000000000002E-2,null,217,"",1,"Y"]
[930071,"Tamworth Grid 33/11kV S Stn",4.7E-2,null,301,"",3,"Y"]
[930072,"Polesworth 33/11kV S Stn",0.11,null,259,"",3,"Y"]
[930073,"Wood End 33/11kV S Stn",0.16500000000000001,null,383,"",3,"Y"]
[930074,"Whittleford 33/11kV S Stn",8.2000000000000003E-2,null,162,"",3,"Y"]
[930076,"Atherstone 33/11kV S Stn",5.1999999999999998E-2,null,90,"",3,"Y"]
[930077,"Nuneaton 33/11kV S Stn",8.5000000000000006E-2,null,632,"",3,"Y"]
[930078,"Arley 33/11kV S Stn",0.14000000000000001,null,217,"",3,"Y"]
[930079,"Newdigate 33/11kV S Stn",0.23,null,390,"",3,"Y"]
[930080,"Gipsy Lane 33/11kV S Stn",6.8000000000000005E-2,null,122,"",3,"Y"]
[930081,"Langdale Drive 33/11kV S Stn",0.112,null,202,"",3,"Y"]
[930082,"Coventry Waste Reduction 33kV S Stn",8.6999999999999994E-2,null,232,"",3,"Y"]
[930083,"Coventry Arena 33/11kV S Stn",0.23,null,202,"",3,"Y"]
[930084,"Interlink Park 33/11 Kv S Stn",0.17100000000000001,null,380,"",3,"Y"]
[930086,"Churchover 33/11kV S Stn",0.19,null,190,"",3,"Y"]
[930087,"Tournament Fields 33/11kV S Stn",0.95,null,441,"",3,"Y"]
[930088,"Middlefield 33/11kV S Stn",0.19700000000000001,null,388,"",3,"Y"]
[930089,"Sapcote 33/11kV S Stn",0.13300000000000001,null,254,"",3,"Y"]
[930090,"Gec Test Bed Whetstone 33kV S Stn",0.33,null,521,"",3,"Y"]
[930091,"Bardon 33/11kV S Stn",0.25700000000000001,null,540,"",3,"Y"]
[930092,"Coalville 33/11kV S Stn",0.109,null,382,"",3,"Y"]
[930093,"Desford 33/11kV S Stn",0.111,null,216,"",3,"Y"]
[930094,"Caterpillar Desford 33/11kV S Stn",0.109,null,124,"",3,"Y"]
[930095,"Alliance & Leicester 33/11kV S Stn",0.17,null,357,"",3,"Y"]
[930096,"Whetstone 33/11kV S Stn",7.1999999999999995E-2,null,142,"",3,"Y"]
[930097,"Nailstone 33/11kV S Stn",0.49399999999999999,null,935,"",3,"Y"]
[930098,"Mantle Lane 33/11kV S Stn",0.05,null,80,"",3,"Y"]
[930099,"Barwell 33/11kV S Stn",0.27100000000000002,null,473,"",3,"Y"]
[930100,"Osbaston 33/11kV S Stn",0.35,null,603,"",3,"Y"]
[930101,"Ashby De La Zouch 33/11kV S Stn",0.107,null,198,"",3,"Y"]
[930102,"Moira 33/11kV S Stn",0.14599999999999999,null,283,"",3,"Y"]
[930103,"Hinckley 132/11kV S Stn",0.159,null,872,"",1,"Y"]
[930104,"Worthington 33/11kV S Stn",0.253,null,314,"",3,"Y"]
[930105,"Bruntingthorpe 33/11kV S Stn",0.21,null,276,"",3,"Y"]
[930107,"Magna Park 33/11kV S Stn",0.127,null,245,"",3,"Y"]
[938836,"Rugby Gateway 33/11kV S Stn",0.25,null,265,"",3,"Y"]
[938992,"Low Spinney Wind Farm 33kV S Stn",0.1,null,140,"",3,"Y"]
[939003,"Swinford Windfarm 33kV S Stn",0.192,null,536,"",3,"Y"]
[939062,"Wood Lane 33/11kV S Stn",0.2,null,226,"",3,"Y"]
[939122,"Hall Farm Newbold Verdon 33kV S Stn",0.22500000000000001,null,338,"",3,"Y"]
[939140,"Atherstone Solar Farm 33kV S Stn",0.215,null,381,"",3,"Y"]
[939146,"Babelake St Packington 33kv S Stn",0.2,null,248,"",3,"Y"]
[939150,"Prestop Fm Burton Rd Ashby 33kv S Stn",0.129,null,500,"Y",3,"Y"]
[939156,"Elms Farm Southam Solar Farm 33kV S Stn",0.2,null,290,"",3,"Y"]
[939208,"Pebble Hall Generation 33kV S Stn",0.182,null,355,"",3,"Y"]
[939242,"Fields Farm Southam Solar Farm 33kV S Stn",0.1,null,138,"",3,"Y"]
[939263,"Lindridge Farm Solar Park 33kV S Stn",0.13700000000000001,null,278,"",3,"Y"]
[939300,"Victoria Road PV Ellistown 33kV S Stn",7.2999999999999995E-2,null,238,"",3,"Y"]
[939301,"Fosse Way Radford Semele Solar Farm 33kV S Stn",0.08,null,100,"",3,"Y"]
[939305,"Jaguar Land Rover 33/11kV S Stn",0.28999999999999998,null,286,"",3,"Y"]
[939417,"Baddesley Energy Park 33kV S Stn",0.30599999999999999,null,727,"",3,"Y"]
[939424,"Wellesbourne 33/11kV S Stn",0.2,null,421,"",3,"Y"]
[939476,"Hill Farm Battery Generation 33kV S Stn",0.38700000000000001,null,617,"",3,"Y"]
[939482,"JLR Whitley 33/11kV S Stn",0.7,null,340,"",3,"Y"]
[939800,"Birch Coppice 33/11kv S Stn",0.13300000000000001,null,189,"",3,"Y"]
[940005,"Stony Stratford 33kV S Stn",9.1999999999999998E-2,null,1074,"",3,"Y"]
[940006,"Bradwell Abbey 33kV S Stn",9.4E-2,null,486,"",3,"Y"]
[940008,"Daventry 33kV S Stn",4.4999999999999998E-2,null,147,"",3,"Y"]
[940009,"Northampton 33kV S Stn",5.2999999999999999E-2,null,570,"",3,"Y"]
[940010,"Northampton East 33kV S Stn",0.09,null,637,"",3,"Y"]
[940011,"Wellingborough 33kV S Stn",4.4999999999999998E-2,null,217,"",3,"Y"]
[940012,"Northampton West 33kV S Stn",5.2999999999999999E-2,null,375,"",3,"Y"]
[940013,"Bletchley 33kV S Stn",2.7E-2,null,166,"",3,"Y"]
[940015,"Wolverton 132/25kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[940017,"Shanks Generation 33kV S Stn",0.06,null,68,"",3,"Y"]
[940020,"Bletchley Landfill 33kV S Stn",0.192,null,416,"",3,"Y"]
[940021,"Pineham 33/11kV S Stn",0.22800000000000001,null,392,"",3,"Y"]
[940022,"Hanslope Park 33/11kV S Stn",0.13100000000000001,null,192,"",3,"Y"]
[940023,"Fen Farm 33/11kV S Stn",9.0999999999999998E-2,null,194,"",3,"Y"]
[940024,"Petsoe Manor Wind Farm 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[940025,"Secklow Gate 33/11kV S Stn",6.3E-2,null,137,"",3,"Y"]
[940026,"Thenford 33/11kV S Stn",0.59,null,965,"",3,"Y"]
[940027,"Woodford Halse 33/11kV S Stn",8.5999999999999993E-2,null,157,"",3,"Y"]
[940028,"Brackley Town 33/11kV S Stn",4.1000000000000002E-2,null,80,"",3,"Y"]
[940029,"Buckingham 33/11kV S Stn",6.7000000000000004E-2,null,99,"",3,"Y"]
[940030,"Calvert 33/11kV S Stn",0.111,null,173,"",3,"Y"]
[940031,"Towcester 33/11kV S Stn",6.9000000000000006E-2,null,98,"",3,"Y"]
[940032,"Silverstone 33/11kV S Stn",0.19400000000000001,null,198,"",3,"Y"]
[940033,"Wicken 33/11kV S Stn",0.45,null,878,"",3,"Y"]
[940034,"Kiln Farm 33/11kV S Stn",3.5000000000000003E-2,null,93,"",3,"Y"]
[940035,"Winslow 33/11kV S Stn",8.3000000000000004E-2,null,160,"",3,"Y"]
[940036,"Wolverton 33/11kV S Stn",6.8000000000000005E-2,null,351,"",3,"Y"]
[940037,"Marlborough Street 33/11kV S Stn",8.1000000000000003E-2,null,230,"",3,"Y"]
[940038,"Portway 33/11kV S Stn",3.3000000000000002E-2,null,65,"",3,"Y"]
[940039,"Childs Way 33/11kV S Stn",0.05,null,125,"",3,"Y"]
[940040,"Newton Road 33/11kV S Stn",0.109,null,167,"",3,"Y"]
[940041,"Newport Pagnell 33/11kV S Stn",0.13100000000000001,null,271,"",3,"Y"]
[940042,"Bletchley 33/11kV S Stn",2.7E-2,null,166,"",3,"Y"]
[940043,"Fox Milne 33/11kV S Stn",4.1000000000000002E-2,null,47,"",3,"Y"]
[940044,"Victoria Road 33/11kV S Stn",8.3000000000000004E-2,null,125,"",3,"Y"]
[940045,"Olney 33/11kV S Stn",0.09,null,137,"",3,"Y"]
[940046,"Wavendon Gate 33/11kV S Stn",0.04,null,78,"",3,"Y"]
[940047,"Braunston Road 33/11kV S Stn",9.8000000000000004E-2,null,245,"",3,"Y"]
[940048,"Welton 33/11kV S Stn",0.13100000000000001,null,262,"",3,"Y"]
[940049,"Daventry 33/11kV S Stn",4.4999999999999998E-2,null,147,"",3,"Y"]
[940050,"Weedon 33/11kV S Stn",0.10100000000000001,null,164,"",3,"Y"]
[940051,"West Haddon 33/11kV S Stn",0.33200000000000002,null,637,"",3,"Y"]
[940052,"Bugbrooke 33/11kV S Stn",0.104,null,151,"",3,"Y"]
[940053,"Earls Barton 33/11kV S Stn",0.15,null,267,"",3,"Y"]
[940054,"Northampton West 33/11kV S Stn",5.2999999999999999E-2,null,43,"",3,"Y"]
[940055,"Ellesmere Avenue 33/11kV S Stn",0.121,null,227,"",3,"Y"]
[940056,"Chapel Brampton 33/11kV S Stn",8.3000000000000004E-2,null,128,"",3,"Y"]
[940057,"Abington 33/11kV S Stn",0.14000000000000001,null,334,"",3,"Y"]
[940058,"Banbury Lane 33/11kV S Stn",0.56999999999999995,null,96,"",3,"Y"]
[940059,"Campbell Street 33/11kV S Stn",0.152,null,391,"",3,"Y"]
[940060,"Kingsthorpe 33/11kV S Stn",0.11899999999999999,null,223,"",3,"Y"]
[940061,"Northampton 33/11kV S Stn",5.2999999999999999E-2,null,570,"",3,"Y"]
[940062,"Wootton 33/11kV S Stn",0.14000000000000001,null,140,"",3,"Y"]
[940063,"Roade 33/11kV S Stn",0.111,null,179,"",3,"Y"]
[940064,"Wellingborough Road 33/11kV S Stn",0.05,null,970,"",3,"Y"]
[940065,"Boothville 33/11kV S Stn",0.06,null,138,"",3,"Y"]
[940066,"Denton 33/11kV S Stn",0.28000000000000003,null,425,"",3,"Y"]
[940067,"Campbell Park 33/11kV S Stn",0.05,null,75,"",3,"Y"]
[940068,"Crick 33/11kV S Stn",8.2000000000000003E-2,null,158,"",3,"Y"]
[940069,"Shenley Wood 33/11kV S Stn",6.4000000000000001E-2,null,124,"",3,"Y"]
[940070,"Kingston 33/11kV S Stn",0.06,null,136,"",3,"Y"]
[940071,"Eldergate 33/11kV S Stn",0.05,null,75,"",3,"Y"]
[940072,"Brackmills 33/11kV S Stn",0.06,null,160,"",3,"Y"]
[945510,"Beachampton Solar Farm 33kV S Stn",7.0000000000000007E-2,null,105,"",3,"Y"]
[945674,"Roade Wind Farm 33kV S Stn",0.12,null,194,"",3,"Y"]
[945675,"Maxwell House Data Centre 33/11kV S Stn",0.23,null,208,"",3,"Y"]
[945726,"Turweston Airfield Solar Farm 33kV S Stn",0.1,null,126,"",3,"Y"]
[945977,"Watford Lodge Windfarm 33kV S Stn",0.13,null,250,"",3,"Y"]
[945978,"Winwick Windfarm 33kV S Stn",0.13,null,145,"",3,"Y"]
[946045,"Northampton East 33/11kV S Stn",0.09,null,637,"",3,"Y"]
[946060,"Whittlebury Road PV 33kV S Stn",6.3E-2,null,56,"",3,"Y"]
[946091,"Yelvertoft Windfarm 33kV S Stn",0.2,null,135,"",3,"Y"]
[946100,"Brackley 33kV S Stn",0.1,null,637,"",3,"Y"]
[946139,"Hartwell Road 33kV S Stn",6.9000000000000006E-2,null,142,"",3,"Y"]
[946140,"Eakley Lanes North PV 33kV S Stn",0.152,null,156,"",3,"Y"]
[946141,"Eakley Lanes South PV 33kV S Stn",7.0000000000000007E-2,null,72,"",3,"Y"]
[946154,"Gawcott Fields Solar Park 33kV S Stn",7.4999999999999997E-2,null,69,"",3,"Y"]
[946165,"Lilbourne Wind Farm 33kV S Stn",0.18,null,257,"",3,"Y"]
[946174,"Mount Mill Solar Park 33kV S Stn",0.09,null,203,"",3,"Y"]
[946176,"Homestead Solar Park 33kV S Stn",0.27100000000000002,null,306,"",3,"Y"]
[946180,"Handley Park Solar Park 33kv S Stn",0.11,null,109,"",3,"Y"]
[946198,"Littlewood Farm Solar 33kV S Stn",0.28000000000000003,null,101,"",3,"Y"]
[946213,"Emberton Pv 33kv S Stn",9.6000000000000002E-2,null,108,"",3,"Y"]
[946240,"Greatmoor Efw Calvert 33kv S Stn",0.05,null,154,"",3,"Y"]
[946268,"Tattenhoe 33/11kV S Stn",0.13,null,420,"",3,"Y"]
[946270,"Manor Farm PV Horton 33kV S Stn",0.11,null,165,"",3,"Y"]
[946271,"Thornborough Grounds Pv 33kv S Stn",0.20699999999999999,null,261,"",3,"Y"]
[946276,"Brafield On The Green PV 33kv S Stn",0.16300000000000001,null,263,"",3,"Y"]
[946329,"Olney Hyde Farm Solar 33kV S Stn",8.8999999999999996E-2,null,137,"",3,"Y"]
[946411,"Lyon Road Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[947000,"Brackley 33/11kV S Stn",0.1,null,637,"",3,"Y"]

{"sheet":"Source-EM-Name","index":19,"n_rows":739,"n_cols":9,"rows_kept":739,"cut":false,"hidden":true,"merged":[]}
[null,1,2,3,4,5,6,7,8]
["SUBSTATION_NAME_EM","SUBSTATION_NAME_TRUNC_EM","SUBSTATION_NUMBER","ZE","Assumed ZE","UE","Assumed UE","t","Assumed t"]
["Abington 33/11kV S Stn","Abington33/11kVSStn",940057,0.14000000000000001,null,334,"",3,"Y"]
["ABR Foods 33kV S Stn","ABRFoods33kVSStn",920064,0.36,null,734,"",3,"Y"]
["Acreage Lane 33/11kV S Stn","AcreageLane33/11kVSStn",890035,0.59599999999999997,null,1173,"",3,"Y"]
["Airfield Farm Windfarm 33kV S Stn","AirfieldFarmWindfarm33kVSStn",926184,0.17,null,391,"",3,"Y"]
["Alford 33/11kV S Stn","Alford33/11kVSStn",900014,0.26500000000000001,null,441,"",3,"Y"]
["Alfreton 132/33kV S Stn","Alfreton132/33kVSStn",680037,0.193,null,752,"",3,"Y"]
["Alfreton 33kV S Stn","Alfreton33kVSStn",890014,0.193,null,752,"",3,"Y"]
["Allenton 33/11kV S Stn","Allenton33/11kVSStn",870043,8.1000000000000003E-2,null,229,"",3,"Y"]
["Alliance & Leicester 33/11kV S Stn","Alliance&Leicester33/11kVSStn",930095,0.17,null,357,"",3,"Y"]
["Ambergate 33/11kV S Stn","Ambergate33/11kVSStn",890077,6.5000000000000002E-2,null,75,"",3,"Y"]
["Anderson Lane 33/11kV S Stn","AndersonLane33/11kVSStn",900032,0.121,null,369,"",3,"Y"]
["Annesley 132/33kV S Stn","Annesley132/33kVSStn",680011,8.2000000000000003E-2,null,370,"",3,"Y"]
["Annesley 33/11kV S Stn","Annesley33/11kVSStn",890033,8.2000000000000003E-2,null,370,"",3,"Y"]
["Annesley 33kV S Stn","Annesley33kVSStn",890007,8.2000000000000003E-2,null,370,"",3,"Y"]
["Ansty 33/11kV S Stn","Ansty33/11kVSStn",930061,9.5000000000000001E-2,null,235,"",3,"Y"]
["Apollo 33/11kV S Stn","Apollo33/11kVSStn",930068,0.107,null,261,"",3,"Y"]
["Arkwright Solar 33kV S Stn","ArkwrightSolar33kVSStn",898436,0.49,null,821,"",3,"Y"]
["Arley 33/11kV S Stn","Arley33/11kVSStn",930078,0.14000000000000001,null,217,"",3,"Y"]
["Arnold 33/11kV S Stn","Arnold33/11kVSStn",880027,0.16700000000000001,null,326,"",3,"Y"]
["Asfordby 132/11kV S Stn","Asfordby132/11kVSStn",910047,9.5000000000000001E-2,null,185,"",1,"Y"]
["Asfordby 132kV S Stn","Asfordby132kVSStn",690034,9.5000000000000001E-2,null,185,"",1,"Y"]
["Ashbourne 33/11kV S Stn","Ashbourne33/11kVSStn",870030,0.125,null,230,"",3,"Y"]
["Ashby De La Zouch 33/11kV S Stn","AshbyDeLaZouch33/11kVSStn",930101,0.107,null,198,"",3,"Y"]
["Asher Lane STOR 33kV S Stn","AsherLaneSTOR33kVSStn",898663,0.7,"Y",500,"Y",3,"Y"]
["Aston House Solar Farm 33kV S Stn","AstonHouseSolarFarm33kVSStn",874987,0.23499999999999999,null,291,"",3,"Y"]
["Astrazeneca 33/11kV S Stn","Astrazeneca33/11kVSStn",920066,9.2999999999999999E-2,null,180,"",3,"Y"]
["Atherstone 33/11kV S Stn","Atherstone33/11kVSStn",930076,5.1999999999999998E-2,null,90,"",3,"Y"]
["Atherstone Solar Farm 33kV S Stn","AtherstoneSolarFarm33kVSStn",939140,0.215,null,381,"",3,"Y"]
["Averill Solar Farm 33kV S Stn","AverillSolarFarm33kVSStn",898444,0.13,null,150,"",3,"Y"]
["Babelake St Packington 33kv S Stn","BabelakeStPackington33kvSStn",939146,0.2,null,248,"",3,"Y"]
["Baddesley Energy Park 33kV S Stn","BaddesleyEnergyPark33kVSStn",939417,0.30599999999999999,null,727,"",3,"Y"]
["Bakewell 33/11kV S Stn","Bakewell33/11kVSStn",890065,0.3,null,268,"",3,"Y"]
["Bambers Farm Wind Generation 33kV S Stn","BambersFarmWindGeneration33kVSStn",900008,0.2,null,272,"",3,"Y"]
["Banbury Lane 33/11kV S Stn","BanburyLane33/11kVSStn",940058,0.56999999999999995,null,96,"",3,"Y"]
["Banbury Road 33/11kV S Stn","BanburyRoad33/11kVSStn",930051,0.123,null,224,"",3,"Y"]
["Bardon 33/11kV S Stn","Bardon33/11kVSStn",930091,0.25700000000000001,null,540,"",3,"Y"]
["Barton Under Needwood 33/11kV S Stn","BartonUnderNeedwood33/11kVSStn",870013,0.16500000000000001,null,185,"",3,"Y"]
["Barwell 33/11kV S Stn","Barwell33/11kVSStn",930099,0.27100000000000002,null,473,"",3,"Y"]
["Beachampton Solar Farm 33kV S Stn","BeachamptonSolarFarm33kVSStn",945510,7.0000000000000007E-2,null,105,"",3,"Y"]
["Beaumont Leys 33/11kV S Stn","BeaumontLeys33/11kVSStn",920026,0.13,null,275,"",3,"Y"]
["Beeston 33/11kV S Stn","Beeston33/11kVSStn",880012,0.1,null,216,"",3,"Y"]
["Beevor Street 33/11kV S Stn","BeevorStreet33/11kVSStn",900009,0.15,null,300,"",3,"Y"]
["Belper 33/11kV S Stn","Belper33/11kVSStn",890076,8.3000000000000004E-2,null,120,"",3,"Y"]
["Bentinck Generating Station 33kV S Stn","BentinckGeneratingStation33kVSStn",898163,1.3,null,2275,"",3,"Y"]
["Berkswell 275/132kV S Stn","Berkswell275/132kVSStn",690001,0.2,"Y",350,"",1,"Y"]
["Bevercotes 33/11kV S Stn","Bevercotes33/11kVSStn",890055,0.17100000000000001,null,171,"",3,"Y"]
["Bicker Fen 400/132kV S Stn","BickerFen400/132kVSStn",690003,0.04,null,710,"",1,"Y"]
["Bicker Fen Wind Generation 33kV S Stn","BickerFenWindGeneration33kVSStn",910019,0.7,"Y",500,"Y",3,"Y"]
["Bilborough 33/11kV S Stn","Bilborough33/11kVSStn",880013,0.13100000000000001,null,277,"",3,"Y"]
["Billingborough 33/11kV S Stn","Billingborough33/11kVSStn",910035,0.32300000000000001,null,633,"",3,"Y"]
["Bilsthorpe 33/11kV S Stn","Bilsthorpe33/11kVSStn",890054,0.2,null,396,"",3,"Y"]
["Bilsthorpe P V Generation 33kV S Stn","BilsthorpePVGeneration33kVSStn",898555,0.24,null,496,"",3,"Y"]
["Bilsthorpe Solar 33kV S Stn","BilsthorpeSolar33kVSStn",898326,0.27,null,208,"",3,"Y"]
["Bingham 33/11kV S Stn","Bingham33/11kVSStn",880039,6.0999999999999999E-2,null,73,"",3,"Y"]
["Birch Coppice 33/11kv S Stn","BirchCoppice33/11kvSStn",939800,0.13300000000000001,null,189,"",3,"Y"]
["Birstall 33/11kV S Stn","Birstall33/11kVSStn",920029,7.6999999999999999E-2,null,182,"",3,"Y"]
["Biwaters 33/11kV S Stn","Biwaters33/11kVSStn",890095,0.26200000000000001,null,349,"",3,"Y"]
["Blackwell 33/11kV S Stn","Blackwell33/11kVSStn",890026,0.114,null,201,"",3,"Y"]
["Bletchley 132/33kV S Stn","Bletchley132/33kVSStn",690046,2.7E-2,null,166,"",3,"Y"]
["Bletchley 33/11kV S Stn","Bletchley33/11kVSStn",940042,2.7E-2,null,166,"",3,"Y"]
["Bletchley 33kV S Stn","Bletchley33kVSStn",940013,2.7E-2,null,166,"",3,"Y"]
["Bletchley Landfill 33kV S Stn","BletchleyLandfill33kVSStn",940020,0.192,null,416,"",3,"Y"]
["Blidworth 33/11kV S Stn","Blidworth33/11kVSStn",890041,0.64400000000000002,null,1173,"",3,"Y"]
["Bolsover 33/11kV S Stn","Bolsover33/11kVSStn",890093,0.15,null,225,"",3,"Y"]
["Bolsover Moor Quarry PV Solar Farm 33kV S Stn","BolsoverMoorQuarryPVSolarFarm33kVSStn",898563,0.35,null,487,"",3,"Y"]
["Bombardier 33kV S Stn","Bombardier33kVSStn",870016,5.3999999999999999E-2,null,127,"",3,"Y"]
["Boothville 33/11kV S Stn","Boothville33/11kVSStn",940065,0.06,null,138,"",3,"Y"]
["Boots 33/11kV S Stn","Boots33/11kVSStn",880016,0.153,null,384,"",3,"Y"]
["Boston 132/33kV S Stn","Boston132/33kVSStn",690043,3.9E-2,null,257,"",3,"Y"]
["Boston 33kV S Stn","Boston33kVSStn",900004,3.9E-2,null,257,"",3,"Y"]
["Boston Biomass Generation 33kV S Stn","BostonBiomassGeneration33kVSStn",907058,9.6000000000000002E-2,null,261,"",3,"Y"]
["Bottesford 33/11kV S Stn","Bottesford33/11kVSStn",910038,0.217,null,260,"",3,"Y"]
["Bourne 132/33kV S Stn","Bourne132/33kVSStn",690044,0.09,null,844,"",3,"Y"]
["Bourne 33/11kV S Stn","Bourne33/11kVSStn",910032,0.09,null,844,"",3,"Y"]
["Bourne 33kV S Stn","Bourne33kVSStn",910005,0.09,null,844,"",3,"Y"]
["Bourne West 132/25kV S Stn","BourneWest132/25kVSStn",690039,0.17399999999999999,null,1366,"",1,"Y"]
["Bowbridge STOR Generation 33kV S Stn","BowbridgeSTORGeneration33kVSStn",690070,0.7,"Y",500,"Y",3,"Y"]
["Brackley 132/33kV S Stn","Brackley132/33kVSStn",690047,0.1,null,637,"",3,"Y"]
["Brackley 33/11kV S Stn","Brackley33/11kVSStn",947000,0.1,null,637,"",3,"Y"]
["Brackley 33kV S Stn","Brackley33kVSStn",946100,0.1,null,637,"",3,"Y"]
["Brackley Town 33/11kV S Stn","BrackleyTown33/11kVSStn",940028,4.1000000000000002E-2,null,80,"",3,"Y"]
["Brackmills 33/11kV S Stn","Brackmills33/11kVSStn",940072,0.06,null,160,"",3,"Y"]
["Bradwell Abbey 132/33kV S Stn","BradwellAbbey132/33kVSStn",690006,9.4E-2,null,486,"",3,"Y"]
["Bradwell Abbey 33kV S Stn","BradwellAbbey33kVSStn",940006,9.4E-2,null,486,"",3,"Y"]
["Brafield On The Green PV 33kv S Stn","BrafieldOnTheGreenPV33kvSStn",946276,0.16300000000000001,null,263,"",3,"Y"]
["Branston South Solar Farm 33kV S Stn","BranstonSouthSolarFarm33kVSStn",907556,0.22,null,418,"",3,"Y"]
["Braunstone 33/11kV S Stn","Braunstone33/11kVSStn",920031,9.2999999999999999E-2,null,55,"",3,"Y"]
["Braunston Road 33/11kV S Stn","BraunstonRoad33/11kVSStn",940047,9.8000000000000004E-2,null,245,"",3,"Y"]
["Breach Farm 33kv S Stn","BreachFarm33kvSStn",875157,0.747,null,1141,"",3,"Y"]
["Bretby 33/11kV S Stn","Bretby33/11kVSStn",870034,8.8999999999999996E-2,null,130,"",3,"Y"]
["British Gypsum 33/11kV S Stn","BritishGypsum33/11kVSStn",920018,0.113,null,219,"",3,"Y"]
["Brownsover 33/11kV S Stn","Brownsover33/11kVSStn",930066,0.151,null,411,"",3,"Y"]
["Bruntingthorpe 33/11kV S Stn","Bruntingthorpe33/11kVSStn",930105,0.21,null,276,"",3,"Y"]
["Brush 33/11kV S Stn","Brush33/11kVSStn",920021,0.09,null,176,"",3,"Y"]
["Buckingham 33/11kV S Stn","Buckingham33/11kVSStn",940029,6.7000000000000004E-2,null,99,"",3,"Y"]
["Budby 33/11kV S Stn","Budby33/11kVSStn",890045,0.51200000000000001,null,737,"",3,"Y"]
["Bugbrooke 33/11kV S Stn","Bugbrooke33/11kVSStn",940052,0.104,null,151,"",3,"Y"]
["Bulwell 33/11kV S Stn","Bulwell33/11kVSStn",880019,7.5999999999999998E-2,null,176,"",3,"Y"]
["Burnaston 132/11kV S Stn","Burnaston132/11kVSStn",680034,9.0999999999999998E-2,null,1237,"",1,"Y"]
["Burton 132/11kV S Stn","Burton132/11kVSStn",874558,1.9E-2,null,141,"",1,"Y"]
["Burton 132/33/11kV S Stn","Burton132/33/11kVSStn",680033,1.9E-2,null,141,"",3,"Y"]
["Burton 33kV S Stn","Burton33kVSStn",875000,1.9E-2,null,141,"",3,"Y"]
["Burton Latimer 33/11kV S Stn","BurtonLatimer33/11kVSStn",920054,6.2E-2,null,106,"",3,"Y"]
["Burton Pedwardine Solar Park 1 33kV S Stn","BurtonPedwardineSolarPark133kVSStn",905663,0.17799999999999999,null,267,"",3,"Y"]
["Burton South 132/33kV S Stn","BurtonSouth132/33kVSStn",680009,0.1,null,2006,"",3,"Y"]
["Burton South 33kV S Stn","BurtonSouth33kVSStn",870004,0.1,null,843,"",3,"Y"]
["Burton Wold North 33kV S Stn","BurtonWoldNorth33kVSStn",925737,0.7,"Y",500,"Y",3,"Y"]
["Burton Wold Wind Farm Generation 33kV S Stn","BurtonWoldWindFarmGeneration33kVSStn",920012,0.13600000000000001,null,256,"",3,"Y"]
["Burton Wold Wind Farm South 33kV S Stn","BurtonWoldWindFarmSouth33kVSStn",923189,0.16600000000000001,null,187,"",3,"Y"]
["Buxton 33kV S Stn","Buxton33kVSStn",680028,0.7,"Y",500,"Y",3,"Y"]
["Calvert 33/11kV S Stn","Calvert33/11kVSStn",940030,0.111,null,173,"",3,"Y"]
["Calverton 33/11kV S Stn","Calverton33/11kVSStn",880031,0.27700000000000002,null,300,"",3,"Y"]
["Campbell Park 33/11kV S Stn","CampbellPark33/11kVSStn",940067,0.05,null,75,"",3,"Y"]
["Campbell Street 33/11kV S Stn","CampbellStreet33/11kVSStn",940059,0.152,null,391,"",3,"Y"]
["Campion Hills 33/11kV S Stn","CampionHills33/11kVSStn",930053,0.11700000000000001,null,220,"",3,"Y"]
["Cannon Street 33/11kV S Stn","CannonStreet33/11kVSStn",920058,4.8000000000000001E-2,null,123,"",3,"Y"]
["Canopus Solar Farm 33kV S Stn","CanopusSolarFarm33kVSStn",906775,5.8000000000000003E-2,null,119,"",3,"Y"]
["Carlton On Trent 33/11kV S Stn","CarltonOnTrent33/11kVSStn",890061,0.67500000000000004,null,989,"",3,"Y"]
["Castle Donington 33/11kV S Stn","CastleDonington33/11kVSStn",870047,0.13600000000000001,null,171,"",3,"Y"]
["Castle Road 33/11kV S Stn","CastleRoad33/11kVSStn",880025,7.2999999999999995E-2,null,194,"",3,"Y"]
["Caterpillar Desford 33/11kV S Stn","CaterpillarDesford33/11kVSStn",930094,0.109,null,124,"",3,"Y"]
["Caythorpe 33/11kV S Stn","Caythorpe33/11kVSStn",880037,0.30499999999999999,null,573,"",3,"Y"]
["Chaddesden 33/11kV S Stn","Chaddesden33/11kVSStn",870044,8.7999999999999995E-2,null,205,"",3,"Y"]
["Chapel Brampton 33/11kV S Stn","ChapelBrampton33/11kVSStn",940056,8.3000000000000004E-2,null,128,"",3,"Y"]
["Chapel St Leonards 33/11kV S Stn","ChapelStLeonards33/11kVSStn",900015,0.219,null,438,"",3,"Y"]
["Checkerhouse 132/33kV S Stn","Checkerhouse132/33kVSStn",680013,0.21,null,685,"",3,"Y"]
["Checkerhouse 33/11kV S Stn","Checkerhouse33/11kVSStn",890010,0.21,null,685,"",3,"Y"]
["Checkerhouse 33kV S Stn","Checkerhouse33kVSStn",890050,0.21,null,685,"",3,"Y"]
["Chelveston Energy Park 33kV S Stn","ChelvestonEnergyPark33kVSStn",927000,0.12,null,211,"",3,"Y"]
["Chelveston Solar Park 33kV S Stn","ChelvestonSolarPark33kVSStn",926237,0.7,"Y",500,"Y",3,"Y"]
["Chesterfield 275/132/33kV S Stn","Chesterfield275/132/33kVSStn",680007,5.6000000000000001E-2,null,1070,"",3,"Y"]
["Chesterfield 33kV S Stn","Chesterfield33kVSStn",680032,5.6000000000000001E-2,null,1070,"",3,"Y"]
["Childs Way 33/11kV S Stn","ChildsWay33/11kVSStn",940039,0.05,null,125,"",3,"Y"]
["Chilwell 33/11kV S Stn","Chilwell33/11kVSStn",880010,0.106,null,190,"",3,"Y"]
["Churchover 33/11kV S Stn","Churchover33/11kVSStn",930086,0.19,null,190,"",3,"Y"]
["Church Street 33/11kV S Stn","ChurchStreet33/11kVSStn",870027,1.4999999999999999E-2,null,206,"",3,"Y"]
["Cinderhill 33/11kV S Stn","Cinderhill33/11kVSStn",880015,0.09,null,136,"",3,"Y"]
["Claverdon 33/11kV S Stn","Claverdon33/11kVSStn",930048,0.129,null,187,"",3,"Y"]
["Clay Lake Generation 33kV S Stn","ClayLakeGeneration33kVSStn",690069,0.7,"Y",500,"Y",3,"Y"]
["Clifton 33/11kV S Stn","Clifton33/11kVSStn",880024,9.7000000000000003E-2,null,363,"",3,"Y"]
["Clipstone 132/33kV S Stn","Clipstone132/33kVSStn",680012,0.18,null,477,"",3,"Y"]
["Clipstone 33/11kV S Stn","Clipstone33/11kVSStn",890040,0.18,null,477,"",3,"Y"]
["Clipstone 33kV S Stn","Clipstone33kVSStn",890006,0.18,null,477,"",3,"Y"]
["Clowne 33/11kV S Stn","Clowne33/11kVSStn",890085,0.5,null,884,"",3,"Y"]
["Coalville 132/33kV S Stn","Coalville132/33kVSStn",690024,0.109,null,382,"",3,"Y"]
["Coalville 33/11kV S Stn","Coalville33/11kVSStn",930092,0.109,null,382,"",3,"Y"]
["Coalville 33kV S Stn","Coalville33kVSStn",930020,0.109,null,382,"",3,"Y"]
["Cobb Farm Solar Generation 33kV S Stn","CobbFarmSolarGeneration33kVSStn",898371,0.19600000000000001,null,175,"",3,"Y"]
["Colwick 33/11kV S Stn","Colwick33/11kVSStn",880035,2.1999999999999999E-2,null,175,"",3,"Y"]
["Copley Farm Solar Generation 33kV S Stn","CopleyFarmSolarGeneration33kVSStn",917592,0.15,null,290,"",3,"Y"]
["Copsewood 33/11kV S Stn","Copsewood33/11kVSStn",930044,0.104,null,253,"",3,"Y"]
["Corby 132/33kV S Stn","Corby132/33kVSStn",690008,0.2,"Y",1000,"Y",3,"Y"]
["Corby Central 33/11kV S Stn","CorbyCentral33/11kVSStn",920049,0.151,null,313,"",3,"Y"]
["Corby No2 33/11kV S Stn","CorbyNo233/11kVSStn",920053,7.3999999999999996E-2,null,1221,"",3,"Y"]
["Corby No2 33kV S Stn","CorbyNo233kVSStn",920007,7.3999999999999996E-2,null,1221,"",3,"Y"]
["Corby North 132kV S Stn","CorbyNorth132kVSStn",690048,6.5000000000000002E-2,null,1049,"",1,"Y"]
["Corby North 33kV S Stn","CorbyNorth33kVSStn",920063,6.5000000000000002E-2,null,1049,"",3,"Y"]
["Cotgrave 33/11kV S Stn","Cotgrave33/11kVSStn",880036,0.126,null,177,"",3,"Y"]
["Coton Road 33/6.6kV S Stn","CotonRoad33/6.6kVSStn",930069,0.109,null,222,"",3,"Y"]
["Courthouse Green 33/11kV S Stn","CourthouseGreen33/11kVSStn",930033,0.127,null,70,"",3,"Y"]
["Courthouse Green 33/6.6kV S Stn","CourthouseGreen33/6.6kVSStn",930035,0.127,null,70,"",3,"Y"]
["Coventry 275/132kV S Stn","Coventry275/132kVSStn",690002,0.2,"Y",2800,"Y",1,"Y"]
["Coventry Arena 33/11kV S Stn","CoventryArena33/11kVSStn",930083,0.23,null,202,"",3,"Y"]
["Coventry Central 132/33kV S Stn","CoventryCentral132/33kVSStn",690013,9.2999999999999999E-2,null,331,"",3,"Y"]
["Coventry Central 33kV S Stn","CoventryCentral33kVSStn",930013,9.2999999999999999E-2,null,331,"",3,"Y"]
["Coventry Colliery 33/11kV S Stn","CoventryColliery33/11kVSStn",930036,0.13300000000000001,null,262,"",3,"Y"]
["Coventry North 132/33kV S Stn","CoventryNorth132/33kVSStn",690012,7.2999999999999995E-2,null,752,"",3,"Y"]
["Coventry North 33/11kV S Stn","CoventryNorth33/11kVSStn",930046,7.2999999999999995E-2,null,752,"",3,"Y"]
["Coventry North 33kV S Stn","CoventryNorth33kVSStn",930009,7.2999999999999995E-2,null,752,"",3,"Y"]
["Coventry South 132/33kV S Stn","CoventrySouth132/33kVSStn",690014,5.7000000000000002E-2,null,553,"",3,"Y"]
["Coventry South 33/11kV S Stn","CoventrySouth33/11kVSStn",930032,5.7000000000000002E-2,null,553,"",3,"Y"]
["Coventry South 33kV S Stn","CoventrySouth33kVSStn",930012,5.7000000000000002E-2,null,553,"",3,"Y"]
["Coventry Waste Reduction 33kV S Stn","CoventryWasteReduction33kVSStn",930082,8.6999999999999994E-2,null,232,"",3,"Y"]
["Coventry West 132/33kV S Stn","CoventryWest132/33kVSStn",690015,0.12,null,1161,"",3,"Y"]
["Coventry West 33/6.6kV S Stn","CoventryWest33/6.6kVSStn",930025,0.12,null,1161,"",3,"Y"]
["Coventry West 33kV S Stn","CoventryWest33kVSStn",930014,0.12,null,1161,"",3,"Y"]
["Cox Street 33/6.6 Kv S Stn","CoxStreet33/6.6KvSStn",930031,9.0999999999999998E-2,null,224,"",3,"Y"]
["Craggs Lane 33/11kV S Stn","CraggsLane33/11kVSStn",890032,0.156,null,293,"",3,"Y"]
["Cranwell 33/11kV S Stn","Cranwell33/11kVSStn",910031,0.11,null,220,"",3,"Y"]
["Crick 33/11kV S Stn","Crick33/11kVSStn",940068,8.2000000000000003E-2,null,158,"",3,"Y"]
["Croft End Solar Farm 33kV S Stn","CroftEndSolarFarm33kVSStn",905191,7.0000000000000007E-2,null,165,"",3,"Y"]
["Cromford 33/11kV S Stn","Cromford33/11kVSStn",890073,0.21,null,422,"",3,"Y"]
["Crowland 33/11kV S Stn","Crowland33/11kVSStn",910029,0.13800000000000001,null,215,"",3,"Y"]
["Crown Farm 33/11kV S Stn","CrownFarm33/11kVSStn",890037,2.5999999999999999E-2,null,487,"",3,"Y"]
["Daneshill Generation 33kV S Stn","DaneshillGeneration33kVSStn",890017,0.28999999999999998,null,335,"",3,"Y"]
["Danesmoor 33/11kV S Stn","Danesmoor33/11kVSStn",890094,0.26300000000000001,null,108,"",3,"Y"]
["Darley Abbey 33/11kV S Stn","DarleyAbbey33/11kVSStn",870039,0.09,null,132,"",3,"Y"]
["Daventry 132/33kV S Stn","Daventry132/33kVSStn",690052,4.4999999999999998E-2,null,147,"",3,"Y"]
["Daventry 33/11kV S Stn","Daventry33/11kVSStn",940049,4.4999999999999998E-2,null,147,"",3,"Y"]
["Daventry 33kV S Stn","Daventry33kVSStn",940008,4.4999999999999998E-2,null,147,"",3,"Y"]
["Dayfields Farm PV 33kV S Stn","DayfieldsFarmPV33kVSStn",875119,0.24,null,278,"",3,"Y"]
["Decoy Farm Generation 33kV S Stn","DecoyFarmGeneration33kVSStn",917572,0.251,null,314,"",3,"Y"]
["Deepdale Solar Farm 33kV S Stn","DeepdaleSolarFarm33kVSStn",917435,0.12,null,123,"",3,"Y"]
["Deeping St Nicholas Wind Generation 33kV S Stn","DeepingStNicholasWindGeneration33kVSStn",910015,0.7,"Y",500,"Y",3,"Y"]
["Denby 33/11kV S Stn","Denby33/11kVSStn",890082,0.11799999999999999,null,250,"",3,"Y"]
["Denton 33/11kV S Stn","Denton33/11kVSStn",940066,0.28000000000000003,null,425,"",3,"Y"]
["Derby 132/11kV S Stn","Derby132/11kVSStn",870036,8.4000000000000005E-2,null,375,"",1,"Y"]
["Derby 132/33/11kV S Stn","Derby132/33/11kVSStn",680041,8.4000000000000005E-2,null,375,"",3,"Y"]
["Derby 33kV S Stn","Derby33kVSStn",870012,8.4000000000000005E-2,null,375,"",3,"Y"]
["Derby South 132/33kV S Stn","DerbySouth132/33kVSStn",680029,0.05,null,481,"",3,"Y"]
["Derby South 33kV S Stn","DerbySouth33kVSStn",870005,0.05,null,134,"",3,"Y"]
["Derby Waste Sinfin Lane 33kV S Stn","DerbyWasteSinfinLane33kVSStn",875073,0.125,null,334,"",3,"Y"]
["Desborough 33/11kV S Stn","Desborough33/11kVSStn",920048,6.4000000000000001E-2,null,100,"",3,"Y"]
["Desford 33/11kV S Stn","Desford33/11kVSStn",930093,0.111,null,216,"",3,"Y"]
["Dillotford Avenue 33/11kV S Stn","DillotfordAvenue33/11kVSStn",930042,6.7000000000000004E-2,null,162,"",3,"Y"]
["Doddington Park 33/11kV S Stn","DoddingtonPark33/11kVSStn",900028,7.9000000000000001E-2,null,146,"",3,"Y"]
["Donington 33/11kV S Stn","Donington33/11kVSStn",910024,0.128,null,192,"",3,"Y"]
["Dowsby Fen 33/11kV S Stn","DowsbyFen33/11kVSStn",910025,0.154,null,394,"",3,"Y"]
["Drakelow 275/132kV S Stn","Drakelow275/132kVSStn",680005,0.2,"Y",2800,"Y",1,"Y"]
["Drakelow Solar Farm 33kV S Stn","DrakelowSolarFarm33kVSStn",875067,0.18,null,119,"",3,"Y"]
["Dunlop 33/6.6kV S Stn","Dunlop33/6.6kVSStn",930039,9.8000000000000004E-2,null,218,"",3,"Y"]
["Eagle Centre 33/11kV S Stn","EagleCentre33/11kVSStn",870015,0.1,null,95,"",3,"Y"]
["Eakley Lanes North PV 33kV S Stn","EakleyLanesNorthPV33kVSStn",946140,0.152,null,156,"",3,"Y"]
["Eakley Lanes South PV 33kV S Stn","EakleyLanesSouthPV33kVSStn",946141,7.0000000000000007E-2,null,72,"",3,"Y"]
["Eakring Solar Farm 33kV S Stn","EakringSolarFarm33kVSStn",898340,0.22,null,395,"",3,"Y"]
["Earls Barton 33/11kV S Stn","EarlsBarton33/11kVSStn",940053,0.15,null,267,"",3,"Y"]
["Earlstrees 33/11kV S Stn","Earlstrees33/11kVSStn",920052,6.3E-2,null,118,"",3,"Y"]
["East Claydon 132/33kV S Stn","EastClaydon132/33kVSStn",690075,3.9E-2,null,936,"",3,"Y"]
["East Claydon 400/132kV S Stn","EastClaydon400/132kVSStn",690061,3.9E-2,null,936,"",1,"Y"]
["East Leake 33/11kV S Stn","EastLeake33/11kVSStn",880023,0.14399999999999999,null,215,"",3,"Y"]
["Easton 33/11kV S Stn","Easton33/11kVSStn",910041,0.113,null,90,"",3,"Y"]
["Eckington 33/11kV S Stn","Eckington33/11kVSStn",890083,0.122,null,262,"",3,"Y"]
["EFW Paving Way 33kV S Stn","EFWPavingWay33kVSStn",904540,7.3999999999999996E-2,null,164,"",3,"Y"]
["Eldergate 33/11kV S Stn","Eldergate33/11kVSStn",940071,0.05,null,75,"",3,"Y"]
["Ellesmere Avenue 33/11kV S Stn","EllesmereAvenue33/11kVSStn",940055,0.121,null,227,"",3,"Y"]
["Elms Farm Southam Solar Farm 33kV S Stn","ElmsFarmSouthamSolarFarm33kVSStn",939156,0.2,null,290,"",3,"Y"]
["Emberton Pv 33kv S Stn","EmbertonPv33kvSStn",946213,9.6000000000000002E-2,null,108,"",3,"Y"]
["Empingham 33/11kV S Stn","Empingham33/11kVSStn",910056,0.10100000000000001,null,148,"",3,"Y"]
["Enderby 400/132kV S Stn","Enderby400/132kVSStn",690004,6.5000000000000002E-2,null,849,"",1,"Y"]
["English Electric 33/11kV S Stn","EnglishElectric33/11kVSStn",930063,6.4000000000000001E-2,null,170,"",3,"Y"]
["Equitix ESI CHP Notts 33kV S Stn","EquitixESICHPNotts33kVSStn",917673,0.13,null,323,"",3,"Y"]
["Erin Road 33/11kV S Stn","ErinRoad33/11kVSStn",898500,0.25,null,397,"",3,"Y"]
["Ermine Farm Solar Farm 33kV S Stn","ErmineFarmSolarFarm33kVSStn",916813,0.16,null,500,"Y",3,"Y"]
["Exton 33/11kV S Stn","Exton33/11kVSStn",910052,0.52800000000000002,null,737,"",3,"Y"]
["Eyam 33/11kV S Stn","Eyam33/11kVSStn",890066,0.5,null,685,"",3,"Y"]
["Farndon Road 33/11kV S Stn","FarndonRoad33/11kVSStn",920046,5.6000000000000001E-2,null,134,"",3,"Y"]
["Farnsfield 33/11kV S Stn","Farnsfield33/11kVSStn",890056,0.38700000000000001,null,766,"",3,"Y"]
["Fen Farm 33/11kV S Stn","FenFarm33/11kVSStn",940023,9.0999999999999998E-2,null,194,"",3,"Y"]
["Fernwood 33/11kV S Stn","Fernwood33/11kVSStn",900011,0.13200000000000001,null,318,"",3,"Y"]
["Fields Farm Southam Solar Farm 33kV S Stn","FieldsFarmSouthamSolarFarm33kVSStn",939242,0.1,null,138,"",3,"Y"]
["Field Street 33/11kV S Stn","FieldStreet33/11kVSStn",920045,4.9000000000000002E-2,null,124,"",3,"Y"]
["Fiskerton 33/11kV S Stn","Fiskerton33/11kVSStn",900035,0.19,null,392,"",3,"Y"]
["Fiskerton Solar Farm 33kV S Stn","FiskertonSolarFarm33kVSStn",906387,8.4000000000000005E-2,null,229,"",3,"Y"]
["Flagg 33/11kV S Stn","Flagg33/11kVSStn",890064,2.2000000000000002,null,2640,"",3,"Y"]
["Fosse Way Radford Semele Solar Farm 33kV S Stn","FosseWayRadfordSemeleSolarFarm33kVSStn",939301,0.08,null,100,"",3,"Y"]
["Fox Milne 33/11kV S Stn","FoxMilne33/11kVSStn",940043,4.1000000000000002E-2,null,47,"",3,"Y"]
["French Farm Wind Farm 33kV S Stn","FrenchFarmWindFarm33kVSStn",917670,0.105,null,234,"",3,"Y"]
["Garnham Close STOR 33kV S Stn","GarnhamCloseSTOR33kVSStn",898530,0.2,null,102,"",3,"Y"]
["Gawcott Fields Solar Park 33kV S Stn","GawcottFieldsSolarPark33kVSStn",946154,7.4999999999999997E-2,null,69,"",3,"Y"]
["Gaydon 33/11kV S Stn","Gaydon33/11kVSStn",930057,0.28999999999999998,null,286,"",3,"Y"]
["Gec Test Bed Whetstone 33kV S Stn","GecTestBedWhetstone33kVSStn",930090,0.33,null,521,"",3,"Y"]
["Gedling 33/11kV S Stn","Gedling33/11kVSStn",880034,8.7999999999999995E-2,null,215,"",3,"Y"]
["Gipsy Lane 33/11kV S Stn","GipsyLane33/11kVSStn",930080,6.8000000000000005E-2,null,122,"",3,"Y"]
["Glebe Farm Solar Park 33kV S Stn","GlebeFarmSolarPark33kVSStn",926242,0.08,null,52,"",3,"Y"]
["Goitside 132/33kV S Stn","Goitside132/33kVSStn",680038,9.1999999999999998E-2,null,88,"",3,"Y"]
["Goitside 33/6.6kV S Stn","Goitside33/6.6kVSStn",890075,9.1999999999999998E-2,null,88,"",3,"Y"]
["Goitside 33kV S Stn","Goitside33kVSStn",890016,9.1999999999999998E-2,null,88,"",3,"Y"]
["Grange Farm Solar Kirkby On Bain 33kV S Stn","GrangeFarmSolarKirkbyOnBain33kVSStn",906537,5.1999999999999998E-2,null,46,"",3,"Y"]
["Grantham 132/33kV S Stn","Grantham132/33kVSStn",690041,0.3,null,1096,"",3,"Y"]
["Grantham 33kV S Stn","Grantham33kVSStn",910003,0.3,null,1096,"",3,"Y"]
["Grantham North 132/11kV S Stn","GranthamNorth132/11kVSStn",910018,0.104,null,376,"",1,"Y"]
["Grantham North 132/25/11kV S Stn","GranthamNorth132/25/11kVSStn",690031,0.104,null,376,"",1,"Y"]
["Grantham South 132/11kV S Stn","GranthamSouth132/11kVSStn",910036,0.2,null,700,"",1,"Y"]
["Grantham South 132kV S Stn","GranthamSouth132kVSStn",690032,0.2,null,700,"",1,"Y"]
["Grassmoor 33/11kV S Stn","Grassmoor33/11kVSStn",890084,0.08,null,182,"",3,"Y"]
["Great Hale 33/11kV S Stn","GreatHale33/11kVSStn",900023,0.19600000000000001,null,226,"",3,"Y"]
["Greatmoor Efw Calvert 33kv S Stn","GreatmoorEfwCalvert33kvSStn",946240,0.05,null,154,"",3,"Y"]
["Green Lane Marchinton PV 33kV S Stn","GreenLaneMarchintonPV33kVSStn",875036,0.24,null,411,"",3,"Y"]
["Grendon 400/132kV S Stn","Grendon400/132kVSStn",690007,0.2,"Y",2800,"Y",1,"Y"]
["Gresley 132/33kV S Stn","Gresley132/33kVSStn",680035,0.11700000000000001,null,671,"",3,"Y"]
["Gresley 33/11kV S Stn","Gresley33/11kVSStn",870053,0.11700000000000001,null,671,"",3,"Y"]
["Gresley 33kV S Stn","Gresley33kVSStn",870010,0.11700000000000001,null,671,"",3,"Y"]
["Groby Road 33/11kV S Stn","GrobyRoad33/11kVSStn",920027,8.4000000000000005E-2,null,164,"",3,"Y"]
["Gulson Road 33/6.6kV S Stn","GulsonRoad33/6.6kVSStn",930043,9.8000000000000004E-2,null,206,"",3,"Y"]
["Gypsum Solar Farm 33kV S Stn","GypsumSolarFarm33kVSStn",926431,0.08,null,112,"",3,"Y"]
["Halfway 33/11kV S Stn","Halfway33/11kVSStn",890089,0.11799999999999999,null,184,"",3,"Y"]
["Hallcroft Road 33/11kV S Stn","HallcroftRoad33/11kVSStn",890052,0.20599999999999999,null,225,"",3,"Y"]
["Hall Farm Newbold Verdon 33kV S Stn","HallFarmNewboldVerdon33kVSStn",939122,0.22500000000000001,null,338,"",3,"Y"]
["Hamilton 33/11kV S Stn","Hamilton33/11kVSStn",920044,7.8E-2,null,204,"",3,"Y"]
["Handley Park Solar Park 33kv S Stn","HandleyParkSolarPark33kvSStn",946180,0.11,null,109,"",3,"Y"]
["Hanslope Park 33/11kV S Stn","HanslopePark33/11kVSStn",940022,0.13100000000000001,null,192,"",3,"Y"]
["Harbury 132/33kV S Stn","Harbury132/33kVSStn",690010,0.06,null,281,"",3,"Y"]
["Harbury 33/11kV S Stn","Harbury33/11kVSStn",930058,0.06,null,281,"",3,"Y"]
["Harbury 33kV S Stn","Harbury33kVSStn",930011,0.06,null,281,"",3,"Y"]
["Harrold 33/11kV S Stn","Harrold33/11kVSStn",920061,0.156,null,232,"",3,"Y"]
["Hartwell Road 33kV S Stn","HartwellRoad33kVSStn",946139,6.9000000000000006E-2,null,142,"",3,"Y"]
["Hatton 33/11kV S Stn","Hatton33/11kVSStn",870031,4.3999999999999997E-2,null,88,"",3,"Y"]
["Hatton Gas Compressor 132kV S Stn","HattonGasCompressor132kVSStn",690064,0.15,null,480,"",1,"Y"]
["Hawkesmill Lane 33/6.6kV S Stn","HawkesmillLane33/6.6kVSStn",930028,0.152,null,269,"",3,"Y"]
["Hawton 132/33kV S Stn","Hawton132/33kVSStn",690042,7.0000000000000007E-2,null,469,"",3,"Y"]
["Hawton 33/11kV S Stn","Hawton33/11kVSStn",900026,7.0000000000000007E-2,null,469,"",3,"Y"]
["Hawton 33kV S Stn","Hawton33kVSStn",900003,7.0000000000000007E-2,null,469,"",3,"Y"]
["Hawton Wind Farm 33kV S Stn","HawtonWindFarm33kVSStn",906972,0.27,null,684,"",3,"Y"]
["Hazelwood 33/11kV S Stn","Hazelwood33/11kVSStn",920050,0.13,null,2117,"",3,"Y"]
["Heanor 132/33kV S Stn","Heanor132/33kVSStn",680036,9.5000000000000001E-2,null,522,"",3,"Y"]
["Heanor 33/11kV S Stn","Heanor33/11kVSStn",870022,9.5000000000000001E-2,null,522,"",3,"Y"]
["Heanor 33kV S Stn","Heanor33kVSStn",870007,9.5000000000000001E-2,null,522,"",3,"Y"]
["Hermitage Lane Generation 33kV S Stn","HermitageLaneGeneration33kVSStn",898541,0.61,null,325,"",3,"Y"]
["Higham Ferrers Switching Station 33kV S Stn","HighamFerrersSwitchingStation33kVSStn",926264,0.27,null,331,"",3,"Y"]
["Highfields 33/11kV S Stn","Highfields33/11kVSStn",920036,9.8000000000000004E-2,null,318,"",3,"Y"]
["Hill Farm Battery Generation 33kV S Stn","HillFarmBatteryGeneration33kVSStn",939476,0.38700000000000001,null,617,"",3,"Y"]
["Hillmorton 33/11kV S Stn","Hillmorton33/11kVSStn",930067,7.0000000000000007E-2,null,182,"",3,"Y"]
["Hinckley 132/11kV S Stn","Hinckley132/11kVSStn",930103,0.159,null,872,"",1,"Y"]
["Hinckley 132/33/11kV S Stn","Hinckley132/33/11kVSStn",690029,0.159,null,872,"",3,"Y"]
["Hinckley 33kV S Stn","Hinckley33kVSStn",930019,0.159,null,872,"",3,"Y"]
["Hindlow 33/11kV S Stn","Hindlow33/11kVSStn",890063,1.3,null,2200,"",3,"Y"]
["Hockley Farm Road 33/11kV S Stn","HockleyFarmRoad33/11kVSStn",926144,0.1,null,331,"",3,"Y"]
["Holbeach 33/11kV S Stn","Holbeach33/11kVSStn",910026,7.5999999999999998E-2,null,111,"",3,"Y"]
["Holbrook Lane 33/6.6kV S Stn","HolbrookLane33/6.6kVSStn",930038,0.04,null,73,"",3,"Y"]
["Holme Carr 33/11kV S Stn","HolmeCarr33/11kVSStn",890042,0.314,null,566,"",3,"Y"]
["Holtwood Farm Solar Park 33kV S Stn","HoltwoodFarmSolarPark33kVSStn",875065,0.22,null,274,"",3,"Y"]
["Holwell 33/11kV S Stn","Holwell33/11kVSStn",910044,7.6999999999999999E-2,null,106,"",3,"Y"]
["Holyhead Road 33/11kV S Stn","HolyheadRoad33/11kVSStn",930037,5.1999999999999998E-2,null,90,"",3,"Y"]
["Homestead Solar Park 33kV S Stn","HomesteadSolarPark33kVSStn",946176,0.27100000000000002,null,306,"",3,"Y"]
["Hopton 33/11kV S Stn","Hopton33/11kVSStn",890071,1.1970000000000001,null,1831,"",3,"Y"]
["Horncastle 33/11kV S Stn","Horncastle33/11kVSStn",900013,0.127,null,251,"",3,"Y"]
["Horsemoor Drove Solar 33kV S Stn","HorsemoorDroveSolar33kVSStn",917574,0.06,null,121,"",3,"Y"]
["Hucknall 33/11kV S Stn","Hucknall33/11kVSStn",880011,0.191,null,285,"",3,"Y"]
["Huthwaite 33/11kV S Stn","Huthwaite33/11kVSStn",890027,7.9000000000000001E-2,null,132,"",3,"Y"]
["Ilkeston 33/11kV S Stn","Ilkeston33/11kVSStn",870048,0.17,null,276,"",3,"Y"]
["Infinity Park 33/11kv S Stn","InfinityPark33/11kvSStn",875136,0.14799999999999999,null,410,"",3,"Y"]
["Ingoldmells 33/11kV S Stn","Ingoldmells33/11kVSStn",900017,0.105,null,210,"",3,"Y"]
["Interlink Park 33/11 Kv S Stn","InterlinkPark33/11KvSStn",930084,0.17100000000000001,null,380,"",3,"Y"]
["Irchester Road Switching Station 33kV S Stn","IrchesterRoadSwitchingStation33kVSStn",926349,0.309,null,200,"",3,"Y"]
["Irthlingborough 132/33kV S Stn","Irthlingborough132/33kVSStn",690049,6.5000000000000002E-2,null,131,"",3,"Y"]
["Irthlingborough 33/11kV S Stn","Irthlingborough33/11kVSStn",921092,6.5000000000000002E-2,null,131,"",3,"Y"]
["Irthlingborough 33kV S Stn","Irthlingborough33kVSStn",928000,6.5000000000000002E-2,null,131,"",3,"Y"]
["Jaguar Browns Lane 33/11kv S Stn","JaguarBrownsLane33/11kvSStn",930029,9.2999999999999999E-2,null,160,"",3,"Y"]
["Jaguar Land Rover 33/11kV S Stn","JaguarLandRover33/11kVSStn",939305,0.28999999999999998,null,286,"",3,"Y"]
["JLR Whitley 33/11kV S Stn","JLRWhitley33/11kVSStn",939482,0.7,null,340,"",3,"Y"]
["Jupiter 33/11kV S Stn","Jupiter33/11kVSStn",920028,7.4999999999999997E-2,null,153,"",3,"Y"]
["Kelmarsh Wind Farm 33kV S Stn","KelmarshWindFarm33kVSStn",926263,0.15,null,329,"",3,"Y"]
["Kenilworth 33/11kV S Stn","Kenilworth33/11kVSStn",930050,0.08,null,142,"",3,"Y"]
["Kettering 132/33kV S Stn","Kettering132/33kVSStn",690050,0.02,null,168,"",3,"Y"]
["Kettering 33kV S Stn","Kettering33kVSStn",920008,0.02,null,168,"",3,"Y"]
["Kettering North 33/11kV S Stn","KetteringNorth33/11kVSStn",920013,5.8999999999999997E-2,null,142,"",3,"Y"]
["Ketton Cement 33/11kV S Stn","KettonCement33/11kVSStn",910051,0.17299999999999999,null,284,"",3,"Y"]
["Keyworth 33/11kV S Stn","Keyworth33/11kVSStn",880033,0.105,null,211,"",3,"Y"]
["Kibworth 132/33kV S Stn","Kibworth132/33kVSStn",690028,9.5000000000000001E-2,null,319,"",3,"Y"]
["Kibworth 33/11kV S Stn","Kibworth33/11kVSStn",920043,9.5000000000000001E-2,null,319,"",3,"Y"]
["Kibworth 33kV S Stn","Kibworth33kVSStn",920001,9.5000000000000001E-2,null,319,"",3,"Y"]
["Kiln Farm 33/11kV S Stn","KilnFarm33/11kVSStn",940034,3.5000000000000003E-2,null,93,"",3,"Y"]
["Kilton Road 33/11kV S Stn","KiltonRoad33/11kVSStn",890043,0.23799999999999999,null,395,"",3,"Y"]
["Kingsthorpe 33/11kV S Stn","Kingsthorpe33/11kVSStn",940060,0.11899999999999999,null,223,"",3,"Y"]
["Kingston 33/11kV S Stn","Kingston33/11kVSStn",940070,0.06,null,136,"",3,"Y"]
["Kirton 33/11kV S Stn","Kirton33/11kVSStn",910022,9.6000000000000002E-2,null,192,"",3,"Y"]
["Langar Solar Switch Room 33kV S Stn","LangarSolarSwitchRoom33kVSStn",883446,0.16400000000000001,null,198,"",3,"Y"]
["Langdale Drive 33/11kV S Stn","LangdaleDrive33/11kVSStn",930081,0.112,null,202,"",3,"Y"]
["Langrick 33/11kV S Stn","Langrick33/11kVSStn",900021,0.22900000000000001,null,307,"",3,"Y"]
["Lawford 33/11kV S Stn","Lawford33/11kVSStn",930055,5.1999999999999998E-2,null,134,"",3,"Y"]
["Leadenham 33/11kV S Stn","Leadenham33/11kVSStn",910058,8.5999999999999993E-2,null,248,"",3,"Y"]
["Lea Marston 400/132kV S Stn","LeaMarston400/132kVSStn",720004,0.2,"Y",2800,"Y",1,"Y"]
["Leicester 132/33kV S Stn","Leicester132/33kVSStn",690026,4.2999999999999997E-2,null,524,"",1,"Y"]
["Leicester 33/11kV S Stn","Leicester33/11kVSStn",920033,4.2999999999999997E-2,null,524,"",1,"Y"]
["Leicester 33kV S Stn","Leicester33kVSStn",920006,4.2999999999999997E-2,null,524,"",1,"Y"]
["Leicester East 132/33kV S Stn","LeicesterEast132/33kVSStn",690025,3.6999999999999998E-2,null,68,"",3,"Y"]
["Leicester East 33/6.6kV S Stn","LeicesterEast33/6.6kVSStn",920040,3.6999999999999998E-2,null,35,"",3,"Y"]
["Leicester East 33kV S Stn","LeicesterEast33kVSStn",920004,3.6999999999999998E-2,null,35,"",3,"Y"]
["Leicester North 132/33kV S Stn","LeicesterNorth132/33kVSStn",690023,0.1,null,113,"",3,"Y"]
["Leicester North 33/11kV S Stn","LeicesterNorth33/11kVSStn",920030,0.1,null,113,"",3,"Y"]
["Leicester North 33kV S Stn","LeicesterNorth33kVSStn",920003,0.1,null,113,"",3,"Y"]
["Lenton 33/11kV S Stn","Lenton33/11kVSStn",880014,0.17599999999999999,null,412,"",3,"Y"]
["Lero 33/6.6kV S Stn","Lero33/6.6kVSStn",920023,0.09,null,166,"",3,"Y"]
["Leverton Battery Storage 33kV S Stn","LevertonBatteryStorage33kVSStn",907046,0.91200000000000003,null,218,"",3,"Y"]
["Leverton Solar Park 33kV S Stn","LevertonSolarPark33kVSStn",906126,0.7,"Y",500,"Y",3,"Y"]
["Lilbourne Wind Farm 33kV S Stn","LilbourneWindFarm33kVSStn",946165,0.18,null,257,"",3,"Y"]
["Lime Tree Place 33/11kV S Stn","LimeTreePlace33/11kVSStn",890039,0.154,null,233,"",3,"Y"]
["Lincoln Farm Solar 33kV S Stn","LincolnFarmSolar33kVSStn",906936,0.14799999999999999,null,359,"",3,"Y"]
["Lincoln Local 132kV S Stn","LincolnLocal132kVSStn",690058,7.0000000000000007E-2,null,261,"",1,"Y"]
["Lincoln Local No 2 132/11kV S Stn","LincolnLocalNo2132/11kVSStn",900034,7.0000000000000007E-2,null,260,"",1,"Y"]
["Lincoln Local No 4 132/11kV S Stn","LincolnLocalNo4132/11kVSStn",907000,7.0000000000000007E-2,null,261,"",1,"Y"]
["Lincoln Main 132/33/11kV S Stn","LincolnMain132/33/11kVSStn",690057,0.04,null,236,"",3,"Y"]
["Lincoln No 1 33kV S Stn","LincolnNo133kVSStn",900002,0.04,null,236,"",3,"Y"]
["Lincoln No 2 33kV S Stn","LincolnNo233kVSStn",690073,0.04,null,236,"",3,"Y"]
["Lincoln No 5 132/11kV S Stn","LincolnNo5132/11kVSStn",900040,0.04,null,236,"",1,"Y"]
["Lindhurst Wind Farm 33kV S Stn","LindhurstWindFarm33kVSStn",890022,0.40400000000000003,null,553,"",3,"Y"]
["Lindridge Farm Solar Park 33kV S Stn","LindridgeFarmSolarPark33kVSStn",939263,0.13700000000000001,null,278,"",3,"Y"]
["Little Hallam 33/11kV S Stn","LittleHallam33/11kVSStn",870049,0.17499999999999999,null,315,"",3,"Y"]
["Little Irchester 33/11kV S Stn","LittleIrchester33/11kVSStn",920060,0.14000000000000001,null,420,"",3,"Y"]
["Little Morton Solar Farm 33kV S Stn","LittleMortonSolarFarm33kVSStn",898284,8.5000000000000006E-2,null,134,"",3,"Y"]
["Littlewood Farm PV 33kV S Stn","LittlewoodFarmPV33kVSStn",898475,0.28999999999999998,null,442,"",3,"Y"]
["Littlewood Farm Solar 33kV S Stn","LittlewoodFarmSolar33kVSStn",946198,0.28000000000000003,null,101,"",3,"Y"]
["Lockheed 33/11kV S Stn","Lockheed33/11kVSStn",930056,0.11700000000000001,null,22,"",3,"Y"]
["Lodge Farm Solar 33kV S Stn","LodgeFarmSolar33kVSStn",898432,0.09,null,132,"",3,"Y"]
["Lodge Farm Solar Park 33kV S Stn","LodgeFarmSolarPark33kVSStn",883349,0.09,null,132,"",3,"Y"]
["London Road 33/6.6kV S Stn","LondonRoad33/6.6kVSStn",930027,8.4000000000000005E-2,null,82,"",3,"Y"]
["London Road Heat Station 33kV S Stn","LondonRoadHeatStation33kVSStn",880042,3.1E-2,null,47,"",3,"Y"]
["Longcliffe 33/11kV S Stn","Longcliffe33/11kVSStn",890067,0.65,null,1276,"",3,"Y"]
["Long Eaton 33/11kV S Stn","LongEaton33/11kVSStn",870050,6.4000000000000001E-2,null,115,"",3,"Y"]
["Long Sutton 33/11kV S Stn","LongSutton33/11kVSStn",910027,0.13400000000000001,null,257,"",3,"Y"]
["Loscoe 132kV S Stn","Loscoe132kVSStn",680069,0.11,null,576,"",1,"Y"]
["Loughborough 132/11kV S Stn","Loughborough132/11kVSStn",920020,9.1999999999999998E-2,null,436,"",1,"Y"]
["Loughborough 132/33/11kV S Stn","Loughborough132/33/11kVSStn",690022,9.1999999999999998E-2,null,436,"",3,"Y"]
["Loughborough 33kV S Stn","Loughborough33kVSStn",920002,9.1999999999999998E-2,null,436,"",3,"Y"]
["Low Farm AD 33kV S Stn","LowFarmAD33kVSStn",897792,0.27300000000000002,null,355,"",3,"Y"]
["Low Spinney Wind Farm 33kV S Stn","LowSpinneyWindFarm33kVSStn",938992,0.1,null,140,"",3,"Y"]
["Lutterworth 33/11kV S Stn","Lutterworth33/11kVSStn",930062,7.1999999999999995E-2,null,122,"",3,"Y"]
["Lyon Road Generation 33kV S Stn","LyonRoadGeneration33kVSStn",946411,0.7,"Y",500,"Y",3,"Y"]
["Mackworth 33/11kV S Stn","Mackworth33/11kVSStn",870038,9.8000000000000004E-2,null,200,"",3,"Y"]
["Magna Park 33/11kV S Stn","MagnaPark33/11kVSStn",930107,0.127,null,245,"",3,"Y"]
["Manor Farm PV Horton 33kV S Stn","ManorFarmPVHorton33kVSStn",946270,0.11,null,165,"",3,"Y"]
["Mansfield 132/33kV S Stn","Mansfield132/33kVSStn",680018,0.1,null,383,"",3,"Y"]
["Mansfield 33/11kV S Stn","Mansfield33/11kVSStn",890036,0.1,null,383,"",3,"Y"]
["Mansfield 33kV S Stn","Mansfield33kVSStn",890008,0.1,null,383,"",3,"Y"]
["Mansfield Street 33/11kV S Stn","MansfieldStreet33/11kVSStn",920024,0.157,null,393,"",3,"Y"]
["Mantle Lane 33/11kV S Stn","MantleLane33/11kVSStn",930098,0.05,null,80,"",3,"Y"]
["Manton 33/11kV S Stn","Manton33/11kVSStn",890044,0.27,null,385,"",3,"Y"]
["Mapperley 33/11kV S Stn","Mapperley33/11kVSStn",880029,9.6000000000000002E-2,null,145,"",3,"Y"]
["Marchington 33/11kV S Stn","Marchington33/11kVSStn",870028,0.215,null,338,"",3,"Y"]
["Market Deeping 33/11kV S Stn","MarketDeeping33/11kVSStn",910045,0.19,null,258,"",3,"Y"]
["Market Harborough 33/11kV S Stn","MarketHarborough33/11kVSStn",920047,0.17,null,262,"",3,"Y"]
["Market Overton 33/11kV S Stn","MarketOverton33/11kVSStn",910048,0.23200000000000001,null,282,"",3,"Y"]
["Marlborough Road 33/11kV S Stn","MarlboroughRoad33/11kVSStn",880026,0.161,null,243,"",3,"Y"]
["Marlborough Street 33/11kV S Stn","MarlboroughStreet33/11kVSStn",940037,8.1000000000000003E-2,null,230,"",3,"Y"]
["Marsh Lane 33/11kV S Stn","MarshLane33/11kVSStn",900007,0.105,null,230,"",3,"Y"]
["Matlock 33/11kV S Stn","Matlock33/11kVSStn",890074,0.106,null,165,"",3,"Y"]
["Maxwell House Data Centre 33/11kV S Stn","MaxwellHouseDataCentre33/11kVSStn",945675,0.23,null,208,"",3,"Y"]
["Meadow Farm Solar 33kV S Stn","MeadowFarmSolar33kVSStn",926406,0.18,null,217,"",3,"Y"]
["Meadow Lane 33/11kV S Stn","MeadowLane33/11kVSStn",890090,0.215,null,424,"",3,"Y"]
["Melbourne 33/11kV S Stn","Melbourne33/11kVSStn",870017,0.129,null,249,"",3,"Y"]
["Melton Mowbray 132/33kV S Stn","MeltonMowbray132/33kVSStn",690033,4.2999999999999997E-2,null,242,"",3,"Y"]
["Melton Mowbray 33/11kV S Stn","MeltonMowbray33/11kVSStn",910039,4.2999999999999997E-2,null,242,"",3,"Y"]
["Melton Mowbray 33kV S Stn","MeltonMowbray33kVSStn",910006,4.2999999999999997E-2,null,242,"",3,"Y"]
["Metheringham 33/11kV S Stn","Metheringham33/11kVSStn",900037,0.13,null,250,"",3,"Y"]
["Middlefield 33/11kV S Stn","Middlefield33/11kVSStn",930088,0.19700000000000001,null,388,"",3,"Y"]
["Middlemarsh 132kV S Stn","Middlemarsh132kVSStn",690021,0.2,"Y",1000,"Y",1,"Y"]
["Millclose 33/11kV S Stn","Millclose33/11kVSStn",890068,0.16400000000000001,null,273,"",3,"Y"]
["Mill Farm Battery Storage 33kV S Stn","MillFarmBatteryStorage33kVSStn",917757,0.57499999999999996,null,642,"",3,"Y"]
["Mill Farm Solar Boothby Great Wood 33kV S Stn","MillFarmSolarBoothbyGreatWood33kVSStn",917647,0.21299999999999999,null,234,"",3,"Y"]
["Misson 33/11kV S Stn","Misson33/11kVSStn",890049,0.17799999999999999,null,343,"",3,"Y"]
["Misterton 33/11kV S Stn","Misterton33/11kVSStn",890060,0.30099999999999999,null,286,"",3,"Y"]
["Moat Farm Draycott-In-The-Clay Solar Site 33kV S Stn","MoatFarmDraycott-In-The-ClaySolarSite33kVSStn",875043,0.7,"Y",500,"Y",3,"Y"]
["Moat Farm Solar Farm 33kV S Stn","MoatFarmSolarFarm33kVSStn",898324,0.43,null,305,"",3,"Y"]
["Moira 33/11kV S Stn","Moira33/11kVSStn",930102,0.14599999999999999,null,283,"",3,"Y"]
["Moorgreen 33/11kV S Stn","Moorgreen33/11kVSStn",890025,0.114,null,251,"",3,"Y"]
["Morley 33/11kV S Stn","Morley33/11kVSStn",870042,0.104,null,208,"",3,"Y"]
["Mount Bridge 33/11kV S Stn","MountBridge33/11kVSStn",900022,0.08,null,151,"",3,"Y"]
["Mount Mill Solar Park 33kV S Stn","MountMillSolarPark33kVSStn",946174,0.09,null,203,"",3,"Y"]
["Mountsorrel 33/11kV S Stn","Mountsorrel33/11kVSStn",920025,0.192,null,369,"",3,"Y"]
["Nailstone 33/11kV S Stn","Nailstone33/11kVSStn",930097,0.49399999999999999,null,935,"",3,"Y"]
["New Albion Wind Farm 33kV S Stn","NewAlbionWindFarm33kVSStn",926186,0.182,null,275,"",3,"Y"]
["Newark Junction 33/11kV S Stn","NewarkJunction33/11kVSStn",900024,0.161,null,240,"",3,"Y"]
["New Beacon Road 33/11kV S Stn","NewBeaconRoad33/11kVSStn",910034,0.08,null,102,"",3,"Y"]
["Newdigate 33/11kV S Stn","Newdigate33/11kVSStn",930079,0.23,null,390,"",3,"Y"]
["Newport Pagnell 33/11kV S Stn","NewportPagnell33/11kVSStn",940041,0.13100000000000001,null,271,"",3,"Y"]
["Newton Road 33/11kV S Stn","NewtonRoad33/11kVSStn",940040,0.109,null,167,"",3,"Y"]
["Normanton 33/11kV S Stn","Normanton33/11kVSStn",870040,0.11899999999999999,null,238,"",3,"Y"]
["Northampton 132/33kV S Stn","Northampton132/33kVSStn",690055,5.2999999999999999E-2,null,570,"",3,"Y"]
["Northampton 33/11kV S Stn","Northampton33/11kVSStn",940061,5.2999999999999999E-2,null,570,"",3,"Y"]
["Northampton 33kV S Stn","Northampton33kVSStn",940009,5.2999999999999999E-2,null,570,"",3,"Y"]
["Northampton East 132/33kV S Stn","NorthamptonEast132/33kVSStn",690053,0.09,null,637,"",3,"Y"]
["Northampton East 33/11kV S Stn","NorthamptonEast33/11kVSStn",946045,0.09,null,637,"",3,"Y"]
["Northampton East 33kV S Stn","NorthamptonEast33kVSStn",940010,0.09,null,637,"",3,"Y"]
["Northampton West 132/33kV S Stn","NorthamptonWest132/33kVSStn",690054,5.2999999999999999E-2,null,1000,"Y",3,"Y"]
["Northampton West 33/11kV S Stn","NorthamptonWest33/11kVSStn",940054,5.2999999999999999E-2,null,43,"",3,"Y"]
["Northampton West 33kV S Stn","NorthamptonWest33kVSStn",940012,5.2999999999999999E-2,null,375,"",3,"Y"]
["North Greetwell 132kV S Stn","NorthGreetwell132kVSStn",690063,0.23200000000000001,null,1392,"",1,"Y"]
["North Hykeham 33/11kV S Stn","NorthHykeham33/11kVSStn",900029,9.4E-2,null,150,"",3,"Y"]
["North Rauceby 33kV S Stn","NorthRauceby33kVSStn",917778,0.93,null,252,"",3,"Y"]
["North Wheatley 33/11kV S Stn","NorthWheatley33/11kVSStn",890057,0.53400000000000003,null,555,"",3,"Y"]
["North Wilford 33/11kV S Stn","NorthWilford33/11kVSStn",880017,6.6000000000000003E-2,null,193,"",3,"Y"]
["Nottingham 132/33kV S Stn","Nottingham132/33kVSStn",680023,7.6999999999999999E-2,null,601,"",3,"Y"]
["Nottingham 33kV S Stn","Nottingham33kVSStn",880003,7.6999999999999999E-2,null,601,"",3,"Y"]
["Nottingham East 132/33kV S Stn","NottinghamEast132/33kVSStn",680015,3.2000000000000001E-2,null,275,"",3,"Y"]
["Nottingham East 33kV S Stn","NottinghamEast33kVSStn",880002,3.2000000000000001E-2,null,275,"",3,"Y"]
["Nottingham North 132/11kV S Stn","NottinghamNorth132/11kVSStn",880021,1.7999999999999999E-2,null,160,"",1,"Y"]
["Nottingham North 132/33/11kV S Stn","NottinghamNorth132/33/11kVSStn",680022,1.7999999999999999E-2,null,160,"",3,"Y"]
["Nottingham North 33kV S Stn","NottinghamNorth33kVSStn",880005,1.7999999999999999E-2,null,160,"",3,"Y"]
["Nottingham Road STOR 33kV S Stn","NottinghamRoadSTOR33kVSStn",875155,0.7,"Y",500,"Y",3,"Y"]
["Nowhere Farm PV 33kV S Stn","NowhereFarmPV33kVSStn",917543,0.05,null,60,"",3,"Y"]
["Nuneaton 132/33kV S Stn","Nuneaton132/33kVSStn",690018,8.5000000000000006E-2,null,632,"",3,"Y"]
["Nuneaton 33/11kV S Stn","Nuneaton33/11kVSStn",930077,8.5000000000000006E-2,null,632,"",3,"Y"]
["Nuneaton 33kV S Stn","Nuneaton33kVSStn",930004,8.5000000000000006E-2,null,632,"",3,"Y"]
["Oakham 132/33kV S Stn","Oakham132/33kVSStn",690038,8.6999999999999994E-2,null,413,"",3,"Y"]
["Oakham 33/11kV S Stn","Oakham33/11kVSStn",910055,8.6999999999999994E-2,null,413,"",3,"Y"]
["Oakham 33kV S Stn","Oakham33kVSStn",910007,8.6999999999999994E-2,null,413,"",3,"Y"]
["Oakley 33/11kV S Stn","Oakley33/11kVSStn",920051,0.05,null,97,"",3,"Y"]
["Old Dalby 33/11kV S Stn","OldDalby33/11kVSStn",910043,0.26100000000000001,null,381,"",3,"Y"]
["Old Dalby Lodge Wind Farm 33kV S Stn","OldDalbyLodgeWindFarm33kVSStn",690071,0.13900000000000001,null,285,"",3,"Y"]
["Ollerton 33/11kV S Stn","Ollerton33/11kVSStn",890051,0.19,null,376,"",3,"Y"]
["Olney 33/11kV S Stn","Olney33/11kVSStn",940045,0.09,null,137,"",3,"Y"]
["Olney Hyde Farm Solar 33kV S Stn","OlneyHydeFarmSolar33kVSStn",946329,8.8999999999999996E-2,null,137,"",3,"Y"]
["Ordsall Road 33/11kV S Stn","OrdsallRoad33/11kVSStn",890053,0.19400000000000001,null,360,"",3,"Y"]
["Osbaston 33/11kV S Stn","Osbaston33/11kVSStn",930100,0.35,null,603,"",3,"Y"]
["Osmaston Road 33/6.6kv S Stn","OsmastonRoad33/6.6kvSStn",870045,0.7,"Y",500,"Y",3,"Y"]
["Oundle 33/11kV S Stn","Oundle33/11kVSStn",920055,0.28000000000000003,null,409,"",3,"Y"]
["Oxcroft Solar Farm 33kV S Stn","OxcroftSolarFarm33kVSStn",898478,0.11899999999999999,null,204,"",3,"Y"]
["Pailton 132/33kV S Stn","Pailton132/33kVSStn",930018,0.19,null,807,"",3,"Y"]
["Pailton 33kV S Stn","Pailton33kVSStn",690067,0.19,null,807,"",3,"Y"]
["Park Farm 33/11kV S Stn","ParkFarm33/11kVSStn",920065,9.6000000000000002E-2,null,188,"",3,"Y"]
["Pebble Hall Generation 33kV S Stn","PebbleHallGeneration33kVSStn",939208,0.182,null,355,"",3,"Y"]
["Petsoe Manor Wind Farm 33kV S Stn","PetsoeManorWindFarm33kVSStn",940024,0.7,"Y",500,"Y",3,"Y"]
["Pineham 33/11kV S Stn","Pineham33/11kVSStn",940021,0.22800000000000001,null,392,"",3,"Y"]
["Pinxton 132/11kV S Stn","Pinxton132/11kVSStn",890021,0.13400000000000001,null,601,"",1,"Y"]
["Pinxton 132kV S Stn","Pinxton132kVSStn",680010,0.13400000000000001,null,601,"",1,"Y"]
["Pipewell Road PV 33kV S Stn","PipewellRoadPV33kVSStn",926202,0.13,null,202,"",3,"Y"]
["Polesworth 33/11kV S Stn","Polesworth33/11kVSStn",930072,0.11,null,259,"",3,"Y"]
["Portway 33/11kV S Stn","Portway33/11kVSStn",940038,3.3000000000000002E-2,null,65,"",3,"Y"]
["Prestop Fm Burton Rd Ashby 33kv S Stn","PrestopFmBurtonRdAshby33kvSStn",939150,0.129,null,500,"Y",3,"Y"]
["Princethorpe 33/11kV S Stn","Princethorpe33/11kVSStn",930059,0.2,null,342,"",3,"Y"]
["Private Road No 5 Colwick STOR 33kV S Stn","PrivateRoadNo5ColwickSTOR33kVSStn",883570,0.7,"Y",500,"Y",3,"Y"]
["Pytchley Road 33/11kV S Stn","PytchleyRoad33/11kVSStn",920009,7.5999999999999998E-2,null,131,"",3,"Y"]
["Queens Park 33/11kV S Stn","QueensPark33/11kVSStn",890079,0.1,null,159,"",3,"Y"]
["Quorn 33/11kV S Stn","Quorn33/11kVSStn",920022,0.20100000000000001,null,390,"",3,"Y"]
["RAF Cranwell High G Facility 33kV S Stn","RAFCranwellHighGFacility33kVSStn",917678,1.04,null,1372,"",3,"Y"]
["Ragdale PV Solar Park 33kV S Stn","RagdalePVSolarPark33kVSStn",926220,9.7000000000000003E-2,null,106,"",3,"Y"]
["Ratcliffe 400/132kV S Stn","Ratcliffe400/132kVSStn",680002,6.4399999999999999E-2,null,1269,"",1,"Y"]
["Ratcliffe On Soar 33/11kV S Stn","RatcliffeOnSoar33/11kVSStn",880018,6.4399999999999999E-2,null,1269,"",3,"Y"]
["Raunds 33/11kV S Stn","Raunds33/11kVSStn",920062,0.12,null,190,"",3,"Y"]
["Raunds 33kV S Stn","Raunds33kVSStn",690074,0.12,null,190,"",3,"Y"]
["Ravensdale Park 33/11kV S Stn","RavensdalePark33/11kVSStn",870033,0.20200000000000001,null,290,"",3,"Y"]
["Redcross Street 33/11kV S Stn","RedcrossStreet33/11kVSStn",920032,9.7000000000000003E-2,null,148,"",3,"Y"]
["Redfield Road 1 STOR 33kV S Stn","RedfieldRoad1STOR33kVSStn",883447,0.42,null,593,"",3,"Y"]
["Redfield Road 2 STOR 33kV S Stn","RedfieldRoad2STOR33kVSStn",883503,0.36,null,683,"",3,"Y"]
["Redhouse Farm Wind Farm Gedney 33kV S Stn","RedhouseFarmWindFarmGedney33kVSStn",910016,4.8000000000000001E-2,null,50,"",3,"Y"]
["Regent Street 33/11kV S Stn","RegentStreet33/11kVSStn",910049,0.21,null,414,"",3,"Y"]
["Retford 132/25kV S Stn","Retford132/25kVSStn",680021,0.253,null,1204,"",1,"Y"]
["Retford Road Solar Generation 33kV S Stn","RetfordRoadSolarGeneration33kVSStn",898483,0.53,null,695,"",3,"Y"]
["Ripley 33/11kV S Stn","Ripley33/11kVSStn",890088,0.16300000000000001,null,319,"",3,"Y"]
["Roade 33/11kV S Stn","Roade33/11kVSStn",940063,0.111,null,179,"",3,"Y"]
["Roade Wind Farm 33kV S Stn","RoadeWindFarm33kVSStn",945674,0.12,null,194,"",3,"Y"]
["Robert Hyde 33/11kV S Stn","RobertHyde33/11kVSStn",890081,0.17699999999999999,null,350,"",3,"Y"]
["Robin Hood 33/11kV S Stn","RobinHood33/11kVSStn",890069,0.26800000000000002,null,359,"",3,"Y"]
["Rocester 33/11kV S Stn","Rocester33/11kVSStn",870026,0.13100000000000001,null,197,"",3,"Y"]
["Rockingham Data Centre 33kV S Stn","RockinghamDataCentre33kVSStn",926100,0.25,null,408,"",3,"Y"]
["Rolleston Park Solar Farm 33kV S Stn","RollestonParkSolarFarm33kVSStn",874992,0.16,null,255,"",3,"Y"]
["Rookery Lane 33/11kV S Stn","RookeryLane33/11kVSStn",900030,0.13,null,208,"",3,"Y"]
["Rufford 33/11kV S Stn","Rufford33/11kVSStn",890047,0.79200000000000004,null,1052,"",3,"Y"]
["Rugby 132/11kV S Stn","Rugby132/11kVSStn",930064,4.2000000000000003E-2,null,361,"",1,"Y"]
["Rugby 132/33/25/11kV S Stn","Rugby132/33/25/11kVSStn",690017,4.2000000000000003E-2,null,361,"",3,"Y"]
["Rugby 33kV S Stn","Rugby33kVSStn",930006,4.2000000000000003E-2,null,361,"",3,"Y"]
["Rugby Gateway 33/11kV S Stn","RugbyGateway33/11kVSStn",938836,0.25,null,265,"",3,"Y"]
["Rugby Portland Cement 33kV S Stn","RugbyPortlandCement33kVSStn",930021,4.2000000000000003E-2,null,361,"",3,"Y"]
["Rushden 33/11kV S Stn","Rushden33/11kVSStn",920056,0.13800000000000001,null,236,"",3,"Y"]
["Ruskington 33/11kV S Stn","Ruskington33/11kVSStn",910033,0.129,null,235,"",3,"Y"]
["Ruston & Hornsby 33/11kV S Stn","Ruston&Hornsby33/11kVSStn",900031,6.4000000000000001E-2,null,278,"",3,"Y"]
["Ryton 33/11kV S Stn","Ryton33/11kVSStn",930049,5.0999999999999997E-2,null,82,"",3,"Y"]
["Salutation 33/6.6kV S Stn","Salutation33/6.6kVSStn",920037,5.8000000000000003E-2,null,211,"",3,"Y"]
["Sandiacre 33/11kV S Stn","Sandiacre33/11kVSStn",870051,9.8000000000000004E-2,null,190,"",3,"Y"]
["Sandy Lane 33/6.6kV S Stn","SandyLane33/6.6kVSStn",930040,6.4000000000000001E-2,null,100,"",3,"Y"]
["Sapcote 33/11kV S Stn","Sapcote33/11kVSStn",930089,0.13300000000000001,null,254,"",3,"Y"]
["Secklow Gate 33/11kV S Stn","SecklowGate33/11kVSStn",940025,6.3E-2,null,137,"",3,"Y"]
["Shanks Generation 33kV S Stn","ShanksGeneration33kVSStn",940017,0.06,null,68,"",3,"Y"]
["Sharnbrook 33/11kV S Stn","Sharnbrook33/11kVSStn",920057,0.06,null,103,"",3,"Y"]
["Sheepbridge 33/11kV S Stn","Sheepbridge33/11kVSStn",890023,0.112,null,318,"",3,"Y"]
["Sheffield Road 33/11/6.6kV S Stn","SheffieldRoad33/11/6.6kVSStn",890070,0.13500000000000001,null,266,"",3,"Y"]
["Shelton Lodge Solar Generation 33kV S Stn","SheltonLodgeSolarGeneration33kVSStn",883456,0.20300000000000001,null,285,"",3,"Y"]
["Shenley Wood 33/11kV S Stn","ShenleyWood33/11kVSStn",940069,6.4000000000000001E-2,null,124,"",3,"Y"]
["Shepshed 33/11kV S Stn","Shepshed33/11kVSStn",920019,0.08,null,154,"",3,"Y"]
["Sherwood Park 33/11kV S Stn","SherwoodPark33/11kVSStn",890099,0.14099999999999999,null,190,"",3,"Y"]
["Shirebrook 33/11kV S Stn","Shirebrook33/11kVSStn",890034,0.23699999999999999,null,332,"",3,"Y"]
["Sibthorpe 33/11kV S Stn","Sibthorpe33/11kVSStn",880038,0.23,null,414,"",3,"Y"]
["Silverstone 33/11kV S Stn","Silverstone33/11kVSStn",940032,0.19400000000000001,null,198,"",3,"Y"]
["Sinfin C 33kV S Stn","SinfinC33kVSStn",870019,8.1000000000000003E-2,null,148,"",3,"Y"]
["Sinfin Lane 33/11kV S Stn","SinfinLane33/11kVSStn",870041,8.1000000000000003E-2,null,148,"",3,"Y"]
["Skegby Lane 33/11kV S Stn","SkegbyLane33/11kVSStn",890030,7.0000000000000007E-2,null,221,"",3,"Y"]
["Skegness 132/33kV S Stn","Skegness132/33kVSStn",690030,5.0999999999999997E-2,null,192,"",3,"Y"]
["Skegness 33kV S Stn","Skegness33kVSStn",900005,5.0999999999999997E-2,null,192,"",3,"Y"]
["Skillington 33/11kV S Stn","Skillington33/11kVSStn",910040,0.433,null,550,"",3,"Y"]
["Sleaford 132/33kV S Stn","Sleaford132/33kVSStn",690037,0.13700000000000001,null,349,"",3,"Y"]
["Sleaford 33/11kV S Stn","Sleaford33/11kVSStn",910021,0.13700000000000001,null,349,"",3,"Y"]
["Sleaford 33kV S Stn","Sleaford33kVSStn",910008,0.13700000000000001,null,349,"",3,"Y"]
["Sleaford REP 132kV S Stn","SleafordREP132kVSStn",690068,0.2,"Y",1000,"Y",1,"Y"]
["Sleaford Road, Boston 33kV S Stn","SleafordRoad,Boston33kVSStn",900006,0.11,null,330,"",3,"Y"]
["Smith Hall Farm Solar Plant 33kV S Stn","SmithHallFarmSolarPlant33kVSStn",874972,0.28999999999999998,null,235,"",3,"Y"]
["Sneinton 33/11kV S Stn","Sneinton33/11kVSStn",880030,9.1999999999999998E-2,null,141,"",3,"Y"]
["Somercotes 33/11kV S Stn","Somercotes33/11kVSStn",890086,9.2999999999999999E-2,null,147,"",3,"Y"]
["Southam 33/11kV S Stn","Southam33/11kVSStn",930060,0.10199999999999999,null,168,"",3,"Y"]
["South Carlton 33kV S Stn","SouthCarlton33kVSStn",900027,0.129,null,249,"",3,"Y"]
["South Croxton 33/11kV S Stn","SouthCroxton33/11kVSStn",920041,0.183,null,207,"",3,"Y"]
["South Holland 132/33kV S Stn","SouthHolland132/33kVSStn",690040,3.9E-2,null,359,"",3,"Y"]
["South Holland 33kV S Stn","SouthHolland33kVSStn",910010,3.9E-2,null,359,"",3,"Y"]
["Southwell 33/11kV S Stn","Southwell33/11kVSStn",890059,0.153,null,289,"",3,"Y"]
["Spalding 132/33kV S Stn","Spalding132/33kVSStn",690036,3.4000000000000002E-2,null,147,"",3,"Y"]
["Spalding Clay Lake 33/11kV S Stn","SpaldingClayLake33/11kVSStn",910028,3.4000000000000002E-2,null,145,"",3,"Y"]
["Spalding Clay Lake 33kV S Stn","SpaldingClayLake33kVSStn",910009,3.4000000000000002E-2,null,145,"",3,"Y"]
["Spalding Park Road 33/11kV S Stn","SpaldingParkRoad33/11kVSStn",910023,0.06,null,90,"",3,"Y"]
["Spilsby 33kV S Stn","Spilsby33kVSStn",900016,0.20300000000000001,null,357,"",3,"Y"]
["Spondon 33/11kV S Stn","Spondon33/11kVSStn",870046,7.1999999999999995E-2,null,984,"",3,"Y"]
["Spondon 33kV S Stn","Spondon33kVSStn",870006,7.1999999999999995E-2,null,984,"",3,"Y"]
["Spondon A 132kV S Stn","SpondonA132kVSStn",680030,0.2,"Y",1000,"Y",1,"Y"]
["Spondon 'B' 132/33kV S Stn","Spondon'B'132/33kVSStn",680031,0.2,"Y",1000,"Y",3,"Y"]
["Spon Street 33/6.6kV S Stn","SponStreet33/6.6kVSStn",930041,0.1,null,200,"",3,"Y"]
["Stamford 132/33kV S Stn","Stamford132/33kVSStn",690035,5.6000000000000001E-2,null,222,"",3,"Y"]
["Stamford 33/11kV S Stn","Stamford33/11kVSStn",910050,5.6000000000000001E-2,null,222,"",3,"Y"]
["Stamford 33kV S Stn","Stamford33kVSStn",910004,5.6000000000000001E-2,null,222,"",3,"Y"]
["St Anns 33/11kV S Stn","StAnns33/11kVSStn",880040,0.218,null,294,"",3,"Y"]
["Stanton 132/33kV S Stn","Stanton132/33kVSStn",680042,7.3200000000000001E-2,null,457,"",3,"Y"]
["Stanton 33kV S Stn","Stanton33kVSStn",870011,7.3200000000000001E-2,null,457,"",3,"Y"]
["Station Street 33/11kV S Stn","StationStreet33/11kVSStn",870032,0.26,null,248,"",3,"Y"]
["Staveley 132/33kV S Stn","Staveley132/33kVSStn",680039,4.8599999999999997E-2,null,372,"",3,"Y"]
["Staveley 33/11kV S Stn","Staveley33/11kVSStn",890080,4.8599999999999997E-2,null,372,"",3,"Y"]
["Staveley 33kV S Stn","Staveley33kVSStn",890015,4.8599999999999997E-2,null,372,"",3,"Y"]
["Staveley Works 33kV S Stn","StaveleyWorks33kVSStn",890098,6.3E-2,null,156,"",3,"Y"]
["Staythorpe B 132kV S Stn","StaythorpeB132kVSStn",680020,0.2,"Y",1000,"Y",1,"Y"]
["Staythorpe C 400/132kV S Stn","StaythorpeC400/132kVSStn",680001,0.2,"Y",2800,"Y",1,"Y"]
["Stickney 33kV S Stn","Stickney33kVSStn",900020,0.27200000000000002,null,310,"",3,"Y"]
["Stoke Bardolph 400/132kV S Stn","StokeBardolph400/132kVSStn",680068,0.2,"Y",2800,"Y",1,"Y"]
["Stoneygate 33/6.6kV S Stn","Stoneygate33/6.6kVSStn",920038,6.9000000000000006E-2,null,111,"",3,"Y"]
["Stonish Hill Windfarm 33kV S Stn","StonishHillWindfarm33kVSStn",898181,0.14000000000000001,null,278,"",3,"Y"]
["Stony Stratford 132/33kV S Stn","StonyStratford132/33kVSStn",690045,9.1999999999999998E-2,null,1074,"",3,"Y"]
["Stony Stratford 33kV S Stn","StonyStratford33kVSStn",940005,9.1999999999999998E-2,null,1074,"",3,"Y"]
["Stragglethorpe Road Pv Solar Park 33kv S Stn","StragglethorpeRoadPvSolarPark33kvSStn",883465,0.128,null,236,"",3,"Y"]
["Sutton Junction 33/11kV S Stn","SuttonJunction33/11kVSStn",890031,0.10100000000000001,null,225,"",3,"Y"]
["Swinderby 33/11kV S Stn","Swinderby33/11kVSStn",900025,0.27200000000000002,null,266,"",3,"Y"]
["Swinford Windfarm 33kV S Stn","SwinfordWindfarm33kVSStn",939003,0.192,null,536,"",3,"Y"]
["Syston 33/11kV S Stn","Syston33/11kVSStn",920035,6.5000000000000002E-2,null,70,"",3,"Y"]
["Sywell PV 33kV S Stn","SywellPV33kVSStn",926308,0.193,null,122,"",3,"Y"]
["Talbot Street 33/11kV S Stn","TalbotStreet33/11kVSStn",880022,0.13500000000000001,null,204,"",3,"Y"]
["Tamworth 132/33kV S Stn","Tamworth132/33kVSStn",690016,4.7E-2,null,301,"",3,"Y"]
["Tamworth 33kV S Stn","Tamworth33kVSStn",930010,4.7E-2,null,301,"",3,"Y"]
["Tamworth Br 132/25kV S Stn","TamworthBr132/25kVSStn",930015,9.2999999999999999E-2,null,579,"",1,"Y"]
["Tamworth Grid 33/11kV S Stn","TamworthGrid33/11kVSStn",930071,4.7E-2,null,301,"",3,"Y"]
["Tamworth Town 132/11kV S Stn","TamworthTown132/11kVSStn",930070,3.4000000000000002E-2,null,217,"",1,"Y"]
["Tamworth Town 132/33/11kV S Stn","TamworthTown132/33/11kVSStn",690011,3.4000000000000002E-2,null,217,"",3,"Y"]
["Tamworth Town 33kV S Stn","TamworthTown33kVSStn",930005,3.4000000000000002E-2,null,217,"",3,"Y"]
["Tattenhoe 33/11kV S Stn","Tattenhoe33/11kVSStn",946268,0.13,null,420,"",3,"Y"]
["Tattershall 33/11kV S Stn","Tattershall33/11kVSStn",900039,0.09,null,180,"",3,"Y"]
["Taylor Lane STOR 33kV S Stn","TaylorLaneSTOR33kVSStn",875141,2,null,522,"",3,"Y"]
["Teversal 33/11kV S Stn","Teversal33/11kVSStn",890029,0.105,null,205,"",3,"Y"]
["The Brek Solar 33kv S Stn","TheBrekSolar33kvSStn",898460,0.14199999999999999,null,404,"",3,"Y"]
["The Grange Windfarm 33kV S Stn","TheGrangeWindfarm33kVSStn",917515,5.1999999999999998E-2,null,81,"",3,"Y"]
["The Hollies Wind Farm 33kV S Stn","TheHolliesWindFarm33kVSStn",900010,7.0000000000000007E-2,null,165,"",3,"Y"]
["Thenford 33/11kV S Stn","Thenford33/11kVSStn",940026,0.59,null,965,"",3,"Y"]
["The Ridge Solar Park 33kV S Stn","TheRidgeSolarPark33kVSStn",926142,8.6999999999999994E-2,null,235,"",3,"Y"]
["Thoresby 33/11kV S Stn","Thoresby33/11kVSStn",890048,0.31,null,2814,"",3,"Y"]
["Thoresby Solar Farm 33kV S Stn","ThoresbySolarFarm33kVSStn",898350,0.24,null,432,"",3,"Y"]
["Thornborough Grounds Pv 33kv S Stn","ThornboroughGroundsPv33kvSStn",946271,0.20699999999999999,null,261,"",3,"Y"]
["Thrapston 33/11kV S Stn","Thrapston33/11kVSStn",920059,0.22,null,420,"",3,"Y"]
["Thurmaston 33/11kV S Stn","Thurmaston33/11kVSStn",920034,5.6000000000000001E-2,null,110,"",3,"Y"]
["Thurnby 33/11kV S Stn","Thurnby33/11kVSStn",920042,5.1999999999999998E-2,null,140,"",3,"Y"]
["Tiln Farm Solar Generation 33kV S Stn","TilnFarmSolarGeneration33kVSStn",898347,0.19,null,246,"",3,"Y"]
["Tinwell Road 33/11kV S Stn","TinwellRoad33/11kVSStn",910054,0.17299999999999999,null,268,"",3,"Y"]
["Torrington Avenue 33/11kV S Stn","TorringtonAvenue33/11kVSStn",930030,8.4000000000000005E-2,null,219,"",3,"Y"]
["Toton 132/33kV S Stn","Toton132/33kVSStn",680019,9.6000000000000002E-2,null,567,"",3,"Y"]
["Toton 33/11kV S Stn","Toton33/11kVSStn",880009,9.6000000000000002E-2,null,567,"",3,"Y"]
["Toton 33kV S Stn","Toton33kVSStn",880004,9.6000000000000002E-2,null,567,"",3,"Y"]
["Tournament Fields 33/11kV S Stn","TournamentFields33/11kVSStn",930087,0.95,null,441,"",3,"Y"]
["Towcester 33/11kV S Stn","Towcester33/11kVSStn",940031,6.9000000000000006E-2,null,98,"",3,"Y"]
["Trafalgar Park Gas Peaking S15 33kV S Stn","TrafalgarParkGasPeakingS1533kVSStn",875086,0.23,null,406,"",3,"Y"]
["Trent Alloys 33/11kV S Stn","TrentAlloys33/11kVSStn",870035,0.17399999999999999,null,216,"",3,"Y"]
["Trent Lane 33/11kV S Stn","TrentLane33/11kVSStn",870014,0.22600000000000001,null,339,"",3,"Y"]
["Trusthorpe 33/11kV S Stn","Trusthorpe33/11kVSStn",900012,0.115,null,230,"",3,"Y"]
["Tunnel Bank 33/11kV S Stn","TunnelBank33/11kVSStn",910042,0.17,null,340,"",3,"Y"]
["Turweston Airfield Solar Farm 33kV S Stn","TurwestonAirfieldSolarFarm33kVSStn",945726,0.1,null,126,"",3,"Y"]
["Tuxford 33/11kV S Stn","Tuxford33/11kVSStn",890058,0.23400000000000001,null,185,"",3,"Y"]
["Twin Oaks STOR 33kV S Stn","TwinOaksSTOR33kVSStn",875166,0.56999999999999995,null,816,"",3,"Y"]
["Twin Yards Solar Farm 33kV S Stn","TwinYardsSolarFarm33kVSStn",898482,0.23,null,283,"",3,"Y"]
["Union Street 33/11kV S Stn","UnionStreet33/11kVSStn",930065,5.2999999999999999E-2,null,80,"",3,"Y"]
["University Of Warwick 33/11kV S Stn","UniversityOfWarwick33/11kVSStn",930034,0.04,null,270,"",3,"Y"]
["Uppingham 33/11kV S Stn","Uppingham33/11kVSStn",910057,0.24399999999999999,null,435,"",3,"Y"]
["Uttoxeter 132/33kV S Stn","Uttoxeter132/33kVSStn",680043,0.156,null,569,"",3,"Y"]
["Uttoxeter 33kV S Stn","Uttoxeter33kVSStn",870009,0.156,null,569,"",3,"Y"]
["Victoria Road 33/11kV S Stn","VictoriaRoad33/11kVSStn",940044,8.3000000000000004E-2,null,125,"",3,"Y"]
["Victoria Road PV Ellistown 33kV S Stn","VictoriaRoadPVEllistown33kVSStn",939300,7.2999999999999995E-2,null,238,"",3,"Y"]
["Waddington 33/11kV S Stn","Waddington33/11kVSStn",900033,0.13300000000000001,null,219,"",3,"Y"]
["Walkers Wood Solar Farm 33kV S Stn","WalkersWoodSolarFarm33kVSStn",898357,0.35,null,581,"",3,"Y"]
["Walpole 400/132kV S Stn","Walpole400/132kVSStn",690005,0.2,"Y",2800,"Y",1,"Y"]
["Walsgrave 33/11kV S Stn","Walsgrave33/11kVSStn",930047,0.16,null,128,"",3,"Y"]
["Walton 33/11kV S Stn","Walton33/11kVSStn",890078,0.16300000000000001,null,199,"",3,"Y"]
["Wardentree Park 33/11kV S Stn","WardentreePark33/11kVSStn",910017,0.18,null,266,"",3,"Y"]
["Warsop 33/11kV S Stn","Warsop33/11kVSStn",890046,0.25600000000000001,null,536,"",3,"Y"]
["Warth Lane 33/11kV S Stn","WarthLane33/11kVSStn",900018,0.12,null,360,"",3,"Y"]
["Warwick 132/33/11kV S Stn","Warwick132/33/11kVSStn",690020,4.1000000000000002E-2,null,274,"",3,"Y"]
["Warwick 33kV S Stn","Warwick33kVSStn",930007,4.1000000000000002E-2,null,274,"",3,"Y"]
["Warwick Grid 132/11kV S Stn","WarwickGrid132/11kVSStn",690059,4.1000000000000002E-2,null,274,"",1,"Y"]
["Watford Lodge Windfarm 33kV S Stn","WatfordLodgeWindfarm33kVSStn",945977,0.13,null,250,"",3,"Y"]
["Watnall Primary 33/11kV S Stn","WatnallPrimary33/11kVSStn",883362,1.04,null,592,"",3,"Y"]
["Wavendon Gate 33/11kV S Stn","WavendonGate33/11kVSStn",940046,0.04,null,78,"",3,"Y"]
["Weedon 33/11kV S Stn","Weedon33/11kVSStn",940050,0.10100000000000001,null,164,"",3,"Y"]
["Welbeck Colliery Solar Generation 33kV S Stn","WelbeckCollierySolarGeneration33kVSStn",898308,0.15,null,420,"",3,"Y"]
["Welbeck Solar Farm 33kV S Stn","WelbeckSolarFarm33kVSStn",898344,0.41,null,712,"",3,"Y"]
["Weldon Shanks Generation 33kV S Stn","WeldonShanksGeneration33kVSStn",920011,0.74,null,1110,"",3,"Y"]
["Wellesbourne 33/11kV S Stn","Wellesbourne33/11kVSStn",939424,0.2,null,421,"",3,"Y"]
["Wellingborough 132/11kV S Stn","Wellingborough132/11kVSStn",920016,4.4999999999999998E-2,null,217,"",1,"Y"]
["Wellingborough 132/33kV S Stn","Wellingborough132/33kVSStn",690051,4.4999999999999998E-2,null,217,"",3,"Y"]
["Wellingborough 33kV S Stn","Wellingborough33kVSStn",940011,4.4999999999999998E-2,null,217,"",3,"Y"]
["Wellingborough Road 33/11kV S Stn","WellingboroughRoad33/11kVSStn",940064,0.05,null,970,"",3,"Y"]
["Wellington Street 33/11kV S Stn","WellingtonStreet33/11kVSStn",870029,8.5000000000000006E-2,null,172,"",3,"Y"]
["Welton 33/11kV S Stn","Welton33/11kVSStn",940048,0.13100000000000001,null,262,"",3,"Y"]
["Wessington 33/11kV S Stn","Wessington33/11kVSStn",890087,0.219,null,350,"",3,"Y"]
["Westborough 33/11kV S Stn","Westborough33/11kVSStn",910037,0.29699999999999999,null,425,"",3,"Y"]
["West Bridgford 33/11kV S Stn","WestBridgford33/11kVSStn",880028,7.8E-2,null,118,"",3,"Y"]
["West Burton 400/132kV S Stn","WestBurton400/132kVSStn",890003,3.7199999999999997E-2,null,599,"",1,"Y"]
["West Deeping 33/11kV S Stn","WestDeeping33/11kVSStn",910046,0.41499999999999998,null,872,"",3,"Y"]
["West End Farm Solar Generation 33kV S Stn","WestEndFarmSolarGeneration33kVSStn",898435,0.2,null,235,"",3,"Y"]
["West Haddon 33/11kV S Stn","WestHaddon33/11kVSStn",940051,0.33200000000000002,null,637,"",3,"Y"]
["Westhorpe 33/11kV S Stn","Westhorpe33/11kVSStn",890091,6.5000000000000002E-2,null,205,"",3,"Y"]
["Westwood 33/11kV S Stn","Westwood33/11kVSStn",890028,0.219,null,314,"",3,"Y"]
["Whaplode Drove 33/11kV S Stn","WhaplodeDrove33/11kVSStn",910030,0.27800000000000002,null,325,"",3,"Y"]
["Whetstone 33/11kV S Stn","Whetstone33/11kVSStn",930096,7.1999999999999995E-2,null,142,"",3,"Y"]
["Whitecross Lane Solar Park Burton Pedwardine 33kV S Stn","WhitecrossLaneSolarParkBurtonPedwardine33kVSStn",906124,0.7,"Y",500,"Y",3,"Y"]
["Whitley 132/33kV S Stn","Whitley132/33kVSStn",930016,7.0000000000000007E-2,null,357,"",3,"Y"]
["Whitley 33/11kV S Stn","Whitley33/11kVSStn",930045,7.0000000000000007E-2,null,357,"",3,"Y"]
["Whitley 33kV S Stn","Whitley33kVSStn",930008,7.0000000000000007E-2,null,574,"",3,"Y"]
["Whittlebury Road PV 33kV S Stn","WhittleburyRoadPV33kVSStn",946060,6.3E-2,null,56,"",3,"Y"]
["Whittleford 33/11kV S Stn","Whittleford33/11kVSStn",930074,8.2000000000000003E-2,null,162,"",3,"Y"]
["Whitwell 132/33kV S Stn","Whitwell132/33kVSStn",680016,0.42699999999999999,null,1320,"",3,"Y"]
["Whitwell 33kV S Stn","Whitwell33kVSStn",890009,0.42699999999999999,null,1320,"",3,"Y"]
["Wicken 33/11kV S Stn","Wicken33/11kVSStn",940033,0.45,null,878,"",3,"Y"]
["Wide Lane Wymeswold Solar Farm 33kV S Stn","WideLaneWymeswoldSolarFarm33kVSStn",926300,7.2999999999999995E-2,null,164,"",3,"Y"]
["Wigston 132/11kV S Stn","Wigston132/11kVSStn",920039,6.0999999999999999E-2,null,393,"",1,"Y"]
["Wigston 132/33/11kV S Stn","Wigston132/33/11kVSStn",690027,0.2,"Y",393,"",3,"Y"]
["Wigston 33kV S Stn","Wigston33kVSStn",920005,6.0999999999999999E-2,null,393,"",3,"Y"]
["Wigston Magna 33/11kV S Stn","WigstonMagna33/11kVSStn",920017,7.9000000000000001E-2,null,34,"",3,"Y"]
["Willesley 33/11kV S Stn","Willesley33/11kVSStn",690060,0.23200000000000001,null,220,"",3,"Y"]
["Willington 400/275/132kV S Stn","Willington400/275/132kVSStn",680006,0.2,"Y",2800,"Y",1,"Y"]
["Willoughby 132/33kV S Stn","Willoughby132/33kVSStn",680014,7.9000000000000001E-2,null,329,"",3,"Y"]
["Willoughby 33/11kV S Stn","Willoughby33/11kVSStn",880032,7.9000000000000001E-2,null,329,"",3,"Y"]
["Willoughby 33kV S Stn","Willoughby33kVSStn",880006,7.9000000000000001E-2,null,329,"",3,"Y"]
["Willoughby STOR 33kV S Stn","WilloughbySTOR33kVSStn",883330,7.9000000000000001E-2,null,500,"Y",3,"Y"]
["Wingerworth 33/11kV S Stn","Wingerworth33/11kVSStn",890072,4.2999999999999997E-2,null,117,"",3,"Y"]
["Winslow 33/11kV S Stn","Winslow33/11kVSStn",940035,8.3000000000000004E-2,null,160,"",3,"Y"]
["Winster 132/33kV S Stn","Winster132/33kVSStn",680040,0.2,"Y",565,"",3,"Y"]
["Winster 33kV S Stn","Winster33kVSStn",890013,0.17899999999999999,null,565,"",3,"Y"]
["Winwick Windfarm 33kV S Stn","WinwickWindfarm33kVSStn",945978,0.13,null,145,"",3,"Y"]
["Wise Street 33/11kV S Stn","WiseStreet33/11kVSStn",930054,0.05,null,73,"",3,"Y"]
["Wittering 33/11kV S Stn","Wittering33/11kVSStn",910053,0.08,null,98,"",3,"Y"]
["Wollaton Road 33/11kV S Stn","WollatonRoad33/11kVSStn",880020,6.5000000000000002E-2,null,130,"",3,"Y"]
["Wolverton 132/25kV S Stn","Wolverton132/25kVSStn",940015,0.2,"Y",1000,"Y",1,"Y"]
["Wolverton 33/11kV S Stn","Wolverton33/11kVSStn",940036,6.8000000000000005E-2,null,351,"",3,"Y"]
["Woodbeck 33/11kV S Stn","Woodbeck33/11kVSStn",890062,0.499,null,528,"",3,"Y"]
["Wood End 33/11kV S Stn","WoodEnd33/11kVSStn",930073,0.16500000000000001,null,383,"",3,"Y"]
["Woodford Halse 33/11kV S Stn","WoodfordHalse33/11kVSStn",940027,8.5999999999999993E-2,null,157,"",3,"Y"]
["Woodhall Spa 33/11kV S Stn","WoodhallSpa33/11kVSStn",900038,0.219,null,799,"",3,"Y"]
["Wood Lane 33/11kV S Stn","WoodLane33/11kVSStn",939062,0.2,null,226,"",3,"Y"]
["Woodville 33/11kV S Stn","Woodville33/11kVSStn",870037,0.28199999999999997,null,333,"",3,"Y"]
["Wootton 33/11kV S Stn","Wootton33/11kVSStn",940062,0.14000000000000001,null,140,"",3,"Y"]
["Worksop 132/33kV S Stn","Worksop132/33kVSStn",680017,0.14399999999999999,null,586,"",3,"Y"]
["Worksop 33kV S Stn","Worksop33kVSStn",890011,0.14399999999999999,null,586,"",3,"Y"]
["Worksop West 33/11kV S Stn","WorksopWest33/11kVSStn",890038,0.157,null,308,"",3,"Y"]
["Worthington 33/11kV S Stn","Worthington33/11kVSStn",930104,0.253,null,314,"",3,"Y"]
["Wragby 33/11kV S Stn","Wragby33/11kVSStn",900036,6.7000000000000004E-2,null,122,"",3,"Y"]
["Wrangle 33/11kV S Stn","Wrangle33/11kVSStn",900019,0.17299999999999999,null,322,"",3,"Y"]
["Wymeswold Airfield PV Farm 33kV S Stn","WymeswoldAirfieldPVFarm33kVSStn",926096,0.1,null,148,"",3,"Y"]
["Wymington Wykes Generation 33kV S Stn","WymingtonWykesGeneration33kVSStn",920010,4.8000000000000001E-2,null,78,"",3,"Y"]
["Yelvertoft Windfarm 33kV S Stn","YelvertoftWindfarm33kVSStn",946091,0.2,null,135,"",3,"Y"]

{"sheet":"Source-WM-Num","index":20,"n_rows":305,"n_cols":8,"rows_kept":305,"cut":false,"hidden":true,"merged":[]}
[1,2,3,4,5,6,7,8]
["SUBSTATION_NUMBER_WM","SUBSTATION_NAME","ZE","Assumed ZE","UE","Assumed UE","t","Assumed t"]
[670001,"Iron Acton 275/132kV S Stn",0.09,null,1503,"",1,"Y"]
[670002,"Bishops Wood 275/132kV S Stn",0.17,null,3145,"",1,"Y"]
[670003,"Feckenham 275/66/11kV S Stn",7.2999999999999995E-2,null,1030,"",3,"Y"]
[670004,"Bustleholm 275/132/11kV S Stn",0.1,null,990,"",1,"Y"]
[670005,"Oldbury 132/11kV S Stn",7.5999999999999998E-2,null,965,"",1,"Y"]
[670006,"Willenhall 275/132/33/25/11kV S Stn",7.0000000000000007E-2,null,211,"",3,"Y"]
[670007,"Nechells East 275/132kV S Stn",7.0000000000000007E-2,null,1540,"",1,"Y"]
[670008,"Port Ham 400/132kV S Stn",0.63,null,561,"",1,"Y"]
[670009,"Penn 400/275/132kV S Stn",9.7000000000000003E-2,null,1242,"",1,"Y"]
[670010,"Ocker Hill C 275/132kV S Stn",7.0000000000000007E-2,null,1266,"",1,"Y"]
[670011,"Kitwell 275/132kV S Stn",0.126,null,2528,"",1,"Y"]
[670012,"Castle Meads 132/33kV S Stn",7.3999999999999996E-2,null,1037,"",3,"Y"]
[670013,"Hereford 132/66kV S Stn",0.129,null,647,"",3,"Y"]
[670014,"Worcester 132/11kV S Stn",9.5000000000000001E-2,null,486,"",1,"Y"]
[670015,"Ryeford 132/33/11kV S Stn",5.6000000000000001E-2,null,209,"",3,"Y"]
[670016,"Walsall 132/33kV S Stn",0.13600000000000001,null,352,"",3,"Y"]
[670017,"Bushbury A 132kV S Stn",8.8999999999999996E-2,null,1664,"",1,"Y"]
[670019,"Timberdine 132/11kV S Stn",0.08,null,515,"",1,"Y"]
[670020,"Tividale 132/11kV S Stn",0.11799999999999999,null,900,"",1,"Y"]
[670021,"Upton Warren 132/66/11kV S Stn",0.104,null,374,"",3,"Y"]
[670022,"Warndon 132/11kV S Stn",4.3999999999999997E-2,null,290,"",1,"Y"]
[670023,"Wednesfield 132/11kV S Stn",0.14699999999999999,null,1102,"",1,"Y"]
[670024,"Wolverhampton 132/33/11kV S Stn",0.114,null,376,"",3,"Y"]
[670025,"Wolverhampton West 132/33/11kV S Stn",0.13300000000000001,null,1157,"",3,"Y"]
[670026,"Woodside 132/11kV S Stn",7.0999999999999994E-2,null,333,"",1,"Y"]
[670027,"Summer Lane 132/11kV S Stn",0.08,null,240,"",1,"Y"]
[670028,"Hall Green 132/11kV S Stn",7.5999999999999998E-2,null,516,"",1,"Y"]
[670029,"Dunlop 132kV S Stn",0.23799999999999999,null,2222,"",1,"Y"]
[670030,"Kitts Green 132/11kV S Stn",0.125,null,635,"",1,"Y"]
[670031,"Lydney Local 132kV S Stn",0.21,null,712,"",1,"Y"]
[670032,"Castle Bromwich 132/11kV S Stn",8.6999999999999994E-2,null,383,"",1,"Y"]
[670033,"Hams Hall 132/33kV S Stn",0.105,null,1775,"",3,"Y"]
[670034,"Erdington 132kV S Stn",0.121,null,581,"",1,"Y"]
[670035,"University Of Birmingham 132/11kV S Stn",2.9000000000000001E-2,null,275,"",1,"Y"]
[670037,"Bushbury B-C 132/33/11kV S Stn",0.12,null,2077,"",3,"Y"]
[670038,"Winson Green 132/11kV S Stn",0.05,null,279,"",1,"Y"]
[670039,"Selly Oak 132kV S Stn",8.5999999999999993E-2,null,791,"",1,"Y"]
[670040,"Ladywood 132/11kV S Stn",0.17299999999999999,null,1358,"",1,"Y"]
[670041,"Bordesley 132/11kV S Stn",9.7000000000000003E-2,null,286,"",1,"Y"]
[670042,"Chipping Sodbury 132/33/11kV S Stn",0.28000000000000003,null,974,"",3,"Y"]
[670043,"Hams Hall South 132/11kV S Stn",0.08,null,1115,"",1,"Y"]
[670045,"Banbury 132/11kV S Stn",6.6000000000000003E-2,null,211,"",1,"Y"]
[670046,"Bentley 132/11kV S Stn",8.8999999999999996E-2,null,694,"",1,"Y"]
[670047,"Birchfield Lane 132/11kV S Stn",5.0999999999999997E-2,null,418,"",1,"Y"]
[670048,"Black Lake 132/11kV S Stn",7.1999999999999995E-2,null,532,"",1,"Y"]
[670049,"Longbridge 132/11kV S Stn",0.04,null,449,"",1,"Y"]
[670050,"Bournville 132/11kV S Stn",6.8000000000000005E-2,null,474,"",1,"Y"]
[670051,"Chad Valley 132/11kV S Stn",0.08,null,336,"",1,"Y"]
[670052,"Cheapside 132/11kV S Stn",7.3999999999999996E-2,null,610,"",1,"Y"]
[670053,"Cheltenham 132/66/11kV S Stn",5.1999999999999998E-2,null,201,"",3,"Y"]
[670054,"Chester Street 132/11kV S Stn",0.38400000000000001,null,614,"",1,"Y"]
[670055,"Copt Heath 132/11kV S Stn",0.115,null,566,"",1,"Y"]
[670056,"Coseley 132/11kV S Stn",0.10100000000000001,null,760,"",1,"Y"]
[670057,"Dudley 132/11kV S Stn",5.3999999999999999E-2,null,437,"",1,"Y"]
[670058,"Eastern Avenue 132/11kV S Stn",3.9E-2,null,416,"",1,"Y"]
[670059,"Elmdon 132/11kV S Stn",0.06,null,424,"",1,"Y"]
[670060,"Halesowen 132/11kV S Stn",8.5000000000000006E-2,null,909,"",1,"Y"]
[670061,"Highters Heath 132/11kV S Stn",6.5000000000000002E-2,null,469,"",1,"Y"]
[670062,"Hinksford 132/33/11kV S Stn",0.12,null,1079,"",3,"Y"]
[670063,"Kidderminster 132/33/11kV S Stn",0.24,null,1546,"",3,"Y"]
[670064,"Ludlow 132/66/33/11kV S Stn",0.15,null,599,"",3,"Y"]
[670065,"Lye 132/11kV S Stn",4.2999999999999997E-2,null,430,"",1,"Y"]
[670066,"Marle Hill 132/66/11kV S Stn",3.5000000000000003E-2,null,160,"",3,"Y"]
[670067,"Malvern 132/11kV S Stn",4.8000000000000001E-2,null,319,"",1,"Y"]
[670068,"Montpellier 132/11kV S Stn",4.3999999999999997E-2,null,216,"",1,"Y"]
[670069,"Nechells West 132/25/11kV S Stn",0.11,null,583,"",1,"Y"]
[670070,"Ocker Hill B 132/33/11kV S Stn",5.1999999999999998E-2,null,854,"",3,"Y"]
[670071,"Perry Barr 132/11kV S Stn",0.112,null,445,"",1,"Y"]
[670072,"Rednal 132/11kV S Stn",6.4000000000000001E-2,null,620,"",1,"Y"]
[670073,"Rushall 132/11kV S Stn",0.16,null,498,"",1,"Y"]
[670074,"Selly Oak 132/11kV S Stn",8.5999999999999993E-2,null,791,"",1,"Y"]
[670075,"Shirley 132/11kV S Stn",6.5000000000000002E-2,null,449,"",1,"Y"]
[670076,"Smethwick 132/11kV S Stn",0.153,null,1121,"",1,"Y"]
[670077,"Solihull 132/11kV S Stn",0.09,null,252,"",1,"Y"]
[670078,"Sparkbrook 132/11kV S Stn",0.04,null,274,"",1,"Y"]
[670079,"Stourport 132/66/33/11kV S Stn",0.112,null,618,"",3,"Y"]
[670080,"Sutton Coldfield 132/11kV S Stn",9.6000000000000002E-2,null,703,"",1,"Y"]
[670081,"Tewkesbury 132/11kV S Stn",5.7000000000000002E-2,null,337,"",1,"Y"]
[670083,"Tewkesbury 66/11kV S Stn",6.4000000000000001E-2,null,532,"",3,"Y"]
[670084,"Abson 33kV S Stn",0.25900000000000001,null,328,"",3,"Y"]
[670085,"Moreton 66/11kV S Stn",0.114,null,191,"",3,"Y"]
[670086,"Bishops Cleeve 66/11kV S Stn",0.115,null,163,"",3,"Y"]
[670087,"Bloxham 66/11kV S Stn",0.31,null,504,"",3,"Y"]
[670088,"Alderton 66/11kV S Stn",0.13,null,179,"",3,"Y"]
[670089,"Broadway 66/11kV S Stn",0.37,null,701,"",3,"Y"]
[670090,"Epwell 66/11kV S Stn",0.34,null,308,"",3,"Y"]
[670091,"Stow 66/11kV S Stn",1.66,null,2296,"",3,"Y"]
[670092,"Wormington 66/11kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[670093,"Shipston 66/11kV S Stn",0.14799999999999999,null,202,"",3,"Y"]
[670094,"Long Marston 66/11kV S Stn",0.10100000000000001,null,128,"",3,"Y"]
[670095,"Pershore 66/11kV S Stn",0.17100000000000001,null,324,"",3,"Y"]
[670096,"Hereford North 66/11kV S Stn",9.6000000000000002E-2,null,141,"",3,"Y"]
[670097,"Evesham 66/11kV S Stn",0.14499999999999999,null,399,"",3,"Y"]
[670098,"Bevington 66/11kV S Stn",0.154,null,248,"",3,"Y"]
[670099,"Peterchurch 66/11kV S Stn",0.22,null,303,"",3,"Y"]
[670100,"Leominster 66/11kV S Stn",0.253,null,441,"",3,"Y"]
[670101,"Stratford 66/11kV S Stn",0.12,null,304,"",3,"Y"]
[670102,"Brotheridge Green 66/11kV S Stn",0.41,null,614,"",3,"Y"]
[670103,"Hereford South 66/11kV S Stn",0.16600000000000001,null,266,"",3,"Y"]
[670104,"Strensham 66/11kV S Stn",0.20200000000000001,null,352,"",3,"Y"]
[670105,"Great Alne 66/11kV S Stn",0.159,null,348,"",3,"Y"]
[670106,"Pontrilas 66/11kV S Stn",0.2,null,380,"",3,"Y"]
[670107,"Arley 33kV S Stn",1.79,null,1545,"",3,"Y"]
[670108,"Bromyard 66/11kV S Stn",0.223,null,386,"",3,"Y"]
[670109,"Madley 66/11kV S Stn",0.28999999999999998,null,592,"",3,"Y"]
[670110,"Woofferton 66/11kV S Stn",0.14000000000000001,null,211,"",3,"Y"]
[670111,"Presteigne 66/11kV S Stn",0.44,null,722,"",3,"Y"]
[670112,"Bodenham 66/11kV S Stn",0.46,null,1334,"",3,"Y"]
[670113,"St Weonards 66/11kV S Stn",0.38400000000000001,null,472,"",3,"Y"]
[670114,"Kington 66/11kV S Stn",0.38500000000000001,null,454,"",3,"Y"]
[670115,"Droitwich 66/11kV S Stn",9.8000000000000004E-2,null,141,"",3,"Y"]
[670116,"Kenswick 66/11kV S Stn",0.48699999999999999,null,360,"",3,"Y"]
[670117,"Lower Chadnor 66/11kV S Stn",0.35499999999999998,null,383,"",3,"Y"]
[670118,"Redditch South 66/11kV S Stn",7.3999999999999996E-2,null,221,"",3,"Y"]
[670119,"Redditch North 66/11kV S Stn",0.122,null,232,"",3,"Y"]
[670120,"Ipsley 66/11kV S Stn",6.8000000000000005E-2,null,146,"",3,"Y"]
[670121,"Knighton 66/11kV S Stn",0.97299999999999998,null,973,"",3,"Y"]
[670122,"Albrighton 33/11kV S Stn",0.16,null,200,"",3,"Y"]
[670124,"Four Ashes 33/11kV S Stn",0.189,null,230,"",3,"Y"]
[670125,"Aldridge 33/6.6kV S Stn",6.2E-2,null,133,"",3,"Y"]
[670126,"Ross 66/11kV S Stn",0.1,null,139,"",3,"Y"]
[670128,"Kingstanding 132/11kV S Stn",0.23,null,265,"",1,"Y"]
[670129,"Ledbury 66/11kV S Stn",9.6000000000000002E-2,null,294,"",3,"Y"]
[670131,"Chelmsley Wood 33/11kV S Stn",3.6999999999999998E-2,null,37,"",3,"Y"]
[670133,"Newent 66/11kV S Stn",0.3,null,851,"",3,"Y"]
[670136,"Erdington 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[670137,"Boughton Rd 132/11kV S Stn",4.3999999999999997E-2,null,498,"",1,"Y"]
[670138,"Bartley Green 132/11kV S Stn",9.2999999999999999E-2,null,1038,"",1,"Y"]
[670139,"Bustleholm 132/11kV S Stn",0.1,null,990,"",1,"Y"]
[670140,"Chelmsley Wood 132/11kV S Stn",2.9000000000000001E-2,null,609,"",1,"Y"]
[670141,"Four Ashes E F W 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[670142,"Pattingham 33/11kV S Stn",0.12,null,205,"",3,"Y"]
[670143,"Dymock 66/11kV S Stn",0.314,null,891,"",3,"Y"]
[670148,"Barton Abrasives 33/11kV S Stn",0.151,null,831,"",3,"Y"]
[670150,"Wolverhampton Waste Services 33kv S Stn",0.7,"Y",500,"Y",3,"Y"]
[670151,"Hereford Central 66/11kv S Stn",0.156,null,279,"",3,"Y"]
[670152,"Wickhamford 66kv S Stn",0.124,null,214,"",3,"Y"]
[670153,"Garreg Lwyd Wind Farm 66kV S Stn",2.2200000000000002,null,2743,"",3,"Y"]
[670154,"Oldbury B 132/33/11kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
[670161,"Air Liquide 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[670170,"Troughton Farm 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[670200,"Hockley 132/11kv S Stn",0.08,null,240,"",1,"Y"]
[675348,"Cambridge Arms 132kV S Stn",7.1999999999999995E-2,null,614,"",1,"Y"]
[680000,"Ironbridge 400/132kV S Stn",0.06,null,1245,"",1,"Y"]
[680004,"Shrewsbury 400/132/33kV S Stn",0.11700000000000001,null,1951,"",3,"Y"]
[680008,"Rugeley 400/132kV S Stn",7.4999999999999997E-2,null,983,"",1,"Y"]
[680024,"Ketley 132/33/11kV S Stn",0.09,null,720,"",3,"Y"]
[680025,"Ironbridge 132/33kV S Stn",0.04,null,91,"",3,"Y"]
[680026,"Meaford C 132/33/11kV S Stn",0.11,null,1013,"",3,"Y"]
[680027,"Barlaston 132kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[680043,"Uttoxeter 132/33kV S Stn",0.2,"Y",1000,"Y",3,"Y"]
[680044,"Kidsgrove 132/25kV S Stn",9.5000000000000001E-2,null,826,"",1,"Y"]
[680045,"Newcastle 33/11kV S Stn",5.8000000000000003E-2,null,681,"",3,"Y"]
[680046,"Whitfield 132kV S Stn",0.14499999999999999,null,1767,"",1,"Y"]
[680048,"Forsbrook 132/33kV S Stn",0.82,null,6239,"",3,"Y"]
[680049,"Stafford South 132/11kV S Stn",4.1000000000000002E-2,null,178,"",1,"Y"]
[680050,"Whitfield 132/33/11kV S Stn",0.14000000000000001,null,1249,"",3,"Y"]
[680051,"Rugeley 132kV S Stn",7.4999999999999997E-2,null,983,"",1,"Y"]
[680052,"Boothen 132/33/11kV S Stn",7.3999999999999996E-2,null,681,"",3,"Y"]
[680053,"Burntwood 132/11kV S Stn",0.115,null,602,"",1,"Y"]
[680054,"Burslem 132/33/11kV S Stn",8.5000000000000006E-2,null,280,"",3,"Y"]
[680055,"Cannock 132/11kV S Stn",4.2000000000000003E-2,null,240,"",1,"Y"]
[680056,"Lichfield 132/11kV S Stn",9.8000000000000004E-2,null,470,"",1,"Y"]
[680057,"Newcastle 132/11kV S Stn",0.11,null,722,"",1,"Y"]
[680058,"Stafford 132/25/11kV S Stn",5.7000000000000002E-2,null,304,"",1,"Y"]
[680059,"Stagefields 132/33/11kV S Stn",6.3E-2,null,632,"",3,"Y"]
[680060,"Hortonwood 132/11kV S Stn",0.111,null,876,"",1,"Y"]
[680061,"Rugeley Town 132/11kV S Stn",0.21,null,507,"",1,"Y"]
[680062,"Stafford South 132/11kV S Stn",0.04,null,70,"",1,"Y"]
[680065,"Burslem 33/11/6.6kV S Stn",8.5000000000000006E-2,null,280,"",3,"Y"]
[680066,"Bushbury D 132kV S Stn",8.8999999999999996E-2,null,1664,"",1,"Y"]
[680067,"Cellarhead 400/132kV S Stn",0.105,null,2405,"",1,"Y"]
[690009,"Tamworth Br 132/25kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[690072,"Carlton Park 132/11kV S Stn",0.2,"Y",1000,"Y",1,"Y"]
[720004,"Lea Marston 400/132kV S Stn",0.2,"Y",2800,"Y",1,"Y"]
[726003,"Bloxwich Ess 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[735832,"I54 33/11kv S Stn",0.7,"Y",500,"Y",3,"Y"]
[735840,"Union Road Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[736099,"Wolverhampton Power 33kv S Stn",0.7,"Y",500,"Y",3,"Y"]
[736183,"Hinksford Farm Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[745465,"Henley Solar Farm 33kV S Stn",0.126,null,252,"",3,"Y"]
[745501,"High Point Solar Pv 33kv S Stn",9.8000000000000004E-2,null,128,"",3,"Y"]
[745828,"Rock Farm ESS 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[750002,"Tenbury 33/11kV S Stn",0.16400000000000001,null,379,"",3,"Y"]
[750003,"Craven Arms 33/11kV S Stn",0.15,null,196,"",3,"Y"]
[750004,"Cleobury Mortimer 33/11kV S Stn",0.17199999999999999,null,241,"",3,"Y"]
[756542,"Larport Farm 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[756593,"Witches Solar Park 66kV S Stn",0.21,null,340,"",3,"Y"]
[759000,"Rotherdale Farm 66kv S Stn",0.13,null,270,"",3,"Y"]
[765589,"Hartlebury 66/11kV S Stn",0.28100000000000003,null,281,"",3,"Y"]
[765590,"Northwick Generation 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[770001,"Wribbenhall 33/11kV S Stn",0.26,null,338,"",3,"Y"]
[770002,"Stockton 33/11kV S Stn",0.375,null,348,"",3,"Y"]
[770003,"Quatt 33/11kV S Stn",0.127,null,254,"",3,"Y"]
[770004,"Star Aluminium 33/11kV S Stn",0.19400000000000001,null,139,"",3,"Y"]
[770005,"Kinver 33/11kV S Stn",1.2130000000000001,null,1237,"",3,"Y"]
[778160,"Rotherdale Farm Pv 66kv S Stn",0.13,null,270,"",3,"Y"]
[778880,"Hartlebury EFW 66kV S Stn",0.28100000000000003,null,281,"",3,"Y"]
[778960,"Drayton Farm North 66/11kv S Stn",9.1999999999999998E-2,null,209,"",3,"Y"]
[779071,"Astley Solar Farm 33kv S Stn",0.47,null,351,"",3,"Y"]
[779441,"Howard Road STOR 66kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[779493,"Upper Meadowly Pv Farm 33kv S Stn",0.7,"Y",500,"Y",3,"Y"]
[790001,"Lydney 33/11kV S Stn",0.21,null,712,"",3,"Y"]
[790002,"Tuffley 33/11kV S Stn",2.5999999999999999E-2,null,54,"",3,"Y"]
[790003,"Wapley 33kV S Stn",0.27900000000000003,null,415,"",3,"Y"]
[790004,"Oxbridge 33/11kV S Stn",0.218,null,312,"",3,"Y"]
[790005,"Brockworth 33/11kV S Stn",2.1000000000000001E-2,null,48,"",3,"Y"]
[790007,"Commercial Road 33/11kV S Stn",8.5000000000000006E-2,null,125,"",3,"Y"]
[790008,"Alveston 33/11kV S Stn",1.1000000000000001,null,1716,"",3,"Y"]
[790009,"Dudbridge 33/11kV S Stn",0.17299999999999999,null,237,"",3,"Y"]
[790010,"Cherington 33/11kV S Stn",2.95,null,2183,"",3,"Y"]
[790011,"Cowhorn 33/11kV S Stn",8.7999999999999995E-2,null,120,"",3,"Y"]
[790012,"Naishcombe Hill 33/11kV S Stn",0.66,null,832,"",3,"Y"]
[790013,"Camp 33/11kV S Stn",1.357,null,1154,"",3,"Y"]
[790014,"Mitcheldean 33/11kV S Stn",0.193,null,239,"",3,"Y"]
[790015,"Berkeley 33/11kV S Stn",0.33800000000000002,null,423,"",3,"Y"]
[790016,"Elton 33/11kV S Stn",0.33800000000000002,null,403,"",3,"Y"]
[790017,"Stowfield 33/11kV S Stn",0.246,null,236,"",3,"Y"]
[790018,"Bixhead 33/11kV S Stn",0.38500000000000001,null,454,"",3,"Y"]
[790019,"Wyelands 33kV S Stn",0.42599999999999999,null,443,"",3,"Y"]
[790021,"Dursley 33/11kV S Stn",6.7000000000000004E-2,null,120,"",3,"Y"]
[790022,"Netherhills 33/11kV S Stn",0.27300000000000002,null,380,"",3,"Y"]
[790023,"Mead Lane 33/11kV S Stn",0.08,null,113,"",3,"Y"]
[790024,"Coaley 33kV S Stn",0.23499999999999999,null,411,"",3,"Y"]
[790025,"Hammerley Down 33/11kV S Stn",0.50600000000000001,null,582,"",3,"Y"]
[790026,"Bilson 33/11kV S Stn",0.104,null,260,"",3,"Y"]
[790028,"Princess Royal 33/11kV S Stn",0.28899999999999998,null,390,"",3,"Y"]
[790029,"Rotol 33/11kV S Stn",0.06,null,186,"",3,"Y"]
[795484,"Tower Hill Solar Farm 33kv S Stn",0.874,null,942,"",3,"Y"]
[795644,"Cambridge Solar Power 33kv S Stn",0.7,"Y",500,"Y",3,"Y"]
[795651,"Upper Wick Solar Farm 33kv S Stn",0.7,"Y",500,"Y",3,"Y"]
[795655,"Upper Huntingford Solar Farm 33kv S Stn",0.1,null,162,"",3,"Y"]
[795658,"Ring O Bells Solar Farm 33kV S Stn",0.14599999999999999,null,203,"",3,"Y"]
[795669,"Hall Farm Pv Awre 33kv S Stn",0.15,null,117,"",3,"Y"]
[795720,"Actrees Solar Farm 33kV S Stn",7.6999999999999999E-2,null,105,"",3,"Y"]
[795721,"Bristol Road 33kV S Stn",0.04,null,84,"",3,"Y"]
[795731,"Yorkley Solar Farm 33kV S Stn",0.19,null,402,"",3,"Y"]
[795794,"Sudmeadow Road STOR Generation 33kV S Stn",0.8,null,1029,"",3,"Y"]
[795870,"EFW Javelin Park 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[798100,"Say Farm 33kv S Stn",0.22,null,303,"",3,"Y"]
[840002,"Halesfield 33/11kV S Stn",7.3999999999999996E-2,null,198,"",3,"Y"]
[840003,"Worfield 33/11kV S Stn",0.36,null,490,"",3,"Y"]
[840004,"Shifnal 33/11kV S Stn",0.22600000000000001,null,407,"",3,"Y"]
[840005,"Priestweston 33/11kV S Stn",0.81,null,811,"",3,"Y"]
[840006,"Leebotwood 33/11kV S Stn",0.48399999999999999,null,523,"",3,"Y"]
[840007,"Bishops Castle 33/11kV S Stn",0.19,null,134,"",3,"Y"]
[840008,"Easthope 33/11kV S Stn",0.6,null,586,"",3,"Y"]
[840009,"Newport 33/11kV S Stn",0.25,null,407,"",3,"Y"]
[840010,"Donnington 33/11kV S Stn",7.8E-2,null,161,"",3,"Y"]
[840011,"Snedshill 33/11kV S Stn",0.1,null,249,"",3,"Y"]
[840012,"Sankey 33/11kV S Stn",0.27400000000000002,null,403,"",3,"Y"]
[840013,"Bayston Hill 33/11kV S Stn",0.26,null,494,"",3,"Y"]
[840014,"Madeley 33/11kV S Stn",6.5000000000000002E-2,null,83,"",3,"Y"]
[840016,"Leaton 33/11kV S Stn",0.41099999999999998,null,652,"",3,"Y"]
[840017,"Malehurst 33/11kV S Stn",0.23599999999999999,null,354,"",3,"Y"]
[840018,"Berrington 33/11kV S Stn",0.36,null,710,"",3,"Y"]
[840019,"Dothill 33/11kV S Stn",0.20799999999999999,null,386,"",3,"Y"]
[840020,"Roushill 33/11kV S Stn",0.08,null,166,"",3,"Y"]
[840021,"Harlescott 33/11kV S Stn",6.3E-2,null,214,"",3,"Y"]
[840022,"Weir Hill 33/11kV S Stn",0.22,null,493,"",3,"Y"]
[840023,"Broseley 33/11kV S Stn",0.13,null,258,"",3,"Y"]
[840024,"Rowton 33/11kV S Stn",0.34,null,510,"",3,"Y"]
[840025,"Spring Gardens 33/11kV S Stn",0.23,null,368,"",3,"Y"]
[840698,"Battlefield Generation 33kV S Stn",0.14000000000000001,null,98,"",3,"Y"]
[840844,"Hayford Solar Farm 33kV S Stn",0.14000000000000001,null,202,"",3,"Y"]
[841517,"Wrockwardine Farm 33kV S Stn",0.14000000000000001,null,275,"",3,"Y"]
[841546,"Condover Solar Farm 33kV S Stn",0.26,null,284,"",3,"Y"]
[841751,"Pitchford Solar Farm 33kV S Stn",0.19,null,191,"",3,"Y"]
[841809,"Sundorne Solar Farm 33kV S Stn",0.12,null,291,"",3,"Y"]
[841865,"Sheriffhales Solar Farm 33kv S Stn",0.13600000000000001,null,272,"",3,"Y"]
[850001,"Longton 132/33/11kV S Stn",4.7E-2,null,420,"",3,"Y"]
[850002,"Bearstone 33/11kV S Stn",0.42699999999999999,null,427,"",3,"Y"]
[850003,"Hill Chorlton 33/11kV S Stn",0.67700000000000005,null,193,"",3,"Y"]
[850004,"High Offley 33/11kV S Stn",0.5,null,526,"",3,"Y"]
[850005,"Cotes Heath 33/11kV S Stn",0.17,null,425,"",3,"Y"]
[850006,"Hookgate 33/11kV S Stn",0.54,null,1030,"",3,"Y"]
[850007,"Hinstock 33/11kV S Stn",0.56999999999999995,null,689,"",3,"Y"]
[850008,"Market Drayton 33/11kV S Stn",0.21,null,700,"",3,"Y"]
[850009,"Gnosall 33/11kV S Stn",0.16300000000000001,null,152,"",3,"Y"]
[850010,"Eccleshall 33/11kV S Stn",0.20100000000000001,null,228,"",3,"Y"]
[850011,"Stoke CHP 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[850012,"Goldenhill Bank 33/11kV S Stn",0.108,null,169,"",3,"Y"]
[850013,"Talke 33/11kV S Stn",0.08,null,110,"",3,"Y"]
[850014,"Scot Hay 33/11kV S Stn",0.34,null,595,"",3,"Y"]
[850015,"Knypersley 33/11kV S Stn",0.15,null,418,"",3,"Y"]
[850016,"Endon 33/11kV S Stn",0.41299999999999998,null,909,"",3,"Y"]
[850017,"Froghall 33/11kV S Stn",0.19400000000000001,null,238,"",3,"Y"]
[850018,"Kingsley Holt 33/11kV S Stn",0.221,null,351,"",3,"Y"]
[850019,"Tean 33/11kV S Stn",0.2,null,256,"",3,"Y"]
[850020,"Cheddleton 33/11kV S Stn",0.23100000000000001,null,416,"",3,"Y"]
[850021,"Cauldon Cement 33kV S Stn",0.251,null,277,"",3,"Y"]
[850022,"Congleton 33/11kV S Stn",7.5999999999999998E-2,null,115,"",3,"Y"]
[850024,"Cheadle 33/11kV S Stn",0.13700000000000001,null,229,"",3,"Y"]
[850026,"Cauldon 33/11kV S Stn",0.34,null,454,"",3,"Y"]
[850027,"British Industrial Sand 33kV S Stn",0.51200000000000001,null,701,"",3,"Y"]
[850028,"Leek 33/11kV S Stn",0.216,null,307,"",3,"Y"]
[850029,"Simplex 33/11kV S Stn",4.9000000000000002E-2,null,110,"",3,"Y"]
[856887,"Lower Newton Solar Farm 33kV S Stn",0.13,null,185,"",3,"Y"]
[856916,"Swancote AD Generation 33kV S Stn",0.7,"Y",500,"Y",3,"Y"]
[857114,"Staunch Standby Generation 33kv S Stn",0.89,null,447,"",3,"Y"]
[863412,"Moneystone Quarry PV Farm 33kV S Stn",0.249,null,373,"",3,"Y"]
[863413,"Heywood Grange PV Farm 33kV S Stn",0.21,null,556,"",3,"Y"]
[930026,"Courtaulds 33/6.6kV S Stn",0.13900000000000001,null,209,"",3,"Y"]

{"sheet":"Source-WM-Name","index":21,"n_rows":305,"n_cols":9,"rows_kept":305,"cut":false,"hidden":true,"merged":[]}
[null,1,2,3,4,5,6,7,8]
["SUBSTATION_NAME_WM","SUBSTATION_NAME_TRUNC_WM","SUBSTATION_NUMBER","ZE","Assumed ZE","UE","Assumed UE","t","Assumed t"]
["Abson 33kV S Stn","Abson33kVSStn",670084,0.25900000000000001,null,328,"",3,"Y"]
["Actrees Solar Farm 33kV S Stn","ActreesSolarFarm33kVSStn",795720,7.6999999999999999E-2,null,105,"",3,"Y"]
["Air Liquide 132kV S Stn","AirLiquide132kVSStn",670161,0.2,"Y",1000,"Y",1,"Y"]
["Albrighton 33/11kV S Stn","Albrighton33/11kVSStn",670122,0.16,null,200,"",3,"Y"]
["Alderton 66/11kV S Stn","Alderton66/11kVSStn",670088,0.13,null,179,"",3,"Y"]
["Aldridge 33/6.6kV S Stn","Aldridge33/6.6kVSStn",670125,6.2E-2,null,133,"",3,"Y"]
["Alveston 33/11kV S Stn","Alveston33/11kVSStn",790008,1.1000000000000001,null,1716,"",3,"Y"]
["Arley 33kV S Stn","Arley33kVSStn",670107,1.79,null,1545,"",3,"Y"]
["Astley Solar Farm 33kv S Stn","AstleySolarFarm33kvSStn",779071,0.47,null,351,"",3,"Y"]
["Banbury 132/11kV S Stn","Banbury132/11kVSStn",670045,6.6000000000000003E-2,null,211,"",1,"Y"]
["Barlaston 132kV S Stn","Barlaston132kVSStn",680027,0.2,"Y",1000,"Y",1,"Y"]
["Bartley Green 132/11kV S Stn","BartleyGreen132/11kVSStn",670138,9.2999999999999999E-2,null,1038,"",1,"Y"]
["Barton Abrasives 33/11kV S Stn","BartonAbrasives33/11kVSStn",670148,0.151,null,831,"",3,"Y"]
["Battlefield Generation 33kV S Stn","BattlefieldGeneration33kVSStn",840698,0.14000000000000001,null,98,"",3,"Y"]
["Bayston Hill 33/11kV S Stn","BaystonHill33/11kVSStn",840013,0.26,null,494,"",3,"Y"]
["Bearstone 33/11kV S Stn","Bearstone33/11kVSStn",850002,0.42699999999999999,null,427,"",3,"Y"]
["Bentley 132/11kV S Stn","Bentley132/11kVSStn",670046,8.8999999999999996E-2,null,694,"",1,"Y"]
["Berkeley 33/11kV S Stn","Berkeley33/11kVSStn",790015,0.33800000000000002,null,423,"",3,"Y"]
["Berrington 33/11kV S Stn","Berrington33/11kVSStn",840018,0.36,null,710,"",3,"Y"]
["Bevington 66/11kV S Stn","Bevington66/11kVSStn",670098,0.154,null,248,"",3,"Y"]
["Bilson 33/11kV S Stn","Bilson33/11kVSStn",790026,0.104,null,260,"",3,"Y"]
["Birchfield Lane 132/11kV S Stn","BirchfieldLane132/11kVSStn",670047,5.0999999999999997E-2,null,418,"",1,"Y"]
["Bishops Castle 33/11kV S Stn","BishopsCastle33/11kVSStn",840007,0.19,null,134,"",3,"Y"]
["Bishops Cleeve 66/11kV S Stn","BishopsCleeve66/11kVSStn",670086,0.115,null,163,"",3,"Y"]
["Bishops Wood 275/132kV S Stn","BishopsWood275/132kVSStn",670002,0.17,null,3145,"",1,"Y"]
["Bixhead 33/11kV S Stn","Bixhead33/11kVSStn",790018,0.38500000000000001,null,454,"",3,"Y"]
["Black Lake 132/11kV S Stn","BlackLake132/11kVSStn",670048,7.1999999999999995E-2,null,532,"",1,"Y"]
["Bloxham 66/11kV S Stn","Bloxham66/11kVSStn",670087,0.31,null,504,"",3,"Y"]
["Bloxwich Ess 33kV S Stn","BloxwichEss33kVSStn",726003,0.7,"Y",500,"Y",3,"Y"]
["Bodenham 66/11kV S Stn","Bodenham66/11kVSStn",670112,0.46,null,1334,"",3,"Y"]
["Boothen 132/33/11kV S Stn","Boothen132/33/11kVSStn",680052,7.3999999999999996E-2,null,681,"",3,"Y"]
["Bordesley 132/11kV S Stn","Bordesley132/11kVSStn",670041,9.7000000000000003E-2,null,286,"",1,"Y"]
["Boughton Rd 132/11kV S Stn","BoughtonRd132/11kVSStn",670137,4.3999999999999997E-2,null,498,"",1,"Y"]
["Bournville 132/11kV S Stn","Bournville132/11kVSStn",670050,6.8000000000000005E-2,null,474,"",1,"Y"]
["Bristol Road 33kV S Stn","BristolRoad33kVSStn",795721,0.04,null,84,"",3,"Y"]
["British Industrial Sand 33kV S Stn","BritishIndustrialSand33kVSStn",850027,0.51200000000000001,null,701,"",3,"Y"]
["Broadway 66/11kV S Stn","Broadway66/11kVSStn",670089,0.37,null,701,"",3,"Y"]
["Brockworth 33/11kV S Stn","Brockworth33/11kVSStn",790005,2.1000000000000001E-2,null,48,"",3,"Y"]
["Bromyard 66/11kV S Stn","Bromyard66/11kVSStn",670108,0.223,null,386,"",3,"Y"]
["Broseley 33/11kV S Stn","Broseley33/11kVSStn",840023,0.13,null,258,"",3,"Y"]
["Brotheridge Green 66/11kV S Stn","BrotheridgeGreen66/11kVSStn",670102,0.41,null,614,"",3,"Y"]
["Burntwood 132/11kV S Stn","Burntwood132/11kVSStn",680053,0.115,null,602,"",1,"Y"]
["Burslem 132/33/11kV S Stn","Burslem132/33/11kVSStn",680054,8.5000000000000006E-2,null,280,"",3,"Y"]
["Burslem 33/11/6.6kV S Stn","Burslem33/11/6.6kVSStn",680065,8.5000000000000006E-2,null,280,"",3,"Y"]
["Bushbury A 132kV S Stn","BushburyA132kVSStn",670017,8.8999999999999996E-2,null,1664,"",1,"Y"]
["Bushbury B-C 132/33/11kV S Stn","BushburyB-C132/33/11kVSStn",670037,0.12,null,2077,"",3,"Y"]
["Bushbury D 132kV S Stn","BushburyD132kVSStn",680066,8.8999999999999996E-2,null,1664,"",1,"Y"]
["Bustleholm 132/11kV S Stn","Bustleholm132/11kVSStn",670139,0.1,null,990,"",1,"Y"]
["Bustleholm 275/132/11kV S Stn","Bustleholm275/132/11kVSStn",670004,0.1,null,990,"",1,"Y"]
["Cambridge Arms 132kV S Stn","CambridgeArms132kVSStn",675348,7.1999999999999995E-2,null,614,"",1,"Y"]
["Cambridge Solar Power 33kv S Stn","CambridgeSolarPower33kvSStn",795644,0.7,"Y",500,"Y",3,"Y"]
["Camp 33/11kV S Stn","Camp33/11kVSStn",790013,1.357,null,1154,"",3,"Y"]
["Cannock 132/11kV S Stn","Cannock132/11kVSStn",680055,4.2000000000000003E-2,null,240,"",1,"Y"]
["Carlton Park 132/11kV S Stn","CarltonPark132/11kVSStn",690072,0.2,"Y",1000,"Y",1,"Y"]
["Castle Bromwich 132/11kV S Stn","CastleBromwich132/11kVSStn",670032,8.6999999999999994E-2,null,383,"",1,"Y"]
["Castle Meads 132/33kV S Stn","CastleMeads132/33kVSStn",670012,7.3999999999999996E-2,null,1037,"",3,"Y"]
["Cauldon 33/11kV S Stn","Cauldon33/11kVSStn",850026,0.34,null,454,"",3,"Y"]
["Cauldon Cement 33kV S Stn","CauldonCement33kVSStn",850021,0.251,null,277,"",3,"Y"]
["Cellarhead 400/132kV S Stn","Cellarhead400/132kVSStn",680067,0.105,null,2405,"",1,"Y"]
["Chad Valley 132/11kV S Stn","ChadValley132/11kVSStn",670051,0.08,null,336,"",1,"Y"]
["Cheadle 33/11kV S Stn","Cheadle33/11kVSStn",850024,0.13700000000000001,null,229,"",3,"Y"]
["Cheapside 132/11kV S Stn","Cheapside132/11kVSStn",670052,7.3999999999999996E-2,null,610,"",1,"Y"]
["Cheddleton 33/11kV S Stn","Cheddleton33/11kVSStn",850020,0.23100000000000001,null,416,"",3,"Y"]
["Chelmsley Wood 132/11kV S Stn","ChelmsleyWood132/11kVSStn",670140,2.9000000000000001E-2,null,609,"",1,"Y"]
["Chelmsley Wood 33/11kV S Stn","ChelmsleyWood33/11kVSStn",670131,3.6999999999999998E-2,null,37,"",3,"Y"]
["Cheltenham 132/66/11kV S Stn","Cheltenham132/66/11kVSStn",670053,5.1999999999999998E-2,null,201,"",3,"Y"]
["Cherington 33/11kV S Stn","Cherington33/11kVSStn",790010,2.95,null,2183,"",3,"Y"]
["Chester Street 132/11kV S Stn","ChesterStreet132/11kVSStn",670054,0.38400000000000001,null,614,"",1,"Y"]
["Chipping Sodbury 132/33/11kV S Stn","ChippingSodbury132/33/11kVSStn",670042,0.28000000000000003,null,974,"",3,"Y"]
["Cleobury Mortimer 33/11kV S Stn","CleoburyMortimer33/11kVSStn",750004,0.17199999999999999,null,241,"",3,"Y"]
["Coaley 33kV S Stn","Coaley33kVSStn",790024,0.23499999999999999,null,411,"",3,"Y"]
["Commercial Road 33/11kV S Stn","CommercialRoad33/11kVSStn",790007,8.5000000000000006E-2,null,125,"",3,"Y"]
["Condover Solar Farm 33kV S Stn","CondoverSolarFarm33kVSStn",841546,0.26,null,284,"",3,"Y"]
["Congleton 33/11kV S Stn","Congleton33/11kVSStn",850022,7.5999999999999998E-2,null,115,"",3,"Y"]
["Copt Heath 132/11kV S Stn","CoptHeath132/11kVSStn",670055,0.115,null,566,"",1,"Y"]
["Coseley 132/11kV S Stn","Coseley132/11kVSStn",670056,0.10100000000000001,null,760,"",1,"Y"]
["Cotes Heath 33/11kV S Stn","CotesHeath33/11kVSStn",850005,0.17,null,425,"",3,"Y"]
["Courtaulds 33/6.6kV S Stn","Courtaulds33/6.6kVSStn",930026,0.13900000000000001,null,209,"",3,"Y"]
["Cowhorn 33/11kV S Stn","Cowhorn33/11kVSStn",790011,8.7999999999999995E-2,null,120,"",3,"Y"]
["Craven Arms 33/11kV S Stn","CravenArms33/11kVSStn",750003,0.15,null,196,"",3,"Y"]
["Donnington 33/11kV S Stn","Donnington33/11kVSStn",840010,7.8E-2,null,161,"",3,"Y"]
["Dothill 33/11kV S Stn","Dothill33/11kVSStn",840019,0.20799999999999999,null,386,"",3,"Y"]
["Drayton Farm North 66/11kv S Stn","DraytonFarmNorth66/11kvSStn",778960,9.1999999999999998E-2,null,209,"",3,"Y"]
["Droitwich 66/11kV S Stn","Droitwich66/11kVSStn",670115,9.8000000000000004E-2,null,141,"",3,"Y"]
["Dudbridge 33/11kV S Stn","Dudbridge33/11kVSStn",790009,0.17299999999999999,null,237,"",3,"Y"]
["Dudley 132/11kV S Stn","Dudley132/11kVSStn",670057,5.3999999999999999E-2,null,437,"",1,"Y"]
["Dunlop 132kV S Stn","Dunlop132kVSStn",670029,0.23799999999999999,null,2222,"",1,"Y"]
["Dursley 33/11kV S Stn","Dursley33/11kVSStn",790021,6.7000000000000004E-2,null,120,"",3,"Y"]
["Dymock 66/11kV S Stn","Dymock66/11kVSStn",670143,0.314,null,891,"",3,"Y"]
["Eastern Avenue 132/11kV S Stn","EasternAvenue132/11kVSStn",670058,3.9E-2,null,416,"",1,"Y"]
["Easthope 33/11kV S Stn","Easthope33/11kVSStn",840008,0.6,null,586,"",3,"Y"]
["Eccleshall 33/11kV S Stn","Eccleshall33/11kVSStn",850010,0.20100000000000001,null,228,"",3,"Y"]
["EFW Javelin Park 33kV S Stn","EFWJavelinPark33kVSStn",795870,0.7,"Y",500,"Y",3,"Y"]
["Elmdon 132/11kV S Stn","Elmdon132/11kVSStn",670059,0.06,null,424,"",1,"Y"]
["Elton 33/11kV S Stn","Elton33/11kVSStn",790016,0.33800000000000002,null,403,"",3,"Y"]
["Endon 33/11kV S Stn","Endon33/11kVSStn",850016,0.41299999999999998,null,909,"",3,"Y"]
["Epwell 66/11kV S Stn","Epwell66/11kVSStn",670090,0.34,null,308,"",3,"Y"]
["Erdington 132/11kV S Stn","Erdington132/11kVSStn",670136,0.2,"Y",1000,"Y",1,"Y"]
["Erdington 132kV S Stn","Erdington132kVSStn",670034,0.121,null,581,"",1,"Y"]
["Evesham 66/11kV S Stn","Evesham66/11kVSStn",670097,0.14499999999999999,null,399,"",3,"Y"]
["Feckenham 275/66/11kV S Stn","Feckenham275/66/11kVSStn",670003,7.2999999999999995E-2,null,1030,"",3,"Y"]
["Forsbrook 132/33kV S Stn","Forsbrook132/33kVSStn",680048,0.82,null,6239,"",3,"Y"]
["Four Ashes 33/11kV S Stn","FourAshes33/11kVSStn",670124,0.189,null,230,"",3,"Y"]
["Four Ashes E F W 33kV S Stn","FourAshesEFW33kVSStn",670141,0.7,"Y",500,"Y",3,"Y"]
["Froghall 33/11kV S Stn","Froghall33/11kVSStn",850017,0.19400000000000001,null,238,"",3,"Y"]
["Garreg Lwyd Wind Farm 66kV S Stn","GarregLwydWindFarm66kVSStn",670153,2.2200000000000002,null,2743,"",3,"Y"]
["Gnosall 33/11kV S Stn","Gnosall33/11kVSStn",850009,0.16300000000000001,null,152,"",3,"Y"]
["Goldenhill Bank 33/11kV S Stn","GoldenhillBank33/11kVSStn",850012,0.108,null,169,"",3,"Y"]
["Great Alne 66/11kV S Stn","GreatAlne66/11kVSStn",670105,0.159,null,348,"",3,"Y"]
["Halesfield 33/11kV S Stn","Halesfield33/11kVSStn",840002,7.3999999999999996E-2,null,198,"",3,"Y"]
["Halesowen 132/11kV S Stn","Halesowen132/11kVSStn",670060,8.5000000000000006E-2,null,909,"",1,"Y"]
["Hall Farm Pv Awre 33kv S Stn","HallFarmPvAwre33kvSStn",795669,0.15,null,117,"",3,"Y"]
["Hall Green 132/11kV S Stn","HallGreen132/11kVSStn",670028,7.5999999999999998E-2,null,516,"",1,"Y"]
["Hammerley Down 33/11kV S Stn","HammerleyDown33/11kVSStn",790025,0.50600000000000001,null,582,"",3,"Y"]
["Hams Hall 132/33kV S Stn","HamsHall132/33kVSStn",670033,0.105,null,1775,"",3,"Y"]
["Hams Hall South 132/11kV S Stn","HamsHallSouth132/11kVSStn",670043,0.08,null,1115,"",1,"Y"]
["Harlescott 33/11kV S Stn","Harlescott33/11kVSStn",840021,6.3E-2,null,214,"",3,"Y"]
["Hartlebury 66/11kV S Stn","Hartlebury66/11kVSStn",765589,0.28100000000000003,null,281,"",3,"Y"]
["Hartlebury EFW 66kV S Stn","HartleburyEFW66kVSStn",778880,0.28100000000000003,null,281,"",3,"Y"]
["Hayford Solar Farm 33kV S Stn","HayfordSolarFarm33kVSStn",840844,0.14000000000000001,null,202,"",3,"Y"]
["Henley Solar Farm 33kV S Stn","HenleySolarFarm33kVSStn",745465,0.126,null,252,"",3,"Y"]
["Hereford 132/66kV S Stn","Hereford132/66kVSStn",670013,0.129,null,647,"",3,"Y"]
["Hereford Central 66/11kv S Stn","HerefordCentral66/11kvSStn",670151,0.156,null,279,"",3,"Y"]
["Hereford North 66/11kV S Stn","HerefordNorth66/11kVSStn",670096,9.6000000000000002E-2,null,141,"",3,"Y"]
["Hereford South 66/11kV S Stn","HerefordSouth66/11kVSStn",670103,0.16600000000000001,null,266,"",3,"Y"]
["Heywood Grange PV Farm 33kV S Stn","HeywoodGrangePVFarm33kVSStn",863413,0.21,null,556,"",3,"Y"]
["High Offley 33/11kV S Stn","HighOffley33/11kVSStn",850004,0.5,null,526,"",3,"Y"]
["High Point Solar Pv 33kv S Stn","HighPointSolarPv33kvSStn",745501,9.8000000000000004E-2,null,128,"",3,"Y"]
["Highters Heath 132/11kV S Stn","HightersHeath132/11kVSStn",670061,6.5000000000000002E-2,null,469,"",1,"Y"]
["Hill Chorlton 33/11kV S Stn","HillChorlton33/11kVSStn",850003,0.67700000000000005,null,193,"",3,"Y"]
["Hinksford 132/33/11kV S Stn","Hinksford132/33/11kVSStn",670062,0.12,null,1079,"",3,"Y"]
["Hinksford Farm Generation 33kV S Stn","HinksfordFarmGeneration33kVSStn",736183,0.7,"Y",500,"Y",3,"Y"]
["Hinstock 33/11kV S Stn","Hinstock33/11kVSStn",850007,0.56999999999999995,null,689,"",3,"Y"]
["Hockley 132/11kv S Stn","Hockley132/11kvSStn",670200,0.08,null,240,"",1,"Y"]
["Hookgate 33/11kV S Stn","Hookgate33/11kVSStn",850006,0.54,null,1030,"",3,"Y"]
["Hortonwood 132/11kV S Stn","Hortonwood132/11kVSStn",680060,0.111,null,876,"",1,"Y"]
["Howard Road STOR 66kV S Stn","HowardRoadSTOR66kVSStn",779441,0.7,"Y",500,"Y",3,"Y"]
["I54 33/11kv S Stn","I5433/11kvSStn",735832,0.7,"Y",500,"Y",3,"Y"]
["Ipsley 66/11kV S Stn","Ipsley66/11kVSStn",670120,6.8000000000000005E-2,null,146,"",3,"Y"]
["Iron Acton 275/132kV S Stn","IronActon275/132kVSStn",670001,0.09,null,1503,"",1,"Y"]
["Ironbridge 132/33kV S Stn","Ironbridge132/33kVSStn",680025,0.04,null,91,"",3,"Y"]
["Ironbridge 400/132kV S Stn","Ironbridge400/132kVSStn",680000,0.06,null,1245,"",1,"Y"]
["Kenswick 66/11kV S Stn","Kenswick66/11kVSStn",670116,0.48699999999999999,null,360,"",3,"Y"]
["Ketley 132/33/11kV S Stn","Ketley132/33/11kVSStn",680024,0.09,null,720,"",3,"Y"]
["Kidderminster 132/33/11kV S Stn","Kidderminster132/33/11kVSStn",670063,0.24,null,1546,"",3,"Y"]
["Kidsgrove 132/25kV S Stn","Kidsgrove132/25kVSStn",680044,9.5000000000000001E-2,null,826,"",1,"Y"]
["Kingsley Holt 33/11kV S Stn","KingsleyHolt33/11kVSStn",850018,0.221,null,351,"",3,"Y"]
["Kingstanding 132/11kV S Stn","Kingstanding132/11kVSStn",670128,0.23,null,265,"",1,"Y"]
["Kington 66/11kV S Stn","Kington66/11kVSStn",670114,0.38500000000000001,null,454,"",3,"Y"]
["Kinver 33/11kV S Stn","Kinver33/11kVSStn",770005,1.2130000000000001,null,1237,"",3,"Y"]
["Kitts Green 132/11kV S Stn","KittsGreen132/11kVSStn",670030,0.125,null,635,"",1,"Y"]
["Kitwell 275/132kV S Stn","Kitwell275/132kVSStn",670011,0.126,null,2528,"",1,"Y"]
["Knighton 66/11kV S Stn","Knighton66/11kVSStn",670121,0.97299999999999998,null,973,"",3,"Y"]
["Knypersley 33/11kV S Stn","Knypersley33/11kVSStn",850015,0.15,null,418,"",3,"Y"]
["Ladywood 132/11kV S Stn","Ladywood132/11kVSStn",670040,0.17299999999999999,null,1358,"",1,"Y"]
["Larport Farm 66kV S Stn","LarportFarm66kVSStn",756542,0.7,"Y",500,"Y",3,"Y"]
["Lea Marston 400/132kV S Stn","LeaMarston400/132kVSStn",720004,0.2,"Y",2800,"Y",1,"Y"]
["Leaton 33/11kV S Stn","Leaton33/11kVSStn",840016,0.41099999999999998,null,652,"",3,"Y"]
["Ledbury 66/11kV S Stn","Ledbury66/11kVSStn",670129,9.6000000000000002E-2,null,294,"",3,"Y"]
["Leebotwood 33/11kV S Stn","Leebotwood33/11kVSStn",840006,0.48399999999999999,null,523,"",3,"Y"]
["Leek 33/11kV S Stn","Leek33/11kVSStn",850028,0.216,null,307,"",3,"Y"]
["Leominster 66/11kV S Stn","Leominster66/11kVSStn",670100,0.253,null,441,"",3,"Y"]
["Lichfield 132/11kV S Stn","Lichfield132/11kVSStn",680056,9.8000000000000004E-2,null,470,"",1,"Y"]
["Longbridge 132/11kV S Stn","Longbridge132/11kVSStn",670049,0.04,null,449,"",1,"Y"]
["Long Marston 66/11kV S Stn","LongMarston66/11kVSStn",670094,0.10100000000000001,null,128,"",3,"Y"]
["Longton 132/33/11kV S Stn","Longton132/33/11kVSStn",850001,4.7E-2,null,420,"",3,"Y"]
["Lower Chadnor 66/11kV S Stn","LowerChadnor66/11kVSStn",670117,0.35499999999999998,null,383,"",3,"Y"]
["Lower Newton Solar Farm 33kV S Stn","LowerNewtonSolarFarm33kVSStn",856887,0.13,null,185,"",3,"Y"]
["Ludlow 132/66/33/11kV S Stn","Ludlow132/66/33/11kVSStn",670064,0.15,null,599,"",3,"Y"]
["Lydney 33/11kV S Stn","Lydney33/11kVSStn",790001,0.21,null,712,"",3,"Y"]
["Lydney Local 132kV S Stn","LydneyLocal132kVSStn",670031,0.21,null,712,"",1,"Y"]
["Lye 132/11kV S Stn","Lye132/11kVSStn",670065,4.2999999999999997E-2,null,430,"",1,"Y"]
["Madeley 33/11kV S Stn","Madeley33/11kVSStn",840014,6.5000000000000002E-2,null,83,"",3,"Y"]
["Madley 66/11kV S Stn","Madley66/11kVSStn",670109,0.28999999999999998,null,592,"",3,"Y"]
["Malehurst 33/11kV S Stn","Malehurst33/11kVSStn",840017,0.23599999999999999,null,354,"",3,"Y"]
["Malvern 132/11kV S Stn","Malvern132/11kVSStn",670067,4.8000000000000001E-2,null,319,"",1,"Y"]
["Market Drayton 33/11kV S Stn","MarketDrayton33/11kVSStn",850008,0.21,null,700,"",3,"Y"]
["Marle Hill 132/66/11kV S Stn","MarleHill132/66/11kVSStn",670066,3.5000000000000003E-2,null,160,"",3,"Y"]
["Mead Lane 33/11kV S Stn","MeadLane33/11kVSStn",790023,0.08,null,113,"",3,"Y"]
["Meaford C 132/33/11kV S Stn","MeafordC132/33/11kVSStn",680026,0.11,null,1013,"",3,"Y"]
["Mitcheldean 33/11kV S Stn","Mitcheldean33/11kVSStn",790014,0.193,null,239,"",3,"Y"]
["Moneystone Quarry PV Farm 33kV S Stn","MoneystoneQuarryPVFarm33kVSStn",863412,0.249,null,373,"",3,"Y"]
["Montpellier 132/11kV S Stn","Montpellier132/11kVSStn",670068,4.3999999999999997E-2,null,216,"",1,"Y"]
["Moreton 66/11kV S Stn","Moreton66/11kVSStn",670085,0.114,null,191,"",3,"Y"]
["Naishcombe Hill 33/11kV S Stn","NaishcombeHill33/11kVSStn",790012,0.66,null,832,"",3,"Y"]
["Nechells East 275/132kV S Stn","NechellsEast275/132kVSStn",670007,7.0000000000000007E-2,null,1540,"",1,"Y"]
["Nechells West 132/25/11kV S Stn","NechellsWest132/25/11kVSStn",670069,0.11,null,583,"",1,"Y"]
["Netherhills 33/11kV S Stn","Netherhills33/11kVSStn",790022,0.27300000000000002,null,380,"",3,"Y"]
["Newcastle 132/11kV S Stn","Newcastle132/11kVSStn",680057,0.11,null,722,"",1,"Y"]
["Newcastle 33/11kV S Stn","Newcastle33/11kVSStn",680045,5.8000000000000003E-2,null,681,"",3,"Y"]
["Newent 66/11kV S Stn","Newent66/11kVSStn",670133,0.3,null,851,"",3,"Y"]
["Newport 33/11kV S Stn","Newport33/11kVSStn",840009,0.25,null,407,"",3,"Y"]
["Northwick Generation 66kV S Stn","NorthwickGeneration66kVSStn",765590,0.7,"Y",500,"Y",3,"Y"]
["Ocker Hill B 132/33/11kV S Stn","OckerHillB132/33/11kVSStn",670070,5.1999999999999998E-2,null,854,"",3,"Y"]
["Ocker Hill C 275/132kV S Stn","OckerHillC275/132kVSStn",670010,7.0000000000000007E-2,null,1266,"",1,"Y"]
["Oldbury 132/11kV S Stn","Oldbury132/11kVSStn",670005,7.5999999999999998E-2,null,965,"",1,"Y"]
["Oldbury B 132/33/11kV S Stn","OldburyB132/33/11kVSStn",670154,0.2,"Y",1000,"Y",3,"Y"]
["Oxbridge 33/11kV S Stn","Oxbridge33/11kVSStn",790004,0.218,null,312,"",3,"Y"]
["Pattingham 33/11kV S Stn","Pattingham33/11kVSStn",670142,0.12,null,205,"",3,"Y"]
["Penn 400/275/132kV S Stn","Penn400/275/132kVSStn",670009,9.7000000000000003E-2,null,1242,"",1,"Y"]
["Perry Barr 132/11kV S Stn","PerryBarr132/11kVSStn",670071,0.112,null,445,"",1,"Y"]
["Pershore 66/11kV S Stn","Pershore66/11kVSStn",670095,0.17100000000000001,null,324,"",3,"Y"]
["Peterchurch 66/11kV S Stn","Peterchurch66/11kVSStn",670099,0.22,null,303,"",3,"Y"]
["Pitchford Solar Farm 33kV S Stn","PitchfordSolarFarm33kVSStn",841751,0.19,null,191,"",3,"Y"]
["Pontrilas 66/11kV S Stn","Pontrilas66/11kVSStn",670106,0.2,null,380,"",3,"Y"]
["Port Ham 400/132kV S Stn","PortHam400/132kVSStn",670008,0.63,null,561,"",1,"Y"]
["Presteigne 66/11kV S Stn","Presteigne66/11kVSStn",670111,0.44,null,722,"",3,"Y"]
["Priestweston 33/11kV S Stn","Priestweston33/11kVSStn",840005,0.81,null,811,"",3,"Y"]
["Princess Royal 33/11kV S Stn","PrincessRoyal33/11kVSStn",790028,0.28899999999999998,null,390,"",3,"Y"]
["Quatt 33/11kV S Stn","Quatt33/11kVSStn",770003,0.127,null,254,"",3,"Y"]
["Redditch North 66/11kV S Stn","RedditchNorth66/11kVSStn",670119,0.122,null,232,"",3,"Y"]
["Redditch South 66/11kV S Stn","RedditchSouth66/11kVSStn",670118,7.3999999999999996E-2,null,221,"",3,"Y"]
["Rednal 132/11kV S Stn","Rednal132/11kVSStn",670072,6.4000000000000001E-2,null,620,"",1,"Y"]
["Ring O Bells Solar Farm 33kV S Stn","RingOBellsSolarFarm33kVSStn",795658,0.14599999999999999,null,203,"",3,"Y"]
["Rock Farm ESS 33kV S Stn","RockFarmESS33kVSStn",745828,0.7,"Y",500,"Y",3,"Y"]
["Ross 66/11kV S Stn","Ross66/11kVSStn",670126,0.1,null,139,"",3,"Y"]
["Rotherdale Farm 66kv S Stn","RotherdaleFarm66kvSStn",759000,0.13,null,270,"",3,"Y"]
["Rotherdale Farm Pv 66kv S Stn","RotherdaleFarmPv66kvSStn",778160,0.13,null,270,"",3,"Y"]
["Rotol 33/11kV S Stn","Rotol33/11kVSStn",790029,0.06,null,186,"",3,"Y"]
["Roushill 33/11kV S Stn","Roushill33/11kVSStn",840020,0.08,null,166,"",3,"Y"]
["Rowton 33/11kV S Stn","Rowton33/11kVSStn",840024,0.34,null,510,"",3,"Y"]
["Rugeley 132kV S Stn","Rugeley132kVSStn",680051,7.4999999999999997E-2,null,983,"",1,"Y"]
["Rugeley 400/132kV S Stn","Rugeley400/132kVSStn",680008,7.4999999999999997E-2,null,983,"",1,"Y"]
["Rugeley Town 132/11kV S Stn","RugeleyTown132/11kVSStn",680061,0.21,null,507,"",1,"Y"]
["Rushall 132/11kV S Stn","Rushall132/11kVSStn",670073,0.16,null,498,"",1,"Y"]
["Ryeford 132/33/11kV S Stn","Ryeford132/33/11kVSStn",670015,5.6000000000000001E-2,null,209,"",3,"Y"]
["Sankey 33/11kV S Stn","Sankey33/11kVSStn",840012,0.27400000000000002,null,403,"",3,"Y"]
["Say Farm 33kv S Stn","SayFarm33kvSStn",798100,0.22,null,303,"",3,"Y"]
["Scot Hay 33/11kV S Stn","ScotHay33/11kVSStn",850014,0.34,null,595,"",3,"Y"]
["Selly Oak 132/11kV S Stn","SellyOak132/11kVSStn",670074,8.5999999999999993E-2,null,791,"",1,"Y"]
["Selly Oak 132kV S Stn","SellyOak132kVSStn",670039,8.5999999999999993E-2,null,791,"",1,"Y"]
["Sheriffhales Solar Farm 33kv S Stn","SheriffhalesSolarFarm33kvSStn",841865,0.13600000000000001,null,272,"",3,"Y"]
["Shifnal 33/11kV S Stn","Shifnal33/11kVSStn",840004,0.22600000000000001,null,407,"",3,"Y"]
["Shipston 66/11kV S Stn","Shipston66/11kVSStn",670093,0.14799999999999999,null,202,"",3,"Y"]
["Shirley 132/11kV S Stn","Shirley132/11kVSStn",670075,6.5000000000000002E-2,null,449,"",1,"Y"]
["Shrewsbury 400/132/33kV S Stn","Shrewsbury400/132/33kVSStn",680004,0.11700000000000001,null,1951,"",3,"Y"]
["Simplex 33/11kV S Stn","Simplex33/11kVSStn",850029,4.9000000000000002E-2,null,110,"",3,"Y"]
["Smethwick 132/11kV S Stn","Smethwick132/11kVSStn",670076,0.153,null,1121,"",1,"Y"]
["Snedshill 33/11kV S Stn","Snedshill33/11kVSStn",840011,0.1,null,249,"",3,"Y"]
["Solihull 132/11kV S Stn","Solihull132/11kVSStn",670077,0.09,null,252,"",1,"Y"]
["Sparkbrook 132/11kV S Stn","Sparkbrook132/11kVSStn",670078,0.04,null,274,"",1,"Y"]
["Spring Gardens 33/11kV S Stn","SpringGardens33/11kVSStn",840025,0.23,null,368,"",3,"Y"]
["Stafford 132/25/11kV S Stn","Stafford132/25/11kVSStn",680058,5.7000000000000002E-2,null,304,"",1,"Y"]
["Stafford South 132/11kV S Stn","StaffordSouth132/11kVSStn",680049,4.1000000000000002E-2,null,178,"",1,"Y"]
["Stafford South 132/11kV S Stn","StaffordSouth132/11kVSStn",680062,0.04,null,70,"",1,"Y"]
["Stagefields 132/33/11kV S Stn","Stagefields132/33/11kVSStn",680059,6.3E-2,null,632,"",3,"Y"]
["Star Aluminium 33/11kV S Stn","StarAluminium33/11kVSStn",770004,0.19400000000000001,null,139,"",3,"Y"]
["Staunch Standby Generation 33kv S Stn","StaunchStandbyGeneration33kvSStn",857114,0.89,null,447,"",3,"Y"]
["Stockton 33/11kV S Stn","Stockton33/11kVSStn",770002,0.375,null,348,"",3,"Y"]
["Stoke CHP 33kV S Stn","StokeCHP33kVSStn",850011,0.7,"Y",500,"Y",3,"Y"]
["Stourport 132/66/33/11kV S Stn","Stourport132/66/33/11kVSStn",670079,0.112,null,618,"",3,"Y"]
["Stow 66/11kV S Stn","Stow66/11kVSStn",670091,1.66,null,2296,"",3,"Y"]
["Stowfield 33/11kV S Stn","Stowfield33/11kVSStn",790017,0.246,null,236,"",3,"Y"]
["Stratford 66/11kV S Stn","Stratford66/11kVSStn",670101,0.12,null,304,"",3,"Y"]
["Strensham 66/11kV S Stn","Strensham66/11kVSStn",670104,0.20200000000000001,null,352,"",3,"Y"]
["St Weonards 66/11kV S Stn","StWeonards66/11kVSStn",670113,0.38400000000000001,null,472,"",3,"Y"]
["Sudmeadow Road STOR Generation 33kV S Stn","SudmeadowRoadSTORGeneration33kVSStn",795794,0.8,null,1029,"",3,"Y"]
["Summer Lane 132/11kV S Stn","SummerLane132/11kVSStn",670027,0.08,null,240,"",1,"Y"]
["Sundorne Solar Farm 33kV S Stn","SundorneSolarFarm33kVSStn",841809,0.12,null,291,"",3,"Y"]
["Sutton Coldfield 132/11kV S Stn","SuttonColdfield132/11kVSStn",670080,9.6000000000000002E-2,null,703,"",1,"Y"]
["Swancote AD Generation 33kV S Stn","SwancoteADGeneration33kVSStn",856916,0.7,"Y",500,"Y",3,"Y"]
["Talke 33/11kV S Stn","Talke33/11kVSStn",850013,0.08,null,110,"",3,"Y"]
["Tamworth Br 132/25kV S Stn","TamworthBr132/25kVSStn",690009,0.2,"Y",1000,"Y",1,"Y"]
["Tean 33/11kV S Stn","Tean33/11kVSStn",850019,0.2,null,256,"",3,"Y"]
["Tenbury 33/11kV S Stn","Tenbury33/11kVSStn",750002,0.16400000000000001,null,379,"",3,"Y"]
["Tewkesbury 132/11kV S Stn","Tewkesbury132/11kVSStn",670081,5.7000000000000002E-2,null,337,"",1,"Y"]
["Tewkesbury 66/11kV S Stn","Tewkesbury66/11kVSStn",670083,6.4000000000000001E-2,null,532,"",3,"Y"]
["Timberdine 132/11kV S Stn","Timberdine132/11kVSStn",670019,0.08,null,515,"",1,"Y"]
["Tividale 132/11kV S Stn","Tividale132/11kVSStn",670020,0.11799999999999999,null,900,"",1,"Y"]
["Tower Hill Solar Farm 33kv S Stn","TowerHillSolarFarm33kvSStn",795484,0.874,null,942,"",3,"Y"]
["Troughton Farm 132kV S Stn","TroughtonFarm132kVSStn",670170,0.2,"Y",1000,"Y",1,"Y"]
["Tuffley 33/11kV S Stn","Tuffley33/11kVSStn",790002,2.5999999999999999E-2,null,54,"",3,"Y"]
["Union Road Generation 33kV S Stn","UnionRoadGeneration33kVSStn",735840,0.7,"Y",500,"Y",3,"Y"]
["University Of Birmingham 132/11kV S Stn","UniversityOfBirmingham132/11kVSStn",670035,2.9000000000000001E-2,null,275,"",1,"Y"]
["Upper Huntingford Solar Farm 33kv S Stn","UpperHuntingfordSolarFarm33kvSStn",795655,0.1,null,162,"",3,"Y"]
["Upper Meadowly Pv Farm 33kv S Stn","UpperMeadowlyPvFarm33kvSStn",779493,0.7,"Y",500,"Y",3,"Y"]
["Upper Wick Solar Farm 33kv S Stn","UpperWickSolarFarm33kvSStn",795651,0.7,"Y",500,"Y",3,"Y"]
["Upton Warren 132/66/11kV S Stn","UptonWarren132/66/11kVSStn",670021,0.104,null,374,"",3,"Y"]
["Uttoxeter 132/33kV S Stn","Uttoxeter132/33kVSStn",680043,0.2,"Y",1000,"Y",3,"Y"]
["Walsall 132/33kV S Stn","Walsall132/33kVSStn",670016,0.13600000000000001,null,352,"",3,"Y"]
["Wapley 33kV S Stn","Wapley33kVSStn",790003,0.27900000000000003,null,415,"",3,"Y"]
["Warndon 132/11kV S Stn","Warndon132/11kVSStn",670022,4.3999999999999997E-2,null,290,"",1,"Y"]
["Wednesfield 132/11kV S Stn","Wednesfield132/11kVSStn",670023,0.14699999999999999,null,1102,"",1,"Y"]
["Weir Hill 33/11kV S Stn","WeirHill33/11kVSStn",840022,0.22,null,493,"",3,"Y"]
["Whitfield 132/33/11kV S Stn","Whitfield132/33/11kVSStn",680050,0.14000000000000001,null,1249,"",3,"Y"]
["Whitfield 132kV S Stn","Whitfield132kVSStn",680046,0.14499999999999999,null,1767,"",1,"Y"]
["Wickhamford 66kv S Stn","Wickhamford66kvSStn",670152,0.124,null,214,"",3,"Y"]
["Willenhall 275/132/33/25/11kV S Stn","Willenhall275/132/33/25/11kVSStn",670006,7.0000000000000007E-2,null,211,"",3,"Y"]
["Winson Green 132/11kV S Stn","WinsonGreen132/11kVSStn",670038,0.05,null,279,"",1,"Y"]
["Witches Solar Park 66kV S Stn","WitchesSolarPark66kVSStn",756593,0.21,null,340,"",3,"Y"]
["Wolverhampton 132/33/11kV S Stn","Wolverhampton132/33/11kVSStn",670024,0.114,null,376,"",3,"Y"]
["Wolverhampton Power 33kv S Stn","WolverhamptonPower33kvSStn",736099,0.7,"Y",500,"Y",3,"Y"]
["Wolverhampton Waste Services 33kv S Stn","WolverhamptonWasteServices33kvSStn",670150,0.7,"Y",500,"Y",3,"Y"]
["Wolverhampton West 132/33/11kV S Stn","WolverhamptonWest132/33/11kVSStn",670025,0.13300000000000001,null,1157,"",3,"Y"]
["Woodside 132/11kV S Stn","Woodside132/11kVSStn",670026,7.0999999999999994E-2,null,333,"",1,"Y"]
["Woofferton 66/11kV S Stn","Woofferton66/11kVSStn",670110,0.14000000000000001,null,211,"",3,"Y"]
["Worcester 132/11kV S Stn","Worcester132/11kVSStn",670014,9.5000000000000001E-2,null,486,"",1,"Y"]
["Worfield 33/11kV S Stn","Worfield33/11kVSStn",840003,0.36,null,490,"",3,"Y"]
["Wormington 66/11kV S Stn","Wormington66/11kVSStn",670092,0.7,"Y",500,"Y",3,"Y"]
["Wribbenhall 33/11kV S Stn","Wribbenhall33/11kVSStn",770001,0.26,null,338,"",3,"Y"]
["Wrockwardine Farm 33kV S Stn","WrockwardineFarm33kVSStn",841517,0.14000000000000001,null,275,"",3,"Y"]
["Wyelands 33kV S Stn","Wyelands33kVSStn",790019,0.42599999999999999,null,443,"",3,"Y"]
["Yorkley Solar Farm 33kV S Stn","YorkleySolarFarm33kVSStn",795731,0.19,null,402,"",3,"Y"]

{"sheet":"Data-General","index":22,"n_rows":41,"n_cols":21,"rows_kept":41,"cut":false,"hidden":true,"merged":[[12,13,12,14],[6,13,6,14],[7,13,7,14],[8,13,8,14],[9,13,9,14],[10,13,10,14],[11,13,11,14]]}
["EDT Version","Format","Format Code","Location","Special","System Voltage","Soil Resistivity","U-L Soil Res Ratio","U-L Soil Res Ratio Comment","Ratio factor","HV Electrode - Ring","HV Electrode - Tail","Urban Area","Network Contribution","Contribution Factor","Cable Type","Cable Type Calculator","Cable Type Tables","1km All Cable Ground Return %","1km Line-Cable Ground Return %","LV Electrode"]
["TP21G_EDT_VERSION 2b","Unit substation in freestanding GRP or masonry housing","A","NO","NO",6600,25,"1 : 1","UNIFORM resistivity soil",1,"3600 x 2700",0,"0 to 0.74","Predominantly PILC cable network",{"$f":"1*O16","v":1.5},"3 x 1c 150mm² XLPE/EPR - 16mm² Cu wire sheaths ","3 x 1c 150mm² EPR - 16mm² Cu wire sheaths ","3 x 1c EPR / XLPE - 16mm² Cu wire sheaths",22,55,10]
[null,"Unit substation integrated within larger building","B","YES - Outdoor swimming pool, paddling pool or shower","YES - Supplies mobile phone base station on tower line",11000,50,"1 : 2","LOW above HIGH resistivity soil",2,null,10,"0.75 to 3.99","Mixed PILC & polymeric cable network",{"$f":"2*O16","v":3},"3 x 1c 150mm² XLPE/EPR - Polylam sheaths","3 x 1c 150mm² XLPE - Polylam sheaths","3 x 1c XLPE - Polylam sheaths",31,59,20]
[null,"Padmount substation","C","YES - Zoo, stable or pond/lake used for commercial fishing","YES - Supplies substation or power station operating at 20kV+",null,75,"1 : 3","LOW above HIGH resistivity soil",3,null,20,"4.00 to 12.99","Predominantly polymeric cable network",{"$f":"5*O16","v":7.5},"3 x 1c 1600mm² XLPE/EPR - 135mm² Cu wire sheaths ","3 x 1c 1600mm² XLPE - 135mm² Cu wire sheaths ","3 x 1c EPR / XLPE - 135mm² Cu wire sheaths",10,50,30]
[null,"LV Connection substation in freestanding GRP or masonry housing","E","YES - Telephone exchange","YES - Supplies ac railway or dc tramway",null,100,"1 : 4","LOW above HIGH resistivity soil",4,null,30,"13.00 or more",null,null,"3 x 1c 185mm² XLPE/EPR - 35mm² Cu wire sheaths ","3 x 1c 185mm² EPR - 35mm² Cu wire sheaths ","3 x 1c EPR / XLPE - 35mm² Cu wire sheaths",12,51,40]
[null,"LV Connection substation integrated within larger building","F","YES - Railway, tramway or metallic pipeline",null,null,150,"1 : 5","LOW above HIGH resistivity soil",5,null,40,null,null,null,"3 x 1c 185mm² XLPE/EPR - 70mm² Cu wire sheaths ","3 x 1c 185mm² XLPE - 70mm² Cu wire sheaths ","3 x 1c EPR / XLPE - 70mm² Cu wire sheaths",7,50,50]
[null,"HV Connection substation in freestanding GRP or masonry housing","G","YES - Bulk storage tank for petrol or flammable liquid",null,null,200,"1 : 6","LOW above HIGH resistivity soil",6,null,50,null,"In theory the contribution factor should be 1, 2 & 5.",null,"3 x 1c 240mm² XLPE/EPR - 16mm² Cu wire sheaths ","3 x 1c 240mm² EPR - 16mm² Cu wire sheaths ","3 x 1c EPR / XLPE - 16mm² Cu wire sheaths",22,55,75]
[null,"HV Connection substation integrated within larger building","H","YES - Steel tower/pole operating at 132kV, 275kV or 400kV",null,null,300,"1 : 7","LOW above HIGH resistivity soil",7,null,75,"0 to 749,999","However, I am concerned that these might be a little",null,"3 x 1c 240mm² XLPE/EPR - Polylam sheaths ","3 x 1c 240mm² XLPE - Polylam sheaths ","3 x 1c XLPE - Polylam sheaths",31,59,100]
[null,null,null,null,null,null,400,"1 : 8","LOW above HIGH resistivity soil",8,null,100,"750,000 to 3,999,999","optimistic. A cautious design is preferred such that the",null,"3 x 1c 300mm² XLPE/EPR - 35mm² Cu wire sheaths ","3 x 1c 300mm² EPR - 35mm² Cu wire sheaths ","3 x 1c EPR / XLPE - 35mm² Cu wire sheaths",12,51,125]
[null,null,null,null,null,null,500,"1 : 9","LOW above HIGH resistivity soil",9,null,125,"4,000,000 to 12,999,999","actual impedance is, more than likely, going to ",null,"3 x 1c 300mm² XLPE/EPR - 70mm² Cu wire sheaths ","3 x 1c 300mm² XLPE - 70mm² Cu wire sheaths ","3 x 1c EPR / XLPE - 70mm² Cu wire sheaths",7,50,150]
[null,null,null,null,null,null,750,"1 : 10","LOW above HIGH resistivity soil",10,null,150,"13,000,000 or more","better the design value so that no remedial action ",null,"3 x 1c 630mm² XLPE/EPR - 90mm² Cu wire sheaths ","3 x 1c 630mm² XLPE - 90mm² Cu wire sheaths ","3 x 1c EPR / XLPE - 90mm² Cu wire sheaths",11,51,175]
[null,null,null,null,null,null,1000,"2 : 1","HIGH above LOW resistivity soil",0.5,null,175,null,"is necessary. Therefore these values have been",null,"3 x 1c 70mm² XLPE/EPR - 12mm² Cu wire sheaths ","3 x 1c 70mm² EPR - 12mm² Cu wire sheaths ","3 x 1c EPR / XLPE - 12mm² Cu wire sheaths",28,57,200]
[null,null,null,null,null,null,null,"3 : 1","HIGH above LOW resistivity soil",0.33329999999999999,null,200,null," multiplied by the NGED precautionary factor below",null,"3 x 1c 95mm² XLPE/EPR - 35mm² Cu wire sheaths ","3 x 1c 95mm² EPR - 35mm² Cu wire sheaths ","3 x 1c EPR / XLPE - 35mm² Cu wire sheaths",12,51]
[null,null,null,null,null,null,null,"4 : 1","HIGH above LOW resistivity soil",0.25,null,null,{"$f":"IF('Data Entered'!B54=\"m2\",\"0 to 749,999\",\"0 to 0.74\")","v":"0 to 0.74"},null,null,"3c 0.04 inch² PILC","3c 0.04 inch² PILC","3c 0.04 inch² PILC",54,69]
[null,null,null,null,null,null,null,"5 : 1","HIGH above LOW resistivity soil",0.2,null,null,{"$f":"IF('Data Entered'!B54=\"m2\",\"750,000 to 3,999,999\",\"0.75 to 3.99\")","v":"0.75 to 3.99"},null,null,"3c 0.04 inch² PILCSWA ","3c 0.04 inch² PILCSWA ","3c 0.04 inch² PILCSWA",30,59]
[null,null,null,null,null,null,null,"6 : 1","HIGH above LOW resistivity soil",0.16669999999999999,null,null,{"$f":"IF('Data Entered'!B54=\"m2\",\"4,000,000 to 12,999,999\",\"4.00 to 12.99\")","v":"4.00 to 12.99"},"NGED Precautionary Factor",1.5,"3c 0.06 inch² PILC ","3c 0.06 inch² PILC ","3c 0.06 inch² PILC",51,67]
[null,null,null,null,null,null,null,"7 : 1","HIGH above LOW resistivity soil",0.1429,null,null,{"$f":"IF('Data Entered'!B54=\"m2\",\"13,000,000 or more\",\"13.00 or more\")","v":"13.00 or more"},null,null,"3c 0.06 inch² PILCSWA ","3c 0.06 inch² PILCSWA ","3c 0.06 inch² PILCSWA",25,56]
[null,null,null,null,null,null,null,"8 : 1","HIGH above LOW resistivity soil",0.125,null,null,null,null,null,"3c 0.1 inch² PILC ","3c 0.1 inch² PILC ","3c 0.1 / 0.15 inch² PILC",44,64]
[null,null,null,null,null,null,null,"9 : 1","HIGH above LOW resistivity soil",0.1111,null,null,null,null,null,"3c 0.1 inch² PILCSWA ","3c 0.1 inch² PILCSWA ","3c 0.1 / 0.15 inch² PILCSWA",22,55]
[null,null,null,null,null,null,null,"10 : 1","HIGH above LOW resistivity soil",0.1,null,null,null,null,null,"3c 0.15 inch² PILC","3c 0.15 inch² PILC","3c 0.1 / 0.15 inch² PILC",44,64]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 0.15 inch² PILCSWA ","3c 0.15 inch² PILCSWA ","3c 0.1 / 0.15 inch² PILCSWA",22,55]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 0.2 inch² PILC ","3c 0.2 inch² PILC ","3c 0.2 / 0.25 inch² PILC",37,54]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 0.2 inch² PILCSWA ","3c 0.2 inch² PILCSWA ","3c 0.2 / 0.25 inch² PILCSWA",18,54]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 0.25 inch² PILC ","3c 0.25 inch² PILC ","3c 0.2 / 0.25 inch² PILC",37,54]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 0.25 inch² PILCSWA ","3c 0.25 inch² PILCSWA ","3c 0.2 / 0.25 inch² PILCSWA",18,54]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 0.3 inch² PILC ","3c 0.3 inch² PILC ","3c 0.3 / 0.4 inch² PILC",31,53]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 0.3 inch² PILCSWA ","3c 0.3 inch² PILCSWA ","3c 0.3 / 0.4 inch² PILCSWA",16,53]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 0.4 inch² PILC ","3c 0.4 inch² PILC ","3c 0.3 / 0.4 inch² PILC",31,53]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 0.4 inch² PILCSWA ","3c 0.4 inch² PILCSWA ","3c 0.3 / 0.4 inch² PILCSWA",16,53]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 185 mm² PILC ","3c 185 mm² PILC ","3c 0.2 / 0.25 inch² PILC",37,54]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 185 mm² PILCSWA ","3c 185 mm² PILCSWA ","3c 0.2 / 0.25 inch² PILCSWA",18,54]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 185mm² PICAS ","3c 185mm² PICAS ","3c 185mm² PICAS",8,50]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 185mm² XLPE/EPR - 50mm² Cu wire sheath ","3c 185mm² XLPE - 50mm² Cu wire sheath ","3c EPR / XLPE - 50mm² Cu wire sheath",21,55]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 300 mm² PILC ","3c 300 mm² PILC ","3c 0.3 / 0.4 inch² PILC",31,53]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 300 mm² PILCSWA ","3c 300 mm² PILCSWA ","3c 0.3 / 0.4 inch² PILCSWA",16,53]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 300mm² PICAS ","3c 300mm² PICAS ","3c 300mm² PICAS",6,49]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 300mm² XLPE/EPR - 50mm² Cu wire sheath ","3c 300mm² XLPE - 50mm² Cu wire sheath ","3c EPR / XLPE - 50mm² Cu wire sheath",21,55]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 50 mm² PILC ","3c 50 mm² PILC ","3c 0.06 inch² PILC",51,67]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 50 mm² PILCSWA ","3c 50 mm² PILCSWA ","3c 0.06 inch² PILCSWA",25,56]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 95mm² PICAS ","3c 95mm² PICAS ","3c 95mm² PICAS",12,52]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3c 95mm² XLPE/EPR - 35mm² Cu wire sheath ","3c 95mm² XLPE - 35mm² Cu wire sheath ","3c EPR / XLPE - 35mm² Cu wire sheath",22,55]

{"sheet":"Data-HV Electrode Resistance","index":23,"n_rows":42,"n_cols":28,"rows_kept":42,"cut":false,"hidden":true,"merged":[[41,0,41,1],[0,16,0,27],[30,0,30,1],[33,0,33,1],[39,0,39,1],[40,0,40,1],[36,0,36,1],[37,0,37,1],[38,0,38,1],[0,1,0,3],[0,4,0,15],[31,0,31,1],[32,0,32,1],[34,0,34,1],[35,0,35,1]]}
["ROW NO","Soil Resistivity ρ",null,null,"horizontal electrode length (m)     [WITH PERIMETER ELECTRODE]",null,null,null,null,null,null,null,null,null,null,null,"horizontal electrode length (m)     [WITHOUT PERIMETER ELECTRODE]"]
[1,"Upper","Lower","U-L Ratio",0,10,20,30,40,50,75,100,125,150,175,200,0,10,20,30,40,50,75,100,125,150,175,200]
[{"$f":"A2+1","v":2},25,{"$f":"B3*D3","v":2.5},0.1,1.56,1.077,0.79700000000000004,0.63400000000000001,0.52700000000000002,0.45100000000000001,0.33200000000000002,0.26300000000000001,0.218,0.187,0.16300000000000001,0.14499999999999999,10000,2.7669999999999999,1.4410000000000001,0.97899999999999998,0.74299999999999999,0.59899999999999998,0.40500000000000003,0.307,0.247,0.20699999999999999,0.17799999999999999,0.156]
[{"$f":"A3+1","v":3},25,2.7775000000000003,0.1111,1.5760000000000001,1.089,0.80700000000000005,0.64200000000000002,0.53300000000000003,0.45600000000000002,0.33600000000000002,0.26700000000000002,0.221,0.189,0.16500000000000001,0.14699999999999999,10000,2.7810000000000001,1.4510000000000001,0.98699999999999999,0.749,0.60499999999999998,0.40899999999999997,0.31,0.25,0.20899999999999999,0.18,0.158]
[4,25,3.125,0.125,1.597,1.1040000000000001,0.81799999999999995,0.65100000000000002,0.54100000000000004,0.46300000000000002,0.34200000000000003,0.27100000000000002,0.22500000000000001,0.192,0.16800000000000001,0.14899999999999999,10000,2.7989999999999999,1.464,0.996,0.75700000000000001,0.61099999999999999,0.41399999999999998,0.314,0.253,0.21199999999999999,0.183,0.161]
[5,25,3.5724999999999998,0.1429,1.6240000000000001,1.125,0.83299999999999996,0.66200000000000003,0.55100000000000005,0.47199999999999998,0.34799999999999998,0.27600000000000002,0.23,0.19600000000000001,0.17199999999999999,0.153,10000,2.8210000000000002,1.4790000000000001,1.0089999999999999,0.76700000000000002,0.62,0.42099999999999999,0.31900000000000001,0.25800000000000001,0.216,0.187,0.16400000000000001]
[6,25,4.1674999999999995,0.16669999999999999,1.66,1.151,0.85199999999999998,0.67800000000000005,0.56399999999999995,0.48299999999999998,0.35699999999999998,0.28299999999999997,0.23499999999999999,0.20200000000000001,0.17599999999999999,0.157,10000,2.85,1.5,1.0249999999999999,0.78100000000000003,0.63200000000000001,0.43,0.32700000000000001,0.26400000000000001,0.222,0.191,0.16800000000000001]
[7,25,5,0.2,1.7070000000000001,1.1879999999999999,0.88,0.7,0.58199999999999996,0.499,0.36899999999999999,0.29299999999999998,0.24399999999999999,0.20899999999999999,0.183,0.16300000000000001,10000,2.8919999999999999,1.5309999999999999,1.05,0.80200000000000005,0.65100000000000002,0.44400000000000001,0.33800000000000002,0.27400000000000002,0.23,0.19900000000000001,0.17499999999999999]
[8,25,6.25,0.25,1.7749999999999999,1.2410000000000001,0.91900000000000004,0.73199999999999998,0.60899999999999999,0.52200000000000002,0.38700000000000001,0.308,0.25700000000000001,0.22,0.193,0.17199999999999999,10000,2.9550000000000001,1.5760000000000001,1.0860000000000001,0.83299999999999996,0.67700000000000005,0.46400000000000002,0.35499999999999998,0.28799999999999998,0.24299999999999999,0.21,0.186]
[9,25,8.3324999999999996,0.33329999999999999,1.885,1.325,0.98099999999999998,0.78200000000000003,0.65200000000000002,0.56000000000000005,0.41599999999999998,0.33200000000000002,0.27700000000000002,0.23799999999999999,0.20899999999999999,0.186,10000,3.044,1.639,1.135,0.873,0.71199999999999997,0.49,0.376,0.30599999999999999,0.25800000000000001,0.224,0.19800000000000001]
[10,25,12.5,0.5,2.0880000000000001,1.484,1.101,0.879,0.73399999999999999,0.63100000000000001,0.47099999999999997,0.377,0.316,0.27200000000000002,0.24,0.214,10000,3.234,1.78,1.2490000000000001,0.96899999999999997,0.79600000000000004,0.55500000000000005,0.42899999999999999,0.35099999999999998,0.29799999999999999,0.25900000000000001,0.23]
[11,25,25,1,2.593,1.8839999999999999,1.41,1.133,0.95199999999999996,0.82399999999999995,0.621,0.502,0.42399999999999999,0.36699999999999999,0.32500000000000001,0.29199999999999998,10000,3.6539999999999999,2.09,1.4990000000000001,1.18,0.97899999999999998,0.69599999999999995,0.54400000000000004,0.45,0.38400000000000001,0.33700000000000002,0.3]
[12,25,50,2,3.3239999999999998,2.4910000000000001,1.8939999999999999,1.54,1.3069999999999999,1.1399999999999999,0.874,0.71499999999999997,0.60899999999999999,0.53200000000000003,0.47299999999999998,0.42699999999999999,10000,4.2729999999999997,2.57,1.8939999999999999,1.52,1.2789999999999999,0.93,0.73899999999999999,0.61799999999999999,0.53300000000000003,0.47,0.42099999999999999]
[13,25,75,3,3.8439999999999999,2.9350000000000001,2.2719999999999998,1.867,1.5960000000000001,1.4019999999999999,1.087,0.89700000000000002,0.76900000000000002,0.67500000000000004,0.60299999999999998,0.54700000000000004,10000,4.7839999999999998,2.9870000000000001,2.25,1.833,1.56,1.157,0.93100000000000005,0.78500000000000003,0.68200000000000005,0.60499999999999998,0.54500000000000004]
[14,25,100,4,4.2720000000000002,3.3119999999999998,2.5830000000000002,2.1389999999999998,1.841,1.6240000000000001,1.272,1.0569999999999999,0.90900000000000003,0.80200000000000005,0.71899999999999997,0.65300000000000002,10000,5.1609999999999996,3.298,2.5169999999999999,2.069,1.7729999999999999,1.331,1.081,0.91700000000000004,0.80100000000000005,0.71299999999999997,0.64400000000000002]
[15,25,125,5,4.6120000000000001,3.6160000000000001,2.8450000000000002,2.3719999999999999,2.052,1.8180000000000001,1.4390000000000001,1.202,1.0389999999999999,0.91900000000000004,0.82599999999999996,0.752,10000,5.4930000000000003,3.5859999999999999,2.7730000000000001,2.2999999999999998,1.9830000000000001,1.504,1.2290000000000001,1.048,0.91800000000000004,0.82,0.74199999999999999]
[16,25,150,6,4.8970000000000002,3.8719999999999999,3.0830000000000002,2.5859999999999999,2.2469999999999999,1.998,1.5880000000000001,1.333,1.1559999999999999,1.0249999999999999,0.92400000000000004,0.84299999999999997,10000,5.7679999999999998,3.8239999999999998,2.9849999999999999,2.4910000000000001,2.1589999999999998,1.651,1.357,1.1619999999999999,1.0209999999999999,0.91400000000000003,0.82899999999999996]
[17,25,175,7,5.1390000000000002,4.1159999999999997,3.2879999999999998,2.7719999999999998,2.4180000000000001,2.157,1.7230000000000001,1.452,1.2629999999999999,1.123,1.014,0.92900000000000005,10000,6.0090000000000003,4.0359999999999996,3.1749999999999998,2.6640000000000001,2.3180000000000001,1.786,1.4750000000000001,1.2669999999999999,1.117,1.002,0.91100000000000003]
[18,25,200,8,5.3840000000000003,4.32,3.4710000000000001,2.9380000000000002,2.5710000000000002,2.2999999999999998,1.853,1.5669999999999999,1.3680000000000001,1.2190000000000001,1.103,1.0089999999999999,10000,6.2229999999999999,4.226,3.3460000000000001,2.8220000000000001,2.464,1.911,1.585,1.3660000000000001,1.206,1.085,0.98799999999999999]
[19,25,225,9,5.58,4.5010000000000003,3.6349999999999998,3.1,2.722,2.4409999999999998,1.97,1.671,1.462,1.3049999999999999,1.1830000000000001,1.0840000000000001,10000,6.4169999999999998,4.3979999999999997,3.5030000000000001,2.9670000000000001,2.5990000000000002,2.0270000000000001,1.6879999999999999,1.458,1.2909999999999999,1.163,1.0609999999999999]
[20,25,250,10,5.7560000000000002,4.665,3.8,3.242,2.8540000000000001,2.5649999999999999,2.0779999999999998,1.768,1.554,1.39,1.262,1.1579999999999999,10000,6.5919999999999996,4.5570000000000004,3.6480000000000001,3.101,2.7250000000000001,2.137,1.7849999999999999,1.5469999999999999,1.3720000000000001,1.2370000000000001,1.131]
[null,null,"COL NO",1,{"$f":"D22+1","v":2},3,4,5,6,7,8,9,10,11,12,13,{"$f":"P22+1","v":14},{"$f":"Q22+1","v":15},{"$f":"R22+1","v":16},{"$f":"S22+1","v":17},{"$f":"T22+1","v":18},{"$f":"U22+1","v":19},{"$f":"V22+1","v":20},{"$f":"W22+1","v":21},{"$f":"X22+1","v":22},{"$f":"Y22+1","v":23},{"$f":"Z22+1","v":24},{"$f":"AA22+1","v":25}]
[]
[null,"U-L Ratio",0,10,20,30,40,50,75,100,125,150,175,200]
["COL NO",1,{"$f":"B25+1","v":2},3,4,5,6,7,8,9,10,11,12,13]
[]
[null,"U-L Ratio",0.1,0.1111,0.125,0.1429,0.16669999999999999,0.2,0.25,0.33329999999999999,0.5,1,2,3,4,5,6,7,8,9,10]
["ROW NO",1,{"$f":"B28+1","v":2},{"$f":"C28+1","v":3},4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20]
[]
[]
["Perimeter electrode",null,{"$f":"IF('Data Entered'!D71=\"Required\",\"YES\",\"NO\")","v":"NO"}]
["Electrode length",null,{"$f":"'Data Entered'!B72","v":0}]
["COL NO",null,{"$f":"HLOOKUP(C32,B24:N25,2,FALSE)","v":2}]
["COL NO Corrected",null,{"$f":"IF(C31=\"YES\",C33,C33+12)","v":14}]
["Upper resistivity",null,{"$f":"'Data Entered'!B67","v":300}]
["Lower resistivity",null,{"$f":"'Data Entered'!D69","v":900}]
["U-L ratio",null,{"$f":"'Data Entered'!B69","v":3}]
["ROW NO",null,{"$f":"HLOOKUP(C37,B27:U28,2,FALSE)","v":13}]
["RESISTANCE",null,{"$f":"INDEX(D2:AB21,C38,C34)","v":10000},"Ω"]
["Insulated 1st section",null,{"$f":"IF(OR('Data Entered'!E10=\"B\",'Data Entered'!E10=\"F\"),\"YES\",\"NO\")","v":"NO"}]
["1st section resistance",null,6.7000000000000004E-2,"Ω","Equivalent to 250m of 70mm2 insulated conductor for 'integrated within larger building' type substations"]
["TOTAL RESISTANCE",null,{"$f":"IF(C40=\"YES\",C39+C41,C39)","v":10000},"Ω"]

{"sheet":"Data-LV Electrode Resistance","index":24,"n_rows":40,"n_cols":21,"rows_kept":40,"cut":false,"hidden":true,"merged":[[33,0,33,1],[0,1,0,3],[0,4,0,14],[30,0,30,1],[31,0,31,1],[32,0,32,1],[37,0,37,1],[38,0,38,1],[39,0,39,1],[34,0,34,1],[35,0,35,1],[36,0,36,1]]}
["ROW NO","Soil Resistivity ρ",null,null,"horizontal electrode length (m)"]
[1,"Upper","Lower","U-L Ratio",10,20,30,40,50,75,100,125,150,175,200]
[{"$f":"A2+1","v":2},25,{"$f":"B3*D3","v":2.5},0.1,2.7669999999999999,1.4410000000000001,0.97899999999999998,0.74299999999999999,0.59899999999999998,0.40500000000000003,0.307,0.247,0.20699999999999999,0.17799999999999999,0.156]
[{"$f":"A3+1","v":3},25,2.7775000000000003,0.1111,2.7810000000000001,1.4510000000000001,0.98699999999999999,0.749,0.60499999999999998,0.40899999999999997,0.31,0.25,0.20899999999999999,0.18,0.158]
[4,25,3.125,0.125,2.7989999999999999,1.464,0.996,0.75700000000000001,0.61099999999999999,0.41399999999999998,0.314,0.253,0.21199999999999999,0.183,0.161]
[5,25,3.5724999999999998,0.1429,2.8210000000000002,1.4790000000000001,1.0089999999999999,0.76700000000000002,0.62,0.42099999999999999,0.31900000000000001,0.25800000000000001,0.216,0.187,0.16400000000000001]
[6,25,4.1674999999999995,0.16669999999999999,2.85,1.5,1.0249999999999999,0.78100000000000003,0.63200000000000001,0.43,0.32700000000000001,0.26400000000000001,0.222,0.191,0.16800000000000001]
[7,25,5,0.2,2.8919999999999999,1.5309999999999999,1.05,0.80200000000000005,0.65100000000000002,0.44400000000000001,0.33800000000000002,0.27400000000000002,0.23,0.19900000000000001,0.17499999999999999]
[8,25,6.25,0.25,2.9550000000000001,1.5760000000000001,1.0860000000000001,0.83299999999999996,0.67700000000000005,0.46400000000000002,0.35499999999999998,0.28799999999999998,0.24299999999999999,0.21,0.186]
[9,25,8.3324999999999996,0.33329999999999999,3.044,1.639,1.135,0.873,0.71199999999999997,0.49,0.376,0.30599999999999999,0.25800000000000001,0.224,0.19800000000000001]
[10,25,12.5,0.5,3.234,1.78,1.2490000000000001,0.96899999999999997,0.79600000000000004,0.55500000000000005,0.42899999999999999,0.35099999999999998,0.29799999999999999,0.25900000000000001,0.23]
[11,25,25,1,3.6539999999999999,2.09,1.4990000000000001,1.18,0.97899999999999998,0.69599999999999995,0.54400000000000004,0.45,0.38400000000000001,0.33700000000000002,0.3]
[12,25,50,2,4.2729999999999997,2.57,1.8939999999999999,1.52,1.2789999999999999,0.93,0.73899999999999999,0.61799999999999999,0.53300000000000003,0.47,0.42099999999999999]
[13,25,75,3,4.7839999999999998,2.9870000000000001,2.25,1.833,1.56,1.157,0.93100000000000005,0.78500000000000003,0.68200000000000005,0.60499999999999998,0.54500000000000004]
[14,25,100,4,5.1609999999999996,3.298,2.5169999999999999,2.069,1.7729999999999999,1.331,1.081,0.91700000000000004,0.80100000000000005,0.71299999999999997,0.64400000000000002]
[15,25,125,5,5.4930000000000003,3.5859999999999999,2.7730000000000001,2.2999999999999998,1.9830000000000001,1.504,1.2290000000000001,1.048,0.91800000000000004,0.82,0.74199999999999999]
[16,25,150,6,5.7679999999999998,3.8239999999999998,2.9849999999999999,2.4910000000000001,2.1589999999999998,1.651,1.357,1.1619999999999999,1.0209999999999999,0.91400000000000003,0.82899999999999996]
[17,25,175,7,6.0090000000000003,4.0359999999999996,3.1749999999999998,2.6640000000000001,2.3180000000000001,1.786,1.4750000000000001,1.2669999999999999,1.117,1.002,0.91100000000000003]
[18,25,200,8,6.2229999999999999,4.226,3.3460000000000001,2.8220000000000001,2.464,1.911,1.585,1.3660000000000001,1.206,1.085,0.98799999999999999]
[19,25,225,9,6.4169999999999998,4.3979999999999997,3.5030000000000001,2.9670000000000001,2.5990000000000002,2.0270000000000001,1.6879999999999999,1.458,1.2909999999999999,1.163,1.0609999999999999]
[20,25,250,10,6.5919999999999996,4.5570000000000004,3.6480000000000001,3.101,2.7250000000000001,2.137,1.7849999999999999,1.5469999999999999,1.3720000000000001,1.2370000000000001,1.131]
[null,null,"COL NO",1,{"$f":"D22+1","v":2},3,4,5,6,7,8,9,10,11,12]
[]
[null,"U-L Ratio",10,20,30,40,50,75,100,125,150,175,200]
["COL NO",1,{"$f":"B25+1","v":2},3,4,5,6,7,8,9,10,11,12]
[]
[null,"U-L Ratio",0.1,0.1111,0.125,0.1429,0.16669999999999999,0.2,0.25,0.33329999999999999,0.5,1,2,3,4,5,6,7,8,9,10]
["ROW NO",1,{"$f":"B28+1","v":2},{"$f":"C28+1","v":3},4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20]
[]
[]
["Electrode length",null,{"$f":"'Data Entered'!B146","v":0}]
["COL NO",null,{"$f":"IF(ISNA(HLOOKUP(C31,B24:M25,2,FALSE)),12,HLOOKUP(C31,B24:M25,2,FALSE))","v":12}]
["Upper resistivity",null,{"$f":"'Data Entered'!B67","v":300}]
["Lower resistivity",null,{"$f":"'Data Entered'!D69","v":900}]
["U-L ratio",null,{"$f":"'Data Entered'!B69","v":3}]
["ROW NO",null,{"$f":"HLOOKUP(C35,B27:U28,2,FALSE)","v":13}]
["RESISTANCE",null,{"$f":"INDEX(D2:O21,C36,C32)","v":0.54500000000000004},"Ω"]
["Insulated 1st Section",null,"YES"]
["1st section resistance",null,{"$f":"IF(OR('Data Entered'!E10=\"B\",'Data Entered'!E10=\"F\"),0.067,0.027)","v":2.7E-2},"Ω","Equivalent to 100m or 250m of 70mm2 insulated conductor for 'GRP/masonry/padmount' & 'integrated within larger building' type substations respectively"]
["TOTAL RESISTANCE",null,{"$f":"C37+C39","v":0.57200000000000006},"Ω"]

{"sheet":"Data-Network Contribution","index":25,"n_rows":31,"n_cols":13,"rows_kept":31,"cut":false,"hidden":true,"merged":[[30,1,30,2],[24,1,24,2],[25,1,25,2],[26,1,26,2],[27,1,27,2],[28,1,28,2],[29,1,29,2]]}
["ROW NO"]
[1,"Soil Resistivity ρ","0 to 0.74","0.75 to 3.99","4.00 to 12.99","13.00 or more"]
[2,25,10,0.08,7.0000000000000007E-2,7.0000000000000007E-2]
[3,50,10,0.08,7.0000000000000007E-2,7.0000000000000007E-2]
[4,75,10,0.13,0.1,0.1]
[5,100,10,0.13,0.1,0.1]
[6,150,10,0.34,0.21,0.17]
[7,200,10,0.34,0.21,0.17]
[8,300,10,0.34,0.21,0.17]
[9,400,10,0.55000000000000004,0.33,0.23]
[10,500,10,0.55000000000000004,0.33,0.23]
[11,750,10,1.08,0.59,0.4]
[12,1000,10,1.08,0.59,0.4]
["COL NO",1,{"$f":"B14+1","v":2},{"$f":"C14+1","v":3},{"$f":"D14+1","v":4},{"$f":"E14+1","v":5}]
[]
[]
[null,"Urban Area","0 to 0.74","0.75 to 3.99","4.00 to 12.99","13.00 or more"]
["COL NO",1,{"$f":"B18+1","v":2},{"$f":"C18+1","v":3},{"$f":"D18+1","v":4},{"$f":"E18+1","v":5}]
[]
[]
[null,"Soil Resistivity ρ",25,50,75,100,150,200,300,400,500,750,1000]
["ROW NO",1,{"$f":"B22+1","v":2},3,4,5,6,7,8,9,10,11,12]
[]
[]
[null,"Urban Area",null,{"$f":"'Data Entered'!F54","v":"13.00 or more"}]
[null,"COL NO",null,{"$f":"IF(ISNA(HLOOKUP(D25,B17:F18,2,FALSE)),2,HLOOKUP(D25,B17:F18,2,FALSE))","v":5}]
[null,"Soil Resistivity",null,{"$f":"'Data Entered'!B67","v":300}]
[null,"ROW NO",null,{"$f":"IF(ISNA(HLOOKUP(D27,B21:M22,2,FALSE)),12,HLOOKUP(D27,B21:M22,2,FALSE))","v":8}]
[null,"Basic Network Contribution",null,{"$f":"INDEX(B2:F13,D28,D26)","v":0.17}]
[null,"Contribution Factor",null,{"$f":"IF(ISNA(VLOOKUP('Data Entered'!B56,'Data-General'!N2:O4,2,FALSE)),5,VLOOKUP('Data Entered'!B56,'Data-General'!N2:O4,2,FALSE))","v":5}]
[null,"Actual Network Contribution",null,{"$f":"IF(D25=\"0 to 4 km2\",D29,D29*D30)","v":0.85000000000000009}]

{"sheet":"Data-HV to LV Separation SNE","index":26,"n_rows":51,"n_cols":32,"rows_kept":51,"cut":false,"hidden":true,"merged":[[34,0,34,1],[0,2,0,21],[30,0,30,1],[31,0,31,1],[32,0,32,1],[33,0,33,1],[50,0,50,2],[35,0,35,1],[36,0,36,2],[37,0,37,1],[40,0,40,1],[41,0,41,1],[42,0,42,1],[43,0,43,1],[44,0,44,1],[45,0,45,1],[46,0,46,2],[47,0,47,1]]}
["ROW NO","Soil","EPR(V) + Clearance Time(s)"]
[1,"U-L Ratio",500.5,501,501.5,502,503,{"$f":"C2+500","v":1000.5},1001,1001.5,1002,1003,1500.5,1501,1501.5,1502,1503,2000.5,2001,2001.5,2002,2003,2500.5,2501,2501.5,2502,2503,3000.5,3001,3001.5,3002,3003]
[{"$f":"A2+1","v":2},0.1,3,3,3,3,3,3,4,4,4,4,3,4,6,6,6,3,6,8,8,8,4,8,10,10,10,4,8,10,12,12]
[{"$f":"A3+1","v":3},0.1111,3,3,3,3,3,3,4,4,4,4,3,4,6,6,6,3,6,8,8,8,4,8,10,10,10,4,8,10,12,12]
[4,0.125,3,3,3,3,3,3,4,4,4,4,3,4,6,6,6,3,6,8,8,8,4,8,10,10,10,4,8,10,12,12]
[5,0.1429,3,3,3,3,3,3,4,4,4,4,3,4,6,6,6,3,6,8,8,8,4,8,10,10,10,4,8,10,12,12]
[6,0.16669999999999999,3,3,3,3,3,3,4,4,4,4,3,4,6,6,6,3,6,8,8,8,4,8,10,10,10,4,8,10,12,12]
[7,0.2,3,3,3,3,3,3,4,4,4,4,3,4,6,6,6,3,6,8,8,8,4,8,10,10,10,4,8,10,12,12]
[8,0.25,3,3,3,3,3,3,4,4,4,4,3,4,6,6,6,3,6,8,8,8,4,8,10,10,10,4,8,10,12,12]
[9,0.33329999999999999,3,3,3,3,3,3,4,4,4,4,3,4,6,6,6,3,6,8,8,8,4,8,10,10,10,4,8,10,12,12]
[10,0.5,3,3,3,3,3,3,4,4,6,6,3,6,8,8,8,3,8,10,10,12,4,10,12,14,14,4,12,14,16,18]
[11,1,3,3,4,4,4,3,6,8,8,8,4,10,12,12,14,4,12,16,18,18,6,16,20,22,24,8,20,24,26,28]
[12,2,3,4,4,6,6,3,8,12,12,14,4,14,18,20,22,6,20,24,26,28,8,24,30,34,36,12,30,38,40,44]
[13,3,3,4,6,6,8,3,12,14,16,18,6,18,24,26,28,8,26,32,34,36,12,32,40,44,46,14,38,48,60,60]
[14,4,3,4,6,8,8,3,14,18,20,20,6,22,28,30,32,10,30,38,42,44,14,38,48,60,60,16,46,60,70,70]
[15,5,3,6,8,8,10,4,16,20,22,24,8,26,32,34,38,12,34,44,48,50,16,44,60,60,70,20,60,70,80,80]
[16,6,3,6,8,10,10,4,16,22,24,26,8,28,36,38,42,12,38,48,60,60,16,50,70,70,80,22,60,80,90,90]
[17,7,3,6,10,10,12,4,18,24,26,28,8,30,40,42,46,14,42,60,60,70,18,60,70,80,80,24,70,90,90,100]
[18,8,3,6,10,12,12,4,20,26,30,32,10,34,42,46,50,14,46,60,70,70,20,60,80,90,90,26,80,90,100,110]
[19,9,3,8,10,12,14,4,22,28,32,34,10,36,46,50,60,16,50,70,70,80,22,70,80,90,100,28,80,100,110,120]
[20,10,3,8,10,12,14,4,22,30,34,36,10,38,50,60,60,16,60,70,80,80,22,70,90,100,110,30,90,110,120,130]
["COL NO",1,{"$f":"B22+1","v":2},3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31]
[]
[null,"U-L Ratio",500.5,501,501.5,502,503,1000.5,1001,1001.5,1002,1003,1500.5,1501,1501.5,1502,1503,2000.5,2001,2001.5,2002,2003,2500.5,2501,2501.5,2502,2503,3000.5,3001,3001.5,3002,3003]
["COL NO",1,{"$f":"B25+1","v":2},{"$f":"C25+1","v":3},4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31]
[]
[null,"U-L Ratio",0.1,0.1111,0.125,0.1429,0.16669999999999999,0.2,0.25,0.33329999999999999,0.5,1,2,3,4,5,6,7,8,9,10]
["ROW NO",1,{"$f":"B28+1","v":2},{"$f":"C28+1","v":3},4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20]
[]
[]
["EPR",null,{"$f":"IF('Data Entered'!B87<=500,500,IF('Data Entered'!B87<=1000,1000,IF('Data Entered'!B87<=1500,1500,IF('Data Entered'!B87<=2000,2000,IF('Data Entered'!B87<=2500,2500,3000)))))","v":3000}]
["Fault Clearance",null,{"$f":"IF('Design Input'!B361<=0.5,0.5,IF('Design Input'!B361<=1,1,IF('Design Input'!B361<=1.5,1.5,IF('Design Input'!B361<=2,2,3))))","v":3}]
["Sum",null,{"$f":"C31+C32","v":3003}]
["COL NO",null,{"$f":"HLOOKUP(C33,B24:AF25,2,FALSE)","v":31}]
["U-L ratio",null,{"$f":"'Data Entered'!B69","v":3}]
["ROW NO",null,{"$f":"HLOOKUP(C35,B27:U28,2,FALSE)","v":13}]
["High EPR?",null,null,{"$f":"IF('Data Entered'!B127=\"HEPR\",\"YES\",\"NO\")","v":"YES"}]
["Distance",null,{"$f":"IF(D37=\"NO\",0,INDEX(B2:AF21,C36,C34))","v":60},"m"]
[]
[]
["Transfer Voltage",null,{"$f":"IF(ISNA('Data Entered'!F140),3000,IF('Data Entered'!F140<=500,500,IF('Data Entered'!F140<=1000,1000,IF('Data Entered'!F140<=1500,1500,IF('Data Entered'!F140<=2000,2000,IF('Data Entered'!F140<=2500,2500,3000))))))","v":500}]
["Fault Clearance",null,{"$f":"IF('Design Input'!B90<=0.5,0.5,IF('Design Input'!B90<=1,1,IF('Design Input'!B90<=1.5,1.5,IF('Design Input'!B90<=2,2,3))))","v":3}]
["Sum",null,{"$f":"C41+C42","v":503}]
["COL NO",null,{"$f":"HLOOKUP(C43,B24:AF25,2,FALSE)","v":6}]
["U-L ratio",null,{"$f":"'Data Entered'!B69","v":3}]
["ROW NO",null,{"$f":"HLOOKUP(C45,B27:U28,2,FALSE)","v":13}]
["High EPR & Cable Connected?",null,null,{"$f":"IF(OR(ISNA('Data Entered'!B48),ISNA('Data Entered'!B137)),\"NO\",IF(AND('Data Entered'!B48=\"YES\",'Data Entered'!B137=\"HEPR\"),\"YES\",\"NO\"))","v":"NO"}]
["Distance",null,{"$f":"IF(D47=\"NO\",0,INDEX(B2:AF21,C46,C44))","v":0},"m"]
[]
[]
["HV Separation Distance",null,null,{"$f":"MAX(C38,C48)","v":60},"m"]

{"sheet":"Data-HV to LV Separation CNE","index":27,"n_rows":51,"n_cols":32,"rows_kept":51,"cut":false,"hidden":true,"merged":[[34,0,34,1],[0,2,0,21],[30,0,30,1],[31,0,31,1],[32,0,32,1],[33,0,33,1],[50,0,50,2],[35,0,35,1],[36,0,36,2],[37,0,37,1],[40,0,40,1],[41,0,41,1],[42,0,42,1],[43,0,43,1],[44,0,44,1],[45,0,45,1],[46,0,46,2],[47,0,47,1]]}
["ROW NO","Soil","EPR(V) + Clearance Time(s)"]
[1,"U-L Ratio",500.5,501,501.5,502,503,{"$f":"C2+500","v":1000.5},1001,1001.5,1002,1003,1500.5,1501,1501.5,1502,1503,2000.5,2001,2001.5,2002,2003,2500.5,2501,2501.5,2502,2503,3000.5,3001,3001.5,3002,3003]
[{"$f":"A2+1","v":2},0.1,3,3,3,3,3,3,3,3,3,3,3,3,3,4,4,3,4,4,4,4,3,4,4,6,6,3,4,6,6,6]
[{"$f":"A3+1","v":3},0.1111,3,3,3,3,3,3,3,3,3,3,3,3,3,4,4,3,4,4,4,4,3,4,4,6,6,3,4,6,6,6]
[4,0.125,3,3,3,3,3,3,3,3,3,3,3,3,3,4,4,3,4,4,4,4,3,4,4,6,6,3,4,6,6,6]
[5,0.1429,3,3,3,3,3,3,3,3,3,3,3,3,3,4,4,3,4,4,4,4,3,4,4,6,6,3,4,6,6,6]
[6,0.16669999999999999,3,3,3,3,3,3,3,3,3,3,3,3,3,4,4,3,4,4,4,4,3,4,4,6,6,3,4,6,6,6]
[7,0.2,3,3,3,3,3,3,3,3,3,3,3,3,3,4,4,3,4,4,4,4,3,4,4,6,6,3,4,6,6,6]
[8,0.25,3,3,3,3,3,3,3,3,3,3,3,3,3,4,4,3,4,4,4,4,3,4,4,6,6,3,4,6,6,6]
[9,0.33329999999999999,3,3,3,3,3,3,3,3,3,3,3,3,3,4,4,3,4,4,4,4,3,4,4,6,6,3,4,6,6,6]
[10,0.5,3,3,3,3,3,3,3,3,3,3,3,3,4,4,4,3,4,4,6,6,3,4,6,6,8,3,6,8,8,8]
[11,1,3,3,3,3,3,3,3,4,4,4,3,4,6,6,6,3,6,8,8,8,3,8,10,10,12,4,10,12,12,14]
[12,2,3,3,3,3,3,3,4,4,6,6,3,6,8,8,10,3,8,12,12,14,4,12,14,16,18,4,14,18,20,22]
[13,3,3,3,3,3,3,3,4,6,6,8,3,8,10,12,12,3,12,14,16,18,4,14,18,20,22,6,18,24,26,28]
[14,4,3,3,3,3,3,3,4,6,8,8,3,8,12,14,14,3,14,18,20,20,4,18,22,24,26,6,22,28,30,32]
[15,5,3,3,3,3,3,3,6,8,8,10,3,10,14,16,16,4,16,20,22,24,6,20,26,28,30,8,24,32,34,38]
[16,6,3,3,3,3,3,3,6,8,10,10,3,12,16,18,18,4,16,22,24,26,6,22,28,32,34,8,28,36,40,42]
[17,7,3,3,3,3,3,3,6,10,10,12,3,12,16,18,20,4,18,24,26,30,6,24,32,36,38,8,30,40,44,46]
[18,8,3,3,3,3,4,3,6,10,12,12,3,14,18,20,22,4,20,26,30,32,6,26,34,38,42,10,34,42,46,50]
[19,9,3,3,3,3,4,3,6,10,12,14,3,14,20,22,24,4,22,28,32,34,8,28,38,40,44,10,36,46,50,60]
[20,10,3,3,3,3,4,3,8,10,12,14,3,14,20,24,26,4,22,30,34,36,8,30,40,44,48,10,38,50,60,60]
["COL NO",1,{"$f":"B22+1","v":2},3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31]
[]
[null,"U-L Ratio",500.5,501,501.5,502,503,1000.5,1001,1001.5,1002,1003,1500.5,1501,1501.5,1502,1503,2000.5,2001,2001.5,2002,2003,2500.5,2501,2501.5,2502,2503,3000.5,3001,3001.5,3002,3003]
["COL NO",1,{"$f":"B25+1","v":2},{"$f":"C25+1","v":3},4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31]
[]
[null,"U-L Ratio",0.1,0.1111,0.125,0.1429,0.16669999999999999,0.2,0.25,0.33329999999999999,0.5,1,2,3,4,5,6,7,8,9,10]
["ROW NO",1,{"$f":"B28+1","v":2},{"$f":"C28+1","v":3},4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20]
[]
[]
["EPR",null,{"$f":"IF(ISNA('Data Entered'!B87),3000,IF('Data Entered'!B87<=500,500,IF('Data Entered'!B87<=1000,1000,IF('Data Entered'!B87<=1500,1500,IF('Data Entered'!B87<=2000,2000,IF('Data Entered'!B87<=2500,2500,3000))))))","v":3000}]
["Fault Clearance",null,{"$f":"IF('Design Input'!B361<=0.5,0.5,IF('Design Input'!B361<=1,1,IF('Design Input'!B361<=1.5,1.5,IF('Design Input'!B361<=2,2,3))))","v":3}]
["Sum",null,{"$f":"C31+C32","v":3003}]
["COL NO",null,{"$f":"HLOOKUP(C33,B24:AF25,2,FALSE)","v":31}]
["U-L ratio",null,{"$f":"'Data Entered'!B69","v":3}]
["ROW NO",null,{"$f":"HLOOKUP(C35,B27:U28,2,FALSE)","v":13}]
["High EPR?",null,null,{"$f":"IF('Data Entered'!B127=\"HEPR\",\"YES\",\"NO\")","v":"YES"}]
["Distance",null,{"$f":"IF(D37=\"NO\",0,INDEX(B2:AF21,C36,C34))","v":28},"m"]
[]
[]
["Transfer Voltage",null,{"$f":"IF(ISNA('Data Entered'!F140),3000,IF('Data Entered'!F140<=500,500,IF('Data Entered'!F140<=1000,1000,IF('Data Entered'!F140<=1500,1500,IF('Data Entered'!F140<=2000,2000,IF('Data Entered'!F140<=2500,2500,3000))))))","v":500}]
["Fault Clearance",null,{"$f":"IF('Design Input'!B90<=0.5,0.5,IF('Design Input'!B90<=1,1,IF('Design Input'!B90<=1.5,1.5,IF('Design Input'!B90<=2,2,3))))","v":3}]
["Sum",null,{"$f":"C41+C42","v":503}]
["COL NO",null,{"$f":"HLOOKUP(C43,B24:AF25,2,FALSE)","v":6}]
["U-L ratio",null,{"$f":"'Data Entered'!B69","v":3}]
["ROW NO",null,{"$f":"HLOOKUP(C45,B27:U28,2,FALSE)","v":13}]
["High EPR & Cable Connected?",null,null,{"$f":"IF(OR(ISNA('Data Entered'!B48),ISNA('Data Entered'!B137)),\"NO\",IF(AND('Data Entered'!B48=\"YES\",'Data Entered'!B137=\"HEPR\"),\"YES\",\"NO\"))","v":"NO"}]
["Distance",null,{"$f":"IF(D47=\"NO\",0,INDEX(B2:AF21,C46,C44))","v":0},"m"]
[]
[]
["HV Separation Distance",null,null,{"$f":"MAX(C38,C48)","v":28},"m"]

{"sheet":"Data-Safety Voltages","index":28,"n_rows":51,"n_cols":22,"rows_kept":51,"cut":false,"hidden":true,"merged":[[33,1,33,2],[35,1,35,2],[43,1,43,2],[45,1,45,2]]}
["ROW NO"]
[1,"Standard Fault Clearance Time (s)","Soil or outdoor concrete","75mm chippings","Indoor concrete","100mm tarmac"]
[{"$f":"A2+1","v":2},0.1,2070,2341,2728,13579]
[{"$f":"A3+1","v":3},0.15,1808,2043,2379,11761]
[4,0.2,1570,1773,2064,10202]
[5,0.3,1179,1331,1548,7622]
[6,0.4,837,944,1095,5376]
[7,0.5,578,650,753,3656]
[8,0.6,420,471,544,2614]
[9,0.7,332,371,428,2012]
[10,0.8,281,314,361,1710]
[11,0.9,250,279,321,1523]
[12,1,233,259,298,1376]
[13,1.1000000000000001,219,244,280,1288]
[14,1.2,209,232,266,1220]
[15,1.3,200,223,255,1167]
[16,1.4,193,215,246,1117]
[17,1.5,188,209,239,1191]
[18,2,173,192,220,992]
[19,3,162,180,205,919]
[20,5,156,173,198,897]
[21,60,153,170,194,884]
["COL NO",1,{"$f":"B23+1","v":2},{"$f":"C23+1","v":3},{"$f":"D23+1","v":4},{"$f":"E23+1","v":5}]
[]
[]
[null,"Standard Fault Clearance Time (s)","Soil or outdoor concrete","75mm chippings","Indoor concrete","100mm tarmac"]
["COL NO",1,{"$f":"B27+1","v":2},{"$f":"C27+1","v":3},{"$f":"D27+1","v":4},{"$f":"E27+1","v":5}]
[]
[]
[null,"Standard Fault Clearance Time (s)",0.1,0.15,0.2,0.3,0.4,0.5,0.6,0.7,0.8,0.9,1,1.1000000000000001,1.2,1.3,1.4,1.5,2,3,5,60]
["ROW NO",1,{"$f":"B31+1","v":2},{"$f":"C31+1","v":3},4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21]
[]
[]
[null,"HV fault clearance time",null,{"$f":"'Design Input'!B361","v":3.4},"s"]
[null,"Nearest standard fault clearance time",null,{"$f":"INDEX(B3:B22,MATCH(D34,B3:B22,1)+1)","v":5},"s"]
[null,"ROW NO",null,{"$f":"HLOOKUP(D35,B30:V31,2,FALSE)","v":20}]
[null,null,"COL NO","HV Safety Voltage"]
[null,"Soil or outdoor concrete",{"$f":"HLOOKUP(B38,B26:F27,2,FALSE)","v":2},{"$f":"INDEX(B2:F22,D36,C38)","v":156}]
[null,"75mm chippings",{"$f":"HLOOKUP(B39,B26:F27,2,FALSE)","v":3},{"$f":"INDEX(B2:F22,D36,C39)","v":173}]
[null,"Indoor concrete",{"$f":"HLOOKUP(B40,B26:F27,2,FALSE)","v":4},{"$f":"INDEX(B2:F22,D36,C40)","v":198}]
[null,"100mm tarmac",{"$f":"HLOOKUP(B41,B26:F27,2,FALSE)","v":5},{"$f":"INDEX(B2:F22,D36,C41)","v":897}]
[]
[]
[null,"EHV fault clearance time",null,{"$f":"'Data Entered'!F23","v":3.4},"s"]
[null,"Nearest standard fault clearance time",null,{"$f":"INDEX(B3:B22,MATCH(D44,B3:B22,1)+1)","v":5},"s"]
[null,"ROW NO",null,{"$f":"HLOOKUP(D45,B30:V31,2,FALSE)","v":20}]
[null,null,"COL NO","EHV Safety Voltage"]
[null,"Soil or outdoor concrete",{"$f":"HLOOKUP(B48,B26:F27,2,FALSE)","v":2},{"$f":"INDEX(B2:F22,D46,C48)","v":156}]
[null,"75mm chippings",{"$f":"HLOOKUP(B49,B26:F27,2,FALSE)","v":3},{"$f":"INDEX(B2:F22,D46,C49)","v":173}]
[null,"Indoor concrete",{"$f":"HLOOKUP(B50,B26:F27,2,FALSE)","v":4},{"$f":"INDEX(B2:F22,D46,C50)","v":198}]
[null,"100mm tarmac",{"$f":"HLOOKUP(B51,B26:F27,2,FALSE)","v":5},{"$f":"INDEX(B2:F22,D46,C51)","v":897}]

{"sheet":"Transfer Potential Default","index":29,"n_rows":60,"n_cols":20,"rows_kept":60,"cut":false,"hidden":true,"merged":[[1,12,1,19],[1,11,2,11],[1,1,2,1],[1,2,2,2],[1,3,1,7]]}
["COL",1,{"$f":"B1+1","v":2},{"$f":"C1+1","v":3},4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19]
[null,"Cable","Formula Available","Cable Sheath Self Impedance Per km [Z1]",null,null,null,null,null,"[A]",null,"Transfer Voltage","GMSUB Earth Resistance"]
["ROW",null,null,"Mod","Arg","Real","Imag","Complex","L*Z1","(L*Z1)+Z2","[Z2]/[A]",null,"≤0.25Ω","≤0.5Ω","≤1Ω","≤2Ω","≤4Ω","≤5Ω","≤10Ω","≤20Ω"]
[1,"3 x 1c 150mm² XLPE/EPR - 16mm² Cu wire sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.26*($C$50^-0.909)>1,1,0.26*($C$50^-0.909))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.4307*($C$50^-0.83)>1,1,0.4307*($C$50^-0.83))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.6308*($C$50^-0.702)>1,1,0.6308*($C$50^-0.702))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.229*LN($C$50)+0.7663>1,1,-0.229*LN($C$50)+0.7663)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0025*($C$50^2)-0.0868*$C$50+0.9685>1,1,0.0025*($C$50^2)-0.0868*$C$50+0.9685)","v":0.96850000000000003},{"$f":"IF(0.002*($C$50^2)-0.0765*$C$50+0.9839>1,1,0.002*($C$50^2)-0.0765*$C$50+0.9839)","v":0.9839},{"$f":"IF(0.0008*($C$50^2)-0.0444*$C$50+1.002>1,1,0.0008*($C$50^2)-0.0444*$C$50+1.002)","v":1},{"$f":"IF(0.0002*($C$50^2)-0.0221*$C$50+1.0018>1,1,0.0002*($C$50^2)-0.0221*$C$50+1.0018)","v":1}]
[{"$f":"A4+1","v":2},"3 x 1c 150mm² XLPE/EPR - Polylam sheaths","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2226*($C$50^-0.907)>1,1,0.2226*($C$50^-0.907))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3735*($C$50^-0.835)>1,1,0.3735*($C$50^-0.835))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5607*($C$50^-0.721)>1,1,0.5607*($C$50^-0.721))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.22*LN($C$50)+0.7059>1,1,-0.22*LN($C$50)+0.7059)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0028*($C$50^2)-0.093*$C$50+0.9284>1,1,0.0028*($C$50^2)-0.093*$C$50+0.9284)","v":0.9284},{"$f":"IF(0.0025*($C$50^2)-0.0849*$C$50+0.952>1,1,0.0025*($C$50^2)-0.0849*$C$50+0.952)","v":0.95199999999999996},{"$f":"IF(0.0013*($C$50^2)-0.0556*$C$50+0.9903>1,1,0.0013*($C$50^2)-0.0556*$C$50+0.9903)","v":0.99029999999999996},{"$f":"IF(0.0005*($C$50^2)-0.0308*$C$50+0.9993>1,1,0.0005*($C$50^2)-0.0308*$C$50+0.9993)","v":0.99929999999999997}]
[{"$f":"A5+1","v":3},"3 x 1c 1600mm² XLPE/EPR - 135mm² Cu wire sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.388*($C$50^-0.902)>1,1,0.388*($C$50^-0.902))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.6103*($C$50^-0.794)>1,1,0.6103*($C$50^-0.794))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.8276*($C$50^-0.629)>1,1,0.8276*($C$50^-0.6293))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.003*($C$50^2)-0.1004*$C$50+1.01>1,1,0.003*($C$50^2)-0.1004*$C$50+1.01)","v":1},{"$f":"IF(0.0011*($C$50^2)-0.0576*$C$50+1.0306>1,1,0.0011*($C$50^2)-0.0576*$C$50+1.0306)","v":1},{"$f":"IF(0.0006*($C$50^2)-0.0443*$C$50+1.0259>1,1,0.0006*($C$50^2)-0.0443*$C$50+1.0259)","v":1},{"$f":"IF(-0.0187*$C$50+1.0152>1,1,-0.0187*$C$50+1.0152)","v":1},{"$f":"IF(-0.0087*$C$50+1.0095>1,1,-0.0087*$C$50+1.0095)","v":1}]
[4,"3 x 1c 185mm² XLPE/EPR - 35mm² Cu wire sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2991*($C$50^-0.918)>1,1,0.2991*($C$50^-0.918))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.4928*($C$50^-0.832)>1,1,0.4928*($C$50^-0.832))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.7085*($C$50^-0.691)>1,1,0.7085*($C$50^-0.691))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.238*LN($C$50)+0.8313>1,1,-0.238*LN($C$50)+0.8313)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0021*($C$50^2)-0.0786*$C$50+1.0083>1,1,0.0021*($C$50^2)-0.0786*$C$50+1.0083)","v":1},{"$f":"IF(0.0015*($C$50^2)-0.066*$C$50+1.0147>1,1,0.0015*($C$50^2)-0.066*$C$50+1.0147)","v":1},{"$f":"IF(0.0003*($C$50^2)-0.0317*$C$50+1.0108>1,1,0.0003*($C$50^2)-0.0317*$C$50+1.0108)","v":1},{"$f":"IF(-0.0141*$C$50+1.0054>1,1,-0.0141*$C$50+1.0054)","v":1}]
[5,"3 x 1c 185mm² XLPE/EPR - 70mm² Cu wire sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.3182*($C$50^-0.931)>1,1,0.3182*($C$50^-0.931))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5223*($C$50^-0.837)>1,1,0.5223*($C$50^-0.837))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.7481*($C$50^-0.692)>1,1,0.74814*($C$50^-0.692))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.243*LN($C$50)+0.8644>1,1,-0.243*LN($C$50)+0.8644)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0018*($C$50^2)-0.0741*$C$50+1.028>1,1,0.0018*($C$50^2)-0.0741*$C$50+1.028)","v":1},{"$f":"IF(0.0012*($C$50^2)-0.0599*$C$50+1.0283>1,1,0.0012*($C$50^2)-0.0599*$C$50+1.0283)","v":1},{"$f":"IF(-0.0234*$C$50+1.0096>1,1,-0.0234*$C$50+1.0096)","v":1},{"$f":"IF(-0.012*$C$50+1.0114>1,1,-0.012*$C$50+1.0114)","v":1}]
[6,"3 x 1c 240mm² XLPE/EPR - 16mm² Cu wire sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2617*($C$50^-0.909)>1,1,0.2617*($C$50^-0.909))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.4321*($C$50^-0.826)>1,1,0.4321*($C$50^-0.826))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.6336*($C$50^-0.701)>1,1,0.6336*($C$50^-0.701))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.229*LN($C$50)+0.7676>1,1,-0.229*LN($C$50)+0.7676)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0025*($C$50^2)-0.0865*$C$50+0.9691>1,1,0.0025*($C$50^2)-0.0865*$C$50+0.9691)","v":0.96909999999999996},{"$f":"IF(0.002*($C$50^2)-0.0762*$C$50+0.9844>1,1,0.002*($C$50^2)-0.0762*$C$50+0.9844)","v":0.98440000000000005},{"$f":"IF(0.0008*($C$50^2)-0.0441*$C$50+1.0018>1,1,0.0008*($C$50^2)-0.0441*$C$50+1.0018)","v":1},{"$f":"IF(0.0002*($C$50^2)-0.022*$C$50+1.0017>1,1,0.0002*($C$50^2)-0.022*$C$50+1.0017)","v":1}]
[7,"3 x 1c 240mm² XLPE/EPR - Polylam sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.237*($C$50^-0.912)>1,1,0.237*($C$50^-0.912))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3926*($C$50^-0.83)>1,1,0.3926*($C$50^-0.83))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5851*($C$50^-0.713)>1,1,0.5851*($C$50^-0.713))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.223*LN($C$50)+0.7266>1,1,-0.223*LN($C$50)+0.7266)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0027*($C$50^2)-0.0909*$C$50+0.9422>1,1,0.0027*($C$50^2)-0.0909*$C$50+0.9422)","v":0.94220000000000004},{"$f":"IF(0.0023*($C$50^2)-0.0821*$C$50+0.963>1,1,0.0023*($C$50^2)-0.0821*$C$50+0.963)","v":0.96299999999999997},{"$f":"IF(0.0011*($C$50^2)-0.0519*$C$50+0.9949>1,1,0.0011*($C$50^2)-0.0519*$C$50+0.9949)","v":0.99490000000000001},{"$f":"IF(0.0004*($C$50^2)-0.0278*$C$50+1.0001>1,1,0.0004*($C$50^2)-0.0278*$C$50+1.0001)","v":1}]
[8,"3 x 1c 300mm² XLPE/EPR - 35mm² Cu wire sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.3037*($C$50^-0.918)>1,1,0.3037*($C$50^-0.918))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.4977*($C$50^-0.828)>1,1,0.4977*($C$50^-0.828))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.714*($C$50^-0.688)>1,1,0.714*($C$50^-0.688))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.238*LN($C$50)+0.8353>1,1,-0.238*LN($C$50)+0.8353)","v":{"$error":"#NUM!"}},{"$f":"IF(0.002*($C$50^2)-0.0777*$C$50+1.0097>1,1,0.002*($C$50^2)-0.0777*$C$50+1.0097)","v":1},{"$f":"IF(0.0015*($C$50^2)-0.0649*$C$50+1.0152>1,1,0.0015*($C$50^2)-0.0649*$C$50+1.0152)","v":1},{"$f":"IF(0.0003*($C$50^2)-0.0308*$C$50+1.0103>1,1,0.0003*($C$50^2)-0.0308*$C$50+1.0103)","v":1},{"$f":"IF(-0.0139*$C$50+1.0057>1,1,-0.0139*$C$50+1.0057)","v":1}]
[9,"3 x 1c 300mm² XLPE/EPR - 70mm² Cu wire sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.3204*($C$50^-0.925)>1,1,0.3204*($C$50^-0.925))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5272*($C$50^-0.836)>1,1,0.5272*($C$50^-0.836))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.7517*($C$50^-0.688)>1,1,0.7517*($C$50^-0.688))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.242*LN($C$50)+0.8663>1,1,-0.242*LN($C$50)+0.8663)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0018*($C$50^2)-0.0733*$C$50+1.0275>1,1,0.0018*($C$50^2)-0.0733*$C$50+1.0275)","v":1},{"$f":"IF(0.0012*($C$50^2)-0.0593*$C$50+1.0282>1,1,0.0012*($C$50^2)-0.0593*$C$50+1.0282)","v":1},{"$f":"IF(-0.0232*$C$50+1.0096>1,1,-0.0232*$C$50+1.0096)","v":1},{"$f":"IF(-0.0119*$C$50+1.0111>1,1,-0.0119*$C$50+1.0111)","v":1}]
[10,"3 x 1c 630mm² XLPE/EPR - 90mm² Cu wire sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.3807*($C$50^-0.904)>1,1,0.3807*($C$50^-0.904))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5978*($C$50^-0.793)>1,1,0.5978*($C$50^-0.793))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.8125*($C$50^-0.63)>1,1,0.8125*($C$50^-0.63))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.231*LN($C$50)+0.9021>1,1,-0.231*LN($C$50)+0.9021)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0012*($C$50^2)-0.0599*$C$50+1.0263>1,1,0.0012*($C$50^2)-0.0599*$C$50+1.0263)","v":1},{"$f":"IF(0.0008*($C$50^2)-0.0468*$C$50+1.0231>1,1,0.0008*($C$50^2)-0.0468*$C$50+1.0231)","v":1},{"$f":"IF(-0.0194*$C$50+1.0112>1,1,-0.0194*$C$50+1.0112)","v":1},{"$f":"IF(-0.0094*$C$50+1.0082>1,1,-0.0094*$C$50+1.0082)","v":1}]
[11,"3 x 1c 70mm² XLPE/EPR - 12mm² Cu wire sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2382*($C$50^-0.914)>1,1,0.2382*($C$50^-0.914))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3949*($C$50^-0.831)>1,1,0.3949*($C$50^-0.831))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5887*($C$50^-0.715)>1,1,0.5887*($C$50^-0.715))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.224*LN($C$50)+0.7305>1,1,-0.224*LN($C$50)+0.7305)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0027*($C$50^2)-0.0909*$C$50+0.9457>1,1,0.0027*($C$50^2)-0.0909*$C$50+0.9457)","v":0.94569999999999999},{"$f":"IF(0.0023*($C$50^2)-0.082*$C$50+0.9663>1,1,0.0023*($C$50^2)-0.082*$C$50+0.9663)","v":0.96630000000000005},{"$f":"IF(0.0011*($C$50^2)-0.0513*$C$50+0.9964>1,1,0.0011*($C$50^2)-0.0513*$C$50+0.9964)","v":0.99639999999999995},{"$f":"IF(0.0004*($C$50^2)-0.0272*$C$50+1.0007>1,1,0.0004*($C$50^2)-0.0272*$C$50+1.0007)","v":1}]
[12,"3 x 1c 95mm² XLPE/EPR - 35mm² Cu wire sheaths ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2961*($C$50^-0.917)>1,1,0.2961*($C$50^-0.917))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.489*($C$50^-0.833)>1,1,0.489*($C$50^-0.833))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.706*($C$50^-0.695)>1,1,0.706*($C$50^-0.695))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.238*LN($C$50)+0.83>1,1,-0.238*LN($C$50)+0.83)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0021*($C$50^2)-0.0792*$C$50+1.0085>1,1,0.0021*($C$50^2)-0.0792*$C$50+1.0085)","v":1},{"$f":"IF(0.0016*($C$50^2)-0.0666*$C$50+1.0151>1,1,0.0016*($C$50^2)-0.0666*$C$50+1.0151)","v":1},{"$f":"IF(0.0003*($C$50^2)-0.032*$C$50+1.0112>1,1,0.0003*($C$50^2)-0.032*$C$50+1.0112)","v":1},{"$f":"IF(-0.0142*$C$50+1.0053>1,1,-0.0142*$C$50+1.0053)","v":1}]
[13,"3c 0.04 inch² PILC","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.1323*($C$50^-0.931)>1,1,0.1323*($C$50^-0.931))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.235*($C$50^-0.887)>1,1,0.235*($C$50^-0.887))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3819*($C$50^-0.803)>1,1,0.3819*($C$50^-0.803))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5604*($C$50^-0.688)>1,1,0.5604*($C$50^-0.688))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.212*LN($C$50)+0.6974>1,1,-0.212*LN($C$50)+0.6974)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.213*LN($C$50)+0.7434>1,1,-0.213*LN($C$50)+0.7434)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0024*($C$50^2)-0.0823*$C$50+0.9361>1,1,0.0024*($C$50^2)-0.0823*$C$50+0.9361)","v":0.93610000000000004},{"$f":"IF(0.0014*($C$50^2)-0.0565*$C$50+0.9809>1,1,0.0014*($C$50^2)-0.0565*$C$50+0.9809)","v":0.98089999999999999}]
[14,"3c 0.04 inch² PILCSWA ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.1323*($C$50^-0.931)>1,1,0.1323*($C$50^-0.931))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.235*($C$50^-0.887)>1,1,0.235*($C$50^-0.887))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3819*($C$50^-0.803)>1,1,0.3819*($C$50^-0.803))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5604*($C$50^-0.688)>1,1,0.5604*($C$50^-0.688))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.212*LN($C$50)+0.6974>1,1,-0.212*LN($C$50)+0.6974)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.213*LN($C$50)+0.7434>1,1,-0.213*LN($C$50)+0.7434)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0024*($C$50^2)-0.0823*$C$50+0.9361>1,1,0.0024*($C$50^2)-0.0823*$C$50+0.9361)","v":0.93610000000000004},{"$f":"IF(0.0014*($C$50^2)-0.0565*$C$50+0.9809>1,1,0.0014*($C$50^2)-0.0565*$C$50+0.9809)","v":0.98089999999999999}]
[15,"3c 0.06 inch² PILC ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.1435*($C$50^-0.944)>1,1,0.1435*($C$50^-0.944))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.2516*($C$50^-0.884)>1,1,0.2516*($C$50^-0.884))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.4043*($C$50^-0.794)>1,1,0.4043*($C$50^-0.794))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5842*($C$50^-0.672)>1,1,0.5842*($C$50^-0.672))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.213*LN($C$50)+0.7171>1,1,-0.213*LN($C$50)+0.7171)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.213*LN($C$50)+0.7618>1,1,-0.213*LN($C$50)+0.7618)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0022*($C$50^2)-0.0785*$C$50+0.9442>1,1,0.0022*($C$50^2)-0.0785*$C$50+0.9442)","v":0.94420000000000004},{"$f":"IF(0.0012*($C$50^2)-0.0531*$C$50+0.9849>1,1,0.0012*($C$50^2)-0.0531*$C$50+0.9849)","v":0.9849}]
[16,"3c 0.06 inch² PILCSWA ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.1435*($C$50^-0.944)>1,1,0.1435*($C$50^-0.944))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.2516*($C$50^-0.884)>1,1,0.2516*($C$50^-0.884))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.4043*($C$50^-0.794)>1,1,0.4043*($C$50^-0.794))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5842*($C$50^-0.672)>1,1,0.5842*($C$50^-0.672))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.213*LN($C$50)+0.7171>1,1,-0.213*LN($C$50)+0.7171)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.213*LN($C$50)+0.7618>1,1,-0.213*LN($C$50)+0.7618)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0022*($C$50^2)-0.0785*$C$50+0.9442>1,1,0.0022*($C$50^2)-0.0785*$C$50+0.9442)","v":0.94420000000000004},{"$f":"IF(0.0012*($C$50^2)-0.0531*$C$50+0.9849>1,1,0.0012*($C$50^2)-0.0531*$C$50+0.9849)","v":0.9849}]
[17,"3c 0.1 inch² PILC ","Y",1.228,33.700000000000003,{"$f":"D20*COS(RADIANS(E20))","v":1.0216396619762325},{"$f":"D20*SIN(RADIANS(E20))","v":0.68134895690614317},{"$f":"COMPLEX(F20,G20,\"j\")","v":"1.02163966197623+0.681348956906143j"},{"$f":"IMPRODUCT(H20,$D$50)","v":"0"},{"$f":"IMSUM(I20,$D$49)","v":"0.849993979209314"},{"$f":"IMDIV($D$49,J20)","v":"1"},{"$f":"ROUND(IMABS(K20),4)","v":1}]
[18,"3c 0.1 inch² PILCSWA ","Y",1.2210000000000001,33.24,1.0212222246023004,0.6692878065364174,"1.0212222246023+0.669287806536417j",{"$f":"IMPRODUCT(H21,$D$50)","v":"0"},{"$f":"IMSUM(I21,$D$49)","v":"0.849993979209314"},{"$f":"IMDIV($D$49,J21)","v":"1"},{"$f":"ROUND(IMABS(K21),4)","v":1}]
[19,"3c 0.15 inch² PILC","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.1791*($C$50^-0.918)>1,1,0.1791*($C$50^-0.918))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3072*($C$50^-0.856)>1,1,0.3072*($C$50^-0.856))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.477*($C$50^-0.756)>1,1,0.477*($C$50^-0.756))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.209*LN($C$50)+0.632>1,1,-0.209*LN($C$50)+0.632)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.215*LN($C$50)+0.7788>1,1,-0.215*LN($C$50)+0.7788)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.21*LN($C$50)+0.8186>1,1,-0.21*LN($C$50)+0.8186)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0018*($C$50^2)-0.0685*$C$50+0.9709>1,1,0.0018*($C$50^2)-0.0685*$C$50+0.97092)","v":0.97092000000000001},{"$f":"IF(0.0008*($C$50^2)-0.042*$C$50+0.9937>1,1,0.0008*($C$50^2)-0.042*$C$50+0.9937)","v":0.99370000000000003}]
[20,"3c 0.15 inch² PILCSWA ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.1791*($C$50^-0.918)>1,1,0.1791*($C$50^-0.918))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3072*($C$50^-0.856)>1,1,0.3072*($C$50^-0.856))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.477*($C$50^-0.756)>1,1,0.477*($C$50^-0.756))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.209*LN($C$50)+0.632>1,1,-0.209*LN($C$50)+0.632)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.215*LN($C$50)+0.7788>1,1,-0.215*LN($C$50)+0.7788)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.21*LN($C$50)+0.8186>1,1,-0.21*LN($C$50)+0.8186)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0018*($C$50^2)-0.0685*$C$50+0.9709>1,1,0.0018*($C$50^2)-0.0685*$C$50+0.97092)","v":0.97092000000000001},{"$f":"IF(0.0008*($C$50^2)-0.042*$C$50+0.9937>1,1,0.0008*($C$50^2)-0.042*$C$50+0.9937)","v":0.99370000000000003}]
[21,"3c 0.2 inch² PILC ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2017*($C$50^-0.917)>1,1,0.2017*($C$50^-0.917))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3404*($C$50^-0.846)>1,1,0.3404*($C$50^-0.846))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5195*($C$50^-0.739)>1,1,0.5195*($C$50^-0.739))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.215*LN($C$50)+0.6694>1,1,-0.215*LN($C$50)+0.6694)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.213*LN($C$50)+0.8103>1,1,-0.213*LN($C$50)+0.8103)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0027*($C$50^2)-0.0894*$C$50+0.9312>1,1,0.0027*$C$50^2)-0.0894*$C$50+0.9312","v":0.93120000000000003},{"$f":"IF(0.0015*($C$50^2)-0.0622*$C$50+0.9819>1,1,0.0015*($C$50^2)-0.0622*$C$50+0.9819)","v":0.9819},{"$f":"IF(0.0006*($C$50^2)-0.0363*$C$50+0.9971>1,1,0.0006*($C$50^2)-0.0363*$C$50+0.9971)","v":0.99709999999999999}]
[22,"3c 0.2 inch² PILCSWA ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2017*($C$50^-0.917)>1,1,0.2017*($C$50^-0.917))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3404*($C$50^-0.846)>1,1,0.3404*($C$50^-0.846))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5195*($C$50^-0.739)>1,1,0.5195*($C$50^-0.739))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.215*LN($C$50)+0.6694>1,1,-0.215*LN($C$50)+0.6694)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.213*LN($C$50)+0.8103>1,1,-0.213*LN($C$50)+0.8103)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0027*($C$50^2)-0.0894*$C$50+0.9312>1,1,0.0027*$C$50^2)-0.0894*$C$50+0.9312","v":0.93120000000000003},{"$f":"IF(0.0015*($C$50^2)-0.0622*$C$50+0.9819>1,1,0.0015*($C$50^2)-0.0622*$C$50+0.9819)","v":0.9819},{"$f":"IF(0.0006*($C$50^2)-0.0363*$C$50+0.9971>1,1,0.0006*($C$50^2)-0.0363*$C$50+0.9971)","v":0.99709999999999999}]
[23,"3c 0.25 inch² PILC ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2079*($C$50^-0.909)>1,1,0.2079*($C$50^-0.909))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3508*($C$50^-0.841)>1,1,0.3508*($C$50^-0.841))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5327*($C$50^-0.733)>1,1,0.5327*($C$50^-0.733))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.217*LN($C$50)+0.6812>1,1,-0.217*LN($C$50)+0.6812)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.213*LN($C$50)+0.82>1,1,-0.213*LN($C$50)+0.82)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0026*($C$50^2)-0.088*$C$50+0.9379>1,1,0.0026*($C$50^2)-0.088*$C$50+0.9379)","v":0.93789999999999996},{"$f":"IF(0.0015*($C$50^2)-0.0602*$C$50+0.9851>1,1,0.0015*($C$50^2)-0.0602*$C$50+0.9851)","v":0.98509999999999998},{"$f":"IF(0.0006*($C$50^2)-0.0345*$C$50+0.998>1,1,0.0006*($C$50^2)-0.0345*$C$50+0.998)","v":0.998}]
[24,"3c 0.25 inch² PILCSWA ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2079*($C$50^-0.909)>1,1,0.2079*($C$50^-0.909))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3508*($C$50^-0.841)>1,1,0.3508*($C$50^-0.841))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5327*($C$50^-0.733)>1,1,0.5327*($C$50^-0.733))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.217*LN($C$50)+0.6812>1,1,-0.217*LN($C$50)+0.6812)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.213*LN($C$50)+0.82>1,1,-0.213*LN($C$50)+0.82)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0026*($C$50^2)-0.088*$C$50+0.9379>1,1,0.0026*($C$50^2)-0.088*$C$50+0.9379)","v":0.93789999999999996},{"$f":"IF(0.0015*($C$50^2)-0.0602*$C$50+0.9851>1,1,0.0015*($C$50^2)-0.0602*$C$50+0.9851)","v":0.98509999999999998},{"$f":"IF(0.0006*($C$50^2)-0.0345*$C$50+0.998>1,1,0.0006*($C$50^2)-0.0345*$C$50+0.998)","v":0.998}]
[25,"3c 0.3 inch² PILC ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2254*($C$50^-0.909)>1,1,0.2254*($C$50^-0.909))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3779*($C$50^-0.838)>1,1,0.3779*($C$50^-0.838))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5661*($C$50^-0.722)>1,1,0.5661*($C$50^-0.722))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.221*LN($C$50)+0.7102>1,1,-0.221*LN($C$50)+0.7102)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0028*($C$50^2)-0.925*$C$50+0.9309>1,1,0.0028*($C$50^2)-0.0925*$C$50+0.9309)","v":0.93089999999999995},{"$f":"IF(0.0024*($C$50^2)-0.0843*$C$50+0.954>1,1,0.0024*($C$50^2)-0.0843*$C$50+0.954)","v":0.95399999999999996},{"$f":"IF(0.0012*($C$50^2)-0.055*$C$50+0.9914>1,1,0.0012*($C$50^2)-0.055*$C$50+0.9914)","v":0.99139999999999995},{"$f":"IF(0.0005*($C$50^2)-0.0303*$C$50+0.9995>1,1,0.0005*($C$50^2)-0.0303*$C$50+0.9995)","v":0.99950000000000006}]
[26,"3c 0.3 inch² PILCSWA ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2254*($C$50^-0.909)>1,1,0.2254*($C$50^-0.909))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3779*($C$50^-0.838)>1,1,0.3779*($C$50^-0.838))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5661*($C$50^-0.722)>1,1,0.5661*($C$50^-0.722))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.221*LN($C$50)+0.7102>1,1,-0.221*LN($C$50)+0.7102)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0028*($C$50^2)-0.925*$C$50+0.9309>1,1,0.0028*($C$50^2)-0.0925*$C$50+0.9309)","v":0.93089999999999995},{"$f":"IF(0.0024*($C$50^2)-0.0843*$C$50+0.954>1,1,0.0024*($C$50^2)-0.0843*$C$50+0.954)","v":0.95399999999999996},{"$f":"IF(0.0012*($C$50^2)-0.055*$C$50+0.9914>1,1,0.0012*($C$50^2)-0.055*$C$50+0.9914)","v":0.99139999999999995},{"$f":"IF(0.0005*($C$50^2)-0.0303*$C$50+0.9995>1,1,0.0005*($C$50^2)-0.0303*$C$50+0.9995)","v":0.99950000000000006}]
[27,"3c 0.4 inch² PILC ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2363*($C$50^-0.916)>1,1,0.2363*($C$50^-0.916))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3928*($C$50^-0.834)>1,1,0.3928*($C$50^-0.834))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.583*($C$50^-0.713)>1,1,0.583*($C$50^-0.713))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.223*LN($C$50)+0.7248>1,1,-0.223*LN($C$50)+0.7248)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0027*($C$50^2)-0.091*$C$50+0.9406>1,1,0.0027*($C$50^2)-0.091*$C$50+0.9406)","v":0.94059999999999999},{"$f":"IF(0.0023*($C$50^2)-0.0823*$C$50+0.9619>1,1,0.0023*($C$50^2)-0.0823*$C$50+0.9619)","v":0.96189999999999998},{"$f":"IF(0.0011*($C$50^2)-0.0522*$C$50+0.994>1,1,0.0011*($C$50^2)-0.0522*$C$50+0.994)","v":0.99399999999999999},{"$f":"IF(0.0004*($C$50^2)-0.028*$C$50+0.9997>1,1,0.0004*($C$50^2)-0.028*$C$50+0.9997)","v":0.99970000000000003}]
[28,"3c 0.4 inch² PILCSWA ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2363*($C$50^-0.916)>1,1,0.2363*($C$50^-0.916))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.3928*($C$50^-0.834)>1,1,0.3928*($C$50^-0.834))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.583*($C$50^-0.713)>1,1,0.583*($C$50^-0.713))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.223*LN($C$50)+0.7248>1,1,-0.223*LN($C$50)+0.7248)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0027*($C$50^2)-0.091*$C$50+0.9406>1,1,0.0027*($C$50^2)-0.091*$C$50+0.9406)","v":0.94059999999999999},{"$f":"IF(0.0023*($C$50^2)-0.0823*$C$50+0.9619>1,1,0.0023*($C$50^2)-0.0823*$C$50+0.9619)","v":0.96189999999999998},{"$f":"IF(0.0011*($C$50^2)-0.0522*$C$50+0.994>1,1,0.0011*($C$50^2)-0.0522*$C$50+0.994)","v":0.99399999999999999},{"$f":"IF(0.0004*($C$50^2)-0.028*$C$50+0.9997>1,1,0.0004*($C$50^2)-0.028*$C$50+0.9997)","v":0.99970000000000003}]
[29,"3c 185 mm² PILC ","Y",0.999,41.66,0.74635531627669793,0.66404423185922645,"0.746355316276698+0.664044231859226j",{"$f":"IMPRODUCT(H32,$D$50)","v":"0"},{"$f":"IMSUM(I32,$D$49)","v":"0.849993979209314"},{"$f":"IMDIV($D$49,J32)","v":"1"},{"$f":"ROUND(IMABS(K32),4)","v":1}]
[30,"3c 185 mm² PILCSWA ","Y",1.099,41.6,0.82183010145788649,0.72965490770481356,"0.821830101457886+0.729654907704814j","0","0.849993979209314","1",1]
[31,"3c 185mm² PICAS ","Y",0.67700000000000005,77.33,0.14849005601557022,0.66051472600123984,"0.14849005601557+0.66051472600124j","0","0.849993979209314","1",1]
[32,"3c 185mm² XLPE/EPR - 50mm² Cu wire sheath ","Y",0.751,59.46,0.3816129671641546,0.64681724102884719,"0.381612967164155+0.646817241028847j","0","0.849993979209314","1",1]
[33,"3c 300 mm² PILC ","Y",0.85799999999999998,49.53,0.55688473843078989,0.65271999211213894,"0.55688473843079+0.652719992112139j","0","0.849993979209314","1",1]
[34,"3c 300 mm² PILCSWA ","Y",0.873,49.1,0.57158873037523761,0.65986007858334927,"0.571588730375238+0.659860078583349j","0","0.849993979209314","1",1]
[35,"3c 300mm² PICAS ","Y",0.65800000000000003,79.599999999999994,0.11878159757486853,0.64719002779520796,"0.118781597574869+0.647190027795208j","0","0.849993979209314","1",1]
[36,"3c 300mm² XLPE/EPR - 50mm² Cu wire sheath ","Y",0.74399999999999999,58.79,0.38552316028735223,0.63632373276662602,"0.385523160287352+0.636323732766626j","0","0.849993979209314","1",1]
[37,"3c 50 mm² PILC ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.1443*($C$50^-0.936)>1,1,0.1443*($C$50^-0.936))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.2514*($C$50^-0.875)>1,1,0.2514*($C$50^-0.875))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.4055*($C$50^-0.79)>1,1,0.4055*($C$50^-0.79))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5867*($C$50^-0.671)>1,1,0.5867*($C$50^-0.671))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.213*LN($C$50)+0.7186>1,1,-0.213*LN($C$50)+0.7186)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.213*LN($C$50)+0.7632>1,1,-0.213*LN($C$50)+0.7632)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0022*($C$50^2)-0.079*$C$50+0.9464>1,1,0.0022*($C$50^2)-0.079*$C$50+0.9464)","v":0.94640000000000002},{"$f":"IF(0.0012*($C$50^2)-0.0529*$C$50+0.9854>1,1,0.0012*($C$50^2)-0.0529*$C$50+0.9854)","v":0.98540000000000005}]
[38,"3c 50 mm² PILCSWA ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.1443*($C$50^-0.936)>1,1,0.1443*($C$50^-0.936))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.2514*($C$50^-0.875)>1,1,0.2514*($C$50^-0.875))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.4055*($C$50^-0.79)>1,1,0.4055*($C$50^-0.79))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.5867*($C$50^-0.671)>1,1,0.5867*($C$50^-0.671))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.213*LN($C$50)+0.7186>1,1,-0.213*LN($C$50)+0.7186)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.213*LN($C$50)+0.7632>1,1,-0.213*LN($C$50)+0.7632)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0022*($C$50^2)-0.079*$C$50+0.9464>1,1,0.0022*($C$50^2)-0.079*$C$50+0.9464)","v":0.94640000000000002},{"$f":"IF(0.0012*($C$50^2)-0.0529*$C$50+0.9854>1,1,0.0012*($C$50^2)-0.0529*$C$50+0.9854)","v":0.98540000000000005}]
[39,"3c 95mm² PICAS ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2946*($C$50^-0.924)>1,1,0.2946*($C$50^-0.924))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.4843*($C$50^-0.832)>1,1,0.4843*($C$50^-0.832))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.232*LN($C$50)+0.666>1,1,-0.232*LN($C$50)+0.666)","v":{"$error":"#NUM!"}},{"$f":"IF(-0.238*LN($C$50)+0.825>1,1,-0.238*LN($C$50)+0.825)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0021*($C$50^2)-0.08*$C$50+1.0058>1,1,0.0021*($C$50^2)-0.08*$C$50+1.0058)","v":1},{"$f":"IF(0.0016*($C$50^2)-0.0673*$C$50+1.0124>1,1,0.0016*($C$50^2)-0.0673*$C$50+1.0124)","v":1},{"$f":"IF(0.0004*($C$50^2)-0.0329*$C$50+1.0101>1,1,0.0004*($C$50^2)-0.0329*$C$50+1.0101)","v":1},{"$f":"IF(1.0119*EXP($C$50*-0.017)>1,1,1.0119*EXP($C$50*-0.017))","v":1}]
[40,"3c 95mm² XLPE/EPR - 35mm² Cu wire sheath ","N",null,null,null,null,null,null,null,null,null,{"$f":"IF(0.2662*($C$50^-0.911)>1,1,0.2662*($C$50^-0.911))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.4381*($C$50^-0.826)>1,1,0.4381*($C$50^-0.826))","v":{"$error":"#DIV/0!"}},{"$f":"IF(0.6396*($C$50^-0.698)>1,1,0.6396*($C$50^-0.698))","v":{"$error":"#DIV/0!"}},{"$f":"IF(-0.229*LN($C$50)+0.7725>1,1,-0.229*LN($C$50)+0.7725)","v":{"$error":"#NUM!"}},{"$f":"IF(0.0024*($C$50^2)-0.0857*$C$50+0.9716>1,1,0.0024*($C$50^2)-0.0857*$C$50+0.9716)","v":0.97160000000000002},{"$f":"IF(0.002*($C$50^2)-0.0753*$C$50+0.9862>1,1,0.002*($C$50^2)-0.0753*$C$50+0.9862)","v":0.98619999999999997},{"$f":"IF(0.0008*($C$50^2)-0.0432*$C$50+1.0025>1,1,0.0008*($C$50^2)-0.0432*$C$50+1.0025)","v":1},{"$f":"IF(0.0002*($C$50^2)-0.0213*$C$50+1.0016>1,1,0.0002*($C$50^2)-0.0213*$C$50+1.0016)","v":1}]
[]
[null,null,null,null,null,null,null,null,null,null,null,"$C$50"]
[]
[null,"Cable connected to source",{"$f":"'Data Entered'!B48","v":"YES"}]
[null,"Predominant cable type",{"$f":"'Data Entered'!B50","v":0}]
["[Z2]","Overall Earthing Resistance",{"$f":"'Data Entered'!F74","v":0.84999397920931408},{"$f":"COMPLEX(C49,0,\"j\")","v":"0.849993979209314"}]
["[L]","Cable Length",{"$f":"'Data Entered'!B51","v":0},{"$f":"COMPLEX(C50,0,\"j\")","v":"0"}]
[null,"Formula Available?",{"$f":"VLOOKUP(C48,B4:T43,2,FALSE)","v":{"$error":"#N/A"}}]
[null,"Lookup Column",{"$f":"IF(C51=\"Y\",11,IF(C49<=0.25,12,IF(C49<=0.5,13,IF(C49<=1,14,IF(C49<=2,15,IF(C49<=4,16,IF(C49<=5,17,IF(C49<=10,18,19))))))))","v":{"$error":"#N/A"}}]
[null,"Lookup Value",{"$f":"VLOOKUP(C48,B4:T43,C52,FALSE)","v":{"$error":"#N/A"}}]
[null,"% Lookup Value (Rounded)",{"$f":"IF(C53<0,0,ROUND(C53*100,0))","v":{"$error":"#N/A"}}]
[null,"Transfer Voltage Value",{"$f":"IF(C48=0,0,IF(C47=\"YES\",C54,0))","v":0}]
[]
[]
["NOTE 1:","Columns 3 to 11 are used where the cable is listed in Table D.1 of S34 Issue 2 i.e. where a cable sheath self impedance value is available. The transfer voltage can then be calculated directly."]
[]
["NOTE 2:","Columns 12 to 19 are used where the cable is not listed in Table D.1 of S34 Issue 2 and hence the transfer voltage cannot be calculated directly. The formulae in the associated cells have been derived using curve fitting techniques against data obtained using the Earthing Solutions calculator. It was not possible to derive a formula based on cable length which was accurate over the entire range of distribution substation earth electrode resistances, however, good accuracy was obtained over a more limited range of resistance."]

{"sheet":"Data-Transfer Voltages","index":30,"n_rows":41,"n_cols":22,"rows_kept":41,"cut":false,"hidden":true,"merged":[[33,1,33,2],[35,1,35,2]]}
["ROW NO"]
[1,"Standard Fault Clearance Time (s)","Soil or outdoor concrete","75mm chippings","150mm chippings","100mm tarmac"]
[{"$f":"A2+1","v":2},0.1,2070,2341,2728,13579]
[{"$f":"A3+1","v":3},0.15,1808,2043,2379,11761]
[4,0.2,1570,1773,2064,10202]
[5,0.3,1179,1331,1548,7622]
[6,0.4,837,944,1095,5376]
[7,0.5,578,650,753,3656]
[8,0.6,420,471,544,2614]
[9,0.7,332,371,428,2012]
[10,0.8,281,314,361,1710]
[11,0.9,250,279,321,1523]
[12,1,233,259,298,1376]
[13,1.1000000000000001,219,244,280,1288]
[14,1.2,209,232,266,1220]
[15,1.3,200,223,255,1167]
[16,1.4,193,215,246,1117]
[17,1.5,188,209,239,1191]
[18,2,173,192,220,992]
[19,3,162,180,205,919]
[20,5,156,173,198,897]
[21,10.01,153,170,194,884]
["COL NO",1,{"$f":"B23+1","v":2},{"$f":"C23+1","v":3},{"$f":"D23+1","v":4},{"$f":"E23+1","v":5}]
[]
[]
[null,"Standard Fault Clearance Time (s)","Soil or outdoor concrete","75mm chippings","150mm chippings","100mm tarmac"]
["COL NO",1,{"$f":"B27+1","v":2},{"$f":"C27+1","v":3},{"$f":"D27+1","v":4},{"$f":"E27+1","v":5}]
[]
[]
[null,"Standard Fault Clearance Time (s)",0.1,0.15,0.2,0.3,0.4,0.5,0.6,0.7,0.8,0.9,1,1.1000000000000001,1.2,1.3,1.4,1.5,2,3,5,10.01]
["ROW NO",1,{"$f":"B31+1","v":2},{"$f":"C31+1","v":3},4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21]
[]
[]
[null,"Source 33kV / 66kV / 132kV fault clearance time",null,{"$f":"'Data Entered'!F23","v":3.4},"s"]
[null,"Nearest standard fault clearance time",null,{"$f":"IF(ISNA(INDEX(B3:B22,MATCH(D34,B3:B22,1)+1)),10.01,INDEX(B3:B22,MATCH(D34,B3:B22,1)+1))","v":5},"s"]
[null,"ROW NO",null,{"$f":"HLOOKUP(D35,B30:V31,2,FALSE)","v":20}]
[null,null,"COL NO","Safety Voltage"]
[null,"Soil or outdoor concrete",{"$f":"HLOOKUP(B38,B26:F27,2,FALSE)","v":2},{"$f":"INDEX(B2:F22,D36,C38)","v":156}]
[null,"75mm chippings",{"$f":"HLOOKUP(B39,B26:F42,2,FALSE)","v":3},{"$f":"INDEX(B2:F22,D36,C39)","v":173}]
[null,"150mm chippings",{"$f":"HLOOKUP(B40,B26:F27,2,FALSE)","v":4},{"$f":"INDEX(B2:F22,D36,C40)","v":198}]
[null,"100mm tarmac",{"$f":"HLOOKUP(B41,B26:F27,2,FALSE)","v":5},{"$f":"INDEX(B2:F22,D36,C41)","v":897}]

{"sheet":"Calculations-Fault Current","index":31,"n_rows":31,"n_cols":3,"rows_kept":31,"cut":false,"hidden":true,"merged":[]}
["System voltage",{"$f":"IF('Data Entered'!B14=0,11000,'Data Entered'!B14)","v":11000}]
["Units",{"$f":"'Data Entered'!B24","v":0},{"$f":"IF(B2=\"Ohms\",\"Ω\",\"%\")","v":"%"}]
["R: Z1",{"$f":"IF('Data Entered'!B25=0,1,'Data Entered'!B25)","v":1}]
["R: Z2",{"$f":"IF('Data Entered'!B26=0,1,'Data Entered'!B26)","v":1}]
["R: Z0",{"$f":"IF('Data Entered'!B27=0,1,'Data Entered'!B27)","v":1}]
["X: Z1",{"$f":"IF('Data Entered'!C25=0,1,'Data Entered'!C25)","v":1}]
["X: Z2",{"$f":"IF('Data Entered'!C26=0,1,'Data Entered'!C26)","v":1}]
["X: Z0",{"$f":"IF('Data Entered'!C27=0,1,'Data Entered'!C27)","v":1}]
["R: Source",{"$f":"IF(OR(ISNA('Design Input'!B50),ISBLANK('Design Input'!B50)),0.1,'Design Input'!B50)","v":0.1}]
["R: GMSUB",{"$f":"IF('Data Entered'!F74=\"\",0.1,'Data Entered'!F74)","v":0.84999397920931408}]
[]
["MVA Base",100]
[]
["1pu current",{"$f":"(B12*1000000)/(B1*SQRT(3))","v":5248.6388108147794}]
["1pu resistance",{"$f":"B1/(B14*SQRT(3))","v":1.2100000000000002}]
[]
[null,"Resistance","Reactance"]
[{"$f":"CONCATENATE(\"Network \",C2)","v":"Network %"},{"$f":"B3+B4+B5","v":3},{"$f":"B6+B7+B8","v":3}]
["Network PU",{"$f":"IF(C2=\"%\",B18/100,B18/B15)","v":0.03},{"$f":"IF(C2=\"%\",C18/100,C18/B15)","v":0.03}]
[]
["Source Ω",{"$f":"B9","v":0.1}]
["Source PU",{"$f":"(3*B21)/B15","v":0.24793388429752067}]
[]
["GMSUB Ω",{"$f":"B10","v":0.84999397920931408}]
["GMSUB PU",{"$f":"(3*B24)/B15","v":2.1074230889487122}]
[]
["Total impedance PU",{"$f":"SQRT((B19+B22+B25)^2+C19^2)","v":2.3855456167959623}]
[]
["IF",{"$f":"3/B27","v":1.2575739398474863},"PU"]
[]
["IF",{"$f":"B29*B14","v":6600.5513881527677},"Amps"]

{"sheet":"Simple Calcs - Fault Current","index":32,"n_rows":99,"n_cols":9,"rows_kept":99,"cut":false,"hidden":true,"merged":[[50,0,50,1],[2,5,2,6],[15,5,15,6],[17,5,17,6],[36,5,36,6],[38,5,38,6],[40,5,40,6],[41,5,41,6],[43,5,43,6],[47,0,47,1],[48,0,48,1],[49,0,49,1],[62,0,62,1],[51,0,51,1],[52,0,52,1],[53,0,53,1],[54,0,54,1],[55,0,55,1],[56,0,56,1],[57,0,57,1],[58,0,58,1],[59,0,59,1],[60,0,60,1],[61,0,61,1],[74,0,74,1],[63,0,63,1],[64,0,64,1],[65,0,65,1],[66,0,66,1],[67,0,67,1],[68,0,68,1],[69,0,69,1],[70,0,70,1],[71,0,71,1],[72,0,72,1],[73,0,73,1],[86,0,86,1],[75,0,75,1],[76,0,76,1],[77,0,77,1],[78,0,78,1],[79,0,79,1],[80,0,80,1],[81,0,81,1],[82,0,82,1],[83,0,83,1],[84,0,84,1],[85,0,85,1],[98,0,98,1],[87,0,87,1],[88,0,88,1],[89,0,89,1],[90,0,90,1],[91,0,91,1],[92,0,92,1],[93,0,93,1],[94,0,94,1],[95,0,95,1],[96,0,96,1],[97,0,97,1]]}
["SIMPLE CALCULATOR FOR EARTH FAULT CURRENT"]
[]
["Source Substation Secondary Voltage",null,{"$f":"IF('Data Entered'!B14=0,11000,'Data Entered'!B14)","v":11000},null,null,"Line-to-Neutral Voltage (V)",null,{"$f":"C3/SQRT(3)","v":6350.8529610858841}]
[]
["Source Impedance"]
[null,null,null,null,null,null,null,"Fault Level (A)","Reactance (Ω)"]
[null,null,null,null,null,null,null,13100,{"$f":"H3/H7","v":0.48479793596075449}]
[]
["Source Substation Neutral Earthing"]
[null,"NER Type","Rating",null,null,null,null,"Resistance (Ω)","Reactance (Ω)"]
[null,{"$f":"'Data Entered'!B28","v":0},{"$f":"'Data Entered'!C28","v":""},"Amps",null,null,null,{"$f":"IF(OR(B11=\"Reactor\",B11=\"Solid\",C11=\"N/A\",C11=0),0,H$3/C11)","v":{"$error":"#VALUE!"}},{"$f":"IF(OR(B11=\"Resistor\",C11=\"N/A\",C11=0),0,H$3/C11)","v":{"$error":"#VALUE!"}}]
["NER 1",{"$f":"'Data Entered'!B29","v":0},{"$f":"'Data Entered'!C29","v":0},"Amps",null,null,null,{"$f":"IF(OR(B12=\"Reactor\",B12=\"Solid\",C12=\"N/A\",C12=0),0,H$3/C12)","v":0},{"$f":"IF(OR(B12=\"Resistor\",C12=\"N/A\",C12=0),0,H$3/C12)","v":0}]
["NER 2",{"$f":"'Data Entered'!B30","v":0},{"$f":"'Data Entered'!C30","v":0},"Amps",null,null,null,{"$f":"IF(OR(B13=\"Reactor\",B13=\"Solid\",C13=\"N/A\",C13=0),0,H$3/C13)","v":0},{"$f":"IF(OR(B13=\"Resistor\",C13=\"N/A\",C13=0),0,H$3/C13)","v":0}]
["NER 3",{"$f":"'Data Entered'!B31","v":0},{"$f":"'Data Entered'!C31","v":0},"Amps",null,null,null,{"$f":"IF(OR(B14=\"Reactor\",B14=\"Solid\",C14=\"N/A\",C14=0),0,H$3/C14)","v":0},0]
["NER 4",{"$f":"'Data Entered'!B32","v":0},{"$f":"'Data Entered'!C32","v":0},"Amps",null,null,null,{"$f":"IF(OR(B15=\"Reactor\",B15=\"Solid\",C15=\"N/A\",C15=0),0,H$3/C15)","v":0},0]
[null,null,null,null,null,"Effective NER Impedance (Ω)",null,{"$f":"IF(SUM(H11:H15)=0,0,(1/(IF(H11=0,0,1/H11)+IF(H12=0,0,1/H12)+IF(H13=0,0,1/H13)+IF(H14=0,0,1/H14)+IF(H15=0,0,1/H15))))","v":{"$error":"#VALUE!"}},{"$f":"IF(SUM(I11:I15)=0,0,(1/(IF(I11=0,0,1/I11)+IF(I12=0,0,1/I12)+IF(I13=0,0,1/I13)+IF(I14=0,0,1/I14)+IF(I15=0,0,1/I15))))","v":{"$error":"#VALUE!"}}]
[]
["Source Substation Earth Electrode Resistance (Ω)",null,{"$f":"IF(OR(ISNA('Design Input'!B50),ISBLANK('Design Input'!B50)),0.1,'Design Input'!B50)","v":0.1},null,null,"Source Electrode Resistance (Ω)",null,{"$f":"IF(C18=\"\",0,C18)","v":0.1}]
[]
[]
["Circuit Resistance (Ω)","Conductor Type","Length (m)",null,null,"Resistance (Ω/km)","Reactance (Ω/km)","Resistance (Ω)","Reactance (Ω)"]
["Section 1",{"$f":"'Data Entered'!B33","v":0},{"$f":"'Data Entered'!C33","v":0},null,null,{"$f":"IF(B22=0,0,VLOOKUP(B22,A$49:D$99,3))","v":0},{"$f":"IF(B22=0,0,VLOOKUP(B22,A$49:D$99,4))","v":0},{"$f":"F22*C22","v":0},{"$f":"G22*C22","v":0}]
["Section 2",{"$f":"'Data Entered'!B34","v":0},{"$f":"'Data Entered'!C34","v":0},null,null,{"$f":"IF(B23=0,0,VLOOKUP(B23,A$49:D$99,3))","v":0},{"$f":"IF(B23=0,0,VLOOKUP(B23,A$49:D$99,4))","v":0},{"$f":"F23*C23","v":0},{"$f":"G23*C23","v":0}]
["Section 3",{"$f":"'Data Entered'!B35","v":0},{"$f":"'Data Entered'!C35","v":0},null,null,{"$f":"IF(B24=0,0,VLOOKUP(B24,A$49:D$99,3))","v":0},{"$f":"IF(B24=0,0,VLOOKUP(B24,A$49:D$99,4))","v":0},{"$f":"F24*C24","v":0},{"$f":"G24*C24","v":0}]
["Section 4",{"$f":"'Data Entered'!B36","v":0},{"$f":"'Data Entered'!C36","v":0},null,null,0,0,0,0]
["Section 5",{"$f":"'Data Entered'!B37","v":0},{"$f":"'Data Entered'!C37","v":0},null,null,0,0,0,0]
["Section 6",{"$f":"'Data Entered'!B38","v":0},{"$f":"'Data Entered'!C38","v":0},null,null,{"$f":"IF(B27=0,0,VLOOKUP(B27,A$49:D$99,3))","v":0},{"$f":"IF(B27=0,0,VLOOKUP(B27,A$49:D$99,4))","v":0},{"$f":"F27*C27","v":0},{"$f":"G27*C27","v":0}]
["Section 7",{"$f":"'Data Entered'!B39","v":0},{"$f":"'Data Entered'!C39","v":0},null,null,0,0,0,0]
["Section 8",{"$f":"'Data Entered'!B40","v":0},{"$f":"'Data Entered'!C40","v":0},null,null,0,0,0,0]
["Section 9",{"$f":"'Data Entered'!B41","v":0},{"$f":"'Data Entered'!C41","v":0},null,null,{"$f":"IF(B30=0,0,VLOOKUP(B30,A$49:D$99,3))","v":0},{"$f":"IF(B30=0,0,VLOOKUP(B30,A$49:D$99,4))","v":0},{"$f":"F30*C30","v":0},{"$f":"G30*C30","v":0}]
["Section 10",{"$f":"'Data Entered'!B42","v":0},{"$f":"'Data Entered'!C42","v":0},null,null,0,0,0,0]
["Section 11",{"$f":"'Data Entered'!B43","v":0},{"$f":"'Data Entered'!C43","v":0},null,null,0,0,0,0]
["Section 12",{"$f":"'Data Entered'!B44","v":0},{"$f":"'Data Entered'!C44","v":0},null,null,0,0,0,0]
["Section 13",{"$f":"'Data Entered'!B45","v":0},{"$f":"'Data Entered'!C45","v":0},null,null,0,0,0,0]
["Section 14",{"$f":"'Data Entered'!B46","v":0},{"$f":"'Data Entered'!C46","v":0},null,null,0,0,0,0]
["Section 15",{"$f":"'Data Entered'!B47","v":0},{"$f":"'Data Entered'!C47","v":0},null,null,0,0,0,0]
[null,null,null,null,null,"Subtotal (Ω)",null,{"$f":"SUM(H22:H36)","v":0},{"$f":"SUM(I22:I36)","v":0}]
[]
["Distribution Substation Earth Electrode Resistance (Ω)",null,{"$f":"IF('Data Entered'!F74=\"\",0.1,'Data Entered'!F74)","v":0.84999397920931408},null,null,"GMSUB Electrode Resistance (Ω)",null,{"$f":"IF(C39=\"\",0,C39)","v":0.84999397920931408}]
[]
[null,null,null,null,null,"Complex Impedance Total (Ω)",null,{"$f":"H16+H18+H37+H39","v":{"$error":"#VALUE!"}},{"$f":"I7+I16+I37","v":{"$error":"#VALUE!"}}]
[null,null,null,null,null,"Modulus Impedance Total (Ω)",null,{"$f":"SQRT(H41^2+I41^2)","v":{"$error":"#VALUE!"}}]
[]
[null,null,null,null,null,"Fault Current (A)",null,{"$f":"IF(ISERR(H3/H42),10000,H3/H42)","v":10000}]
[]
[]
[]
["Line & Cable",null,"R (Ω)","jX (Ω)"]
["Overhead Aluminium 0.075 sq in",null,0.41,0.38700000000000001]
["Overhead Aluminium 0.1 sq in",null,0.27300000000000002,0.378]
["Overhead Aluminium 0.15 sq in",null,0.18099999999999999,0.33500000000000002]
["Overhead Aluminium 0.2 sq in",null,0.13700000000000001,0.30299999999999999]
["Overhead Aluminium 0.3 sq in",null,8.8999999999999996E-2,0.27700000000000002]
["Overhead Aluminium 100 sq mm",null,0.27300000000000002,0.378]
["Overhead Aluminium 150 sq mm",null,0.18099999999999999,0.33500000000000002]
["Overhead Aluminium 175 sq mm",null,0.16500000000000001,0.32500000000000001]
["Overhead Aluminium 200 sq mm",null,0.13900000000000001,0.32500000000000001]
["Overhead Aluminium 50 sq mm",null,0.54700000000000004,0.39500000000000002]
["Overhead Copper 0.075 sq in",null,0.41,0.38700000000000001]
["Overhead Copper 0.1 sq in",null,0.27500000000000002,0.34]
["Overhead Copper 0.15 sq in",null,0.18099999999999999,0.33500000000000002]
["Overhead Copper 0.2 sq in",null,0.14000000000000001,0.308]
["Overhead Copper 0.25 sq in",null,0.11,0.30499999999999999]
["Overhead Copper 0.3 sq in",null,8.5999999999999993E-2,0.30399999999999999]
["Overhead Copper 100 sq mm",null,0.17599999999999999,0.35599999999999998]
["Underground Aluminium 0.1 sq in",null,0.45600000000000002,8.9700000000000002E-2]
["Underground Aluminium 0.15 sq in",null,0.312,8.3900000000000002E-2]
["Underground Aluminium 0.2 sq in",null,0.23400000000000001,8.2000000000000003E-2]
["Underground Aluminium 0.3 sq in",null,0.152,7.7799999999999994E-2]
["Underground Aluminium 0.4 sq in",null,0.113,7.6999999999999999E-2]
["Underground Aluminium 0.5 sq in",null,9.2299999999999993E-2,7.4200000000000002E-2]
["Underground Aluminium 0.6 sq in",null,7.8E-2,7.4999999999999997E-2]
["Underground Aluminium 0.75 sq in",null,5.8999999999999997E-2,7.3999999999999996E-2]
["Underground Aluminium 1.0 sq in",null,4.2000000000000003E-2,7.2999999999999995E-2]
["Underground Aluminium 120 sq mm",null,0.253,8.4000000000000005E-2]
["Underground Aluminium 150 sq mm",null,0.20599999999999999,8.2000000000000003E-2]
["Underground Aluminium 185 sq mm",null,0.16400000000000001,0.08]
["Underground Aluminium 240 sq mm",null,0.125,7.8E-2]
["Underground Aluminium 300 sq mm",null,0.1,7.6999999999999999E-2]
["Underground Aluminium 70 sq mm",null,0.443,0.09]
["Underground Aluminium 95 sq mm",null,0.32,8.6999999999999994E-2]
["Underground Copper 0.1 sq in",null,0.27600000000000002,8.9700000000000002E-2]
["Underground Copper 0.15 sq in",null,0.188,8.3900000000000002E-2]
["Underground Copper 0.2 sq in",null,0.14199999999999999,8.2000000000000003E-2]
["Underground Copper 0.3 sq in",null,9.1999999999999998E-2,7.7799999999999994E-2]
["Underground Copper 0.4 sq in",null,6.8000000000000005E-2,7.6999999999999999E-2]
["Underground Copper 0.5 sq in",null,5.6000000000000001E-2,7.3999999999999996E-2]
["Underground Copper 0.6 sq in",null,4.7E-2,7.4999999999999997E-2]
["Underground Copper 0.75 sq in",null,3.6999999999999998E-2,0.08]
["Underground Copper 1.0 sq in",null,2.8000000000000001E-2,8.3000000000000004E-2]
["Underground Copper 120 sq mm",null,0.153,8.4000000000000005E-2]
["Underground Copper 150 sq mm",null,0.124,8.2000000000000003E-2]
["Underground Copper 185 sq mm",null,9.9000000000000005E-2,0.08]
["Underground Copper 240 sq mm",null,7.5399999999999995E-2,7.9000000000000001E-2]
["Underground Copper 300 sq mm",null,0.06,7.6999999999999999E-2]
["Underground Copper 400 sq mm",null,4.7E-2,7.5999999999999998E-2]
["Underground Copper 630 sq mm",null,2.8299999999999999E-2,8.5000000000000006E-2]
["Underground Copper 70 sq mm",null,0.26800000000000002,0.09]
["Underground Copper 95 sq mm",null,0.193,8.6999999999999994E-2]

{"sheet":"Ground Current Default","index":33,"n_rows":70,"n_cols":7,"rows_kept":70,"cut":false,"hidden":true,"merged":[[0,0,1,0],[0,1,0,2],[0,3,1,3],[49,1,49,5],[43,2,46,6],[50,1,50,5],[51,1,51,5],[52,1,52,5],[53,1,53,5],[54,1,54,5],[55,1,55,5],[56,1,56,5],[57,1,57,5],[58,1,58,5],[59,1,59,5],[60,1,60,5],[61,1,61,5],[62,1,62,5],[63,1,63,5],[64,1,64,5],[65,1,65,5],[66,1,66,5],[67,1,67,5],[68,1,68,5],[69,1,69,5]]}
["Cable","C Factor",null,"XSA"]
[null,"All Cable","Line - Cable"]
["3 x 1c 150mm² XLPE/EPR - 16mm² Cu wire sheaths ",87,82,150]
["3 x 1c 150mm² XLPE/EPR - Polylam sheaths",137,130,150]
["3 x 1c 1600mm² XLPE/EPR - 135mm² Cu wire sheaths ",221,144,1600]
["3 x 1c 185mm² XLPE/EPR - 35mm² Cu wire sheaths ",47,42,185]
["3 x 1c 185mm² XLPE/EPR - 70mm² Cu wire sheaths ",25,20,185]
["3 x 1c 240mm² XLPE/EPR - 16mm² Cu wire sheaths ",115,107,240]
["3 x 1c 240mm² XLPE/EPR - Polylam sheaths ",162,152,240]
["3 x 1c 300mm² XLPE/EPR - 35mm² Cu wire sheaths ",64,57,300]
["3 x 1c 300mm² XLPE/EPR - 70mm² Cu wire sheaths ",36,27,300]
["3 x 1c 630mm² XLPE/EPR - 90mm² Cu wire sheaths ",109,86,630]
["3 x 1c 70mm² XLPE/EPR - 12mm² Cu wire sheaths ",81,77,70]
["3 x 1c 95mm² XLPE/EPR - 35mm² Cu wire sheaths ",33,30,95]
["3c 0.04 inch² PILC",173,166,26]
["3c 0.04 inch² PILCSWA ",67,66,26]
["3c 0.06 inch² PILC ",170,163,38]
["3c 0.06 inch² PILCSWA ",56,56,38]
["3c 0.1 inch² PILC ",154,147,65]
["3c 0.1 inch² PILCSWA ",57,55,65]
["3c 0.15 inch² PILC",169,161,97]
["3c 0.15 inch² PILCSWA ",62,60,97]
["3c 0.2 inch² PILC ",158,150,129]
["3c 0.2 inch² PILCSWA ",63,61,129]
["3c 0.25 inch² PILC ",168,159,161]
["3c 0.25 inch² PILCSWA ",68,65,161]
["3c 0.3 inch² PILC ",157,148,194]
["3c 0.3 inch² PILCSWA ",68,65,194]
["3c 0.4 inch² PILC ",173,162,258]
["3c 0.4 inch² PILCSWA ",76,71,258]
["3c 185 mm² PILC ",189,179,185]
["3c 185 mm² PILCSWA ",78,74,185]
["3c 185mm² PICAS ",30,26,185]
["3c 185mm² XLPE/EPR - 50mm² Cu wire sheath ",92,87,185]
["3c 300 mm² PILC ",193,181,300]
["3c 300 mm² PILCSWA ",97,93,300]
["3c 300mm² PICAS ",28,23,300]
["3c 300mm² XLPE/EPR - 50mm² Cu wire sheath ",130,122,300]
["3c 50 mm² PILC ",183,174,50]
["3c 50 mm² PILCSWA ",63,62,50]
["3c 95mm² PICAS ",34,32,95]
["3c 95mm² XLPE/EPR - 35mm² Cu wire sheath ",66,63,95]
[]
["Note: Assumed Values",null,"Values selected in order to equal or to closely approximate the ground current value derived using Earthing Solutions' Ground Return Current Calculator (100 ohm.m soil resistivity assumed)."]
[]
[]
[]
[]
[]
["Voltage ( E )",{"$f":"'Data Entered'!B14/1000","v":0},null,null,null,null,"kV"]
["Upper Layer Soil Resisitvity ( ρ )",{"$f":"'Data Entered'!B67","v":300},null,null,null,null,"Ωm"]
["Cable Type",{"$f":"'Data Entered'!B50","v":0}]
["Cable Length ( l )",{"$f":"'Data Entered'!B51","v":0},null,null,null,null,"km"]
["All Cable",{"$f":"'Data Entered'!B48","v":"YES"}]
["Column Reference",{"$f":"IF(B54=\"YES\",2,3)","v":2}]
["Cable Cross Sectional Area ( a )",{"$f":"VLOOKUP(B52,A1:D42,4,FALSE)","v":{"$error":"#N/A"}},null,null,null,null,"mm2"]
["C Factor",{"$f":"VLOOKUP(B52,A1:D42,B55,FALSE)","v":{"$error":"#N/A"}}]
["RA",{"$f":"IF('Data Entered'!B48=\"YES\",'Data Entered'!F18,IF('Data Entered'!B48=\"NO\",'Data Entered'!H53,\"0\"))","v":0.1},null,null,null,null,"Ω"]
["RB",{"$f":"'Data Entered'!F74","v":0.84999397920931408},null,null,null,null,"Ω"]
["RA + RB",{"$f":"B58+B59","v":0.94999397920931405},null,null,null,null,"Ω"]
["IF",{"$f":"'Data Entered'!B75","v":10000},null,null,null,null,"A"]
["C/(a+9E)",{"$f":"B57/(B56+(9*B50))","v":{"$error":"#N/A"}}]
["RA/l",{"$f":"IF(B54=\"YES\",0,(B58/B53))","v":0}]
["(RA + RB)/l",{"$f":"B60/B53","v":{"$error":"#DIV/0!"}}]
["[ C/(a+9E) + (RA + RB)/l ] 2",{"$f":"(B62+B64)^2","v":{"$error":"#N/A"}},null,null,null,null,"[X]"]
["ρ/(a*E)",{"$f":"B51/(B56*B50)","v":{"$error":"#N/A"}}]
["0.6*[ ρ/(a*E) ] 0.1",{"$f":"0.6*(B66^0.1)","v":{"$error":"#N/A"}},null,null,null,null,"[Y]"]
["([X]+[Y]) 0.5",{"$f":"(B65+B67)^0.5","v":{"$error":"#N/A"}}]
["IE",{"$f":"B61*((B62+B63)/B68)","v":{"$error":"#N/A"}},null,null,null,null,"A"]
["IE %",{"$f":"IF(ISNA(B69),100,ROUND((B69/B61)*100,0))","v":100},null,null,null,null,"%"]

{"sheet":"Calculations-IDMT Op Time","index":34,"n_rows":18,"n_cols":6,"rows_kept":18,"cut":false,"hidden":true,"merged":[[17,0,17,1],[0,0,0,1],[1,0,1,1],[2,0,2,1],[5,0,5,1],[6,0,6,1],[7,0,7,1],[10,0,10,1],[11,0,11,1],[12,0,12,1],[13,0,13,1],[16,0,16,1]]}
["Characteristic",null,"SI","VI","EI","LTI"]
["k",null,0.14000000000000001,13.5,80,120]
["α",null,0.02,1,2,1]
[]
[]
["Selected characteristic",null,{"$f":"'Data Entered'!B96","v":0}]
["Selected k value",null,{"$f":"IF(ISNA(HLOOKUP(C6,C1:F3,2,FALSE)),0.14,HLOOKUP(C6,C1:F3,2,FALSE))","v":0.14000000000000001}]
["Selected α value",null,{"$f":"IF(ISNA(HLOOKUP(C6,C1:F3,3,FALSE)),0.02,HLOOKUP(C6,C1:F3,3,FALSE))","v":0.02}]
[]
[]
["IF",null,{"$f":"IF(ISNA('Data Entered'!B75),2000,'Data Entered'!B75)","v":10000}]
["IS",null,{"$f":"'Data Entered'!B95","v":0}]
["IF / IS",null,{"$f":"IF(ISERR(C11/C12),20,C11/C12)","v":20}]
["Time multiplier",null,{"$f":"'Data Entered'!B97","v":0}]
[]
[]
["Operating time",null,{"$f":"1000*(C7*C14)/((C13^C8)-1)","v":0},"ms"]
["Operating time",null,{"$f":"C17/1000","v":0},"s"]

{"sheet":"Calculations-Surface Area","index":35,"n_rows":22,"n_cols":3,"rows_kept":22,"cut":false,"hidden":true,"merged":[[8,0,8,1]]}
[null,"Surface Area Per Metre Length"]
["Rod",39898,"mm2"]
["Stranded Conductor",29659,"mm2"]
[]
[]
["Perimeter electrode",{"$f":"IF('Data Entered'!D71=\"Required\",\"YES\",\"NO\")","v":"NO"}]
[]
[]
["Number of parallel 'tail' conductors",null,{"$f":"'Data Entered'!B81","v":0}]
[]
[]
[null,"Surface Area"]
["4No 12.7 x 1200mm rods",{"$f":"IF(B6=\"YES\",4*1.2*B2,0)","v":0},"mm2"]
["Perimeter electrode",{"$f":"IF(B6=\"YES\",(3.6+2.7+3.6+2.7)*B3,0)","v":0},"mm2"]
["Tail electrode",{"$f":"'Data Entered'!B72*B3*C9","v":0},"mm2"]
["TOTAL",{"$f":"SUM(B13:B15)","v":0},"mm2"]
[]
[]
["IGR",{"$f":"IF(ISNA('Data Entered'!D79),2000,'Data Entered'!D79)","v":7.7916114760853805E-2},"A"]
["ρ",{"$f":"'Data Entered'!B67","v":300},"Ωm"]
["t",3,"s"]
["Minimum surface area",{"$f":"IF(ISERR((1000*B19)/SQRT(57.7/(B20*B21))),6500000,(1000*B19)/SQRT(57.7/(B20*B21)))","v":307.72348110429317},"mm2"]