## Battery Calculator
BATTERY CALCULATOR FOR EE SPEC 24/4 |  |  |  | Version 1
Battery Nominal Voltage | 30
Battery Voltage At End Of Duty Cycle | 27.8
Standby Period (Hours) | 72
Design Margin | 1.1
Ageing Factor | 1.25
Temperature Correction Factor | 1.31
Circuit Breakers | Quantity Tripped Simultaneously | Tripping Burden (Watts) | Tripping Duration (Seconds)
Type 1 | 1 | 300 | 0.06
Standing Load (Watts) | 7.5
[5 empty] | Accurate 15degC | Accurate 5degC
Battery Capacity Required (Ah) | 35.3423 |  |  |  | 27.898 | 30.3887
Monobloc Type | Number of Parallel Strings | Actual Battery Capacity (Ah)
Enersys Powersafe SBS 41 | 1 | 37.7 | BATTERY CAPACITY IS ADEQUATE
Minimum Charger Rating (A) | 4.0668

## Kt_Data_Tables (hidden)
1
Kt: 1.85V/Cell @ 20degC |  | 1s | 5s | 30s | 60s | 3m | 5m | 10m | 15m | 20m | 30m | 40m | 50m | 1h | 1.5h | 3h | 5h | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
Time | 0 | 0.00032777 | 0.0014389 | 0.0083833 | 0.016717 | 0.05005 | 0.083383 | 0.16672 | 0.25005 | 0.33338 | 0.50005 | 0.66672 | 0.83338 | 1 | 1.5 | 3 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200
Enersys Powersafe SBS 8 | 0.22024 | 0.22024 | 0.22024 | 0.22024 | 0.22024 | 0.22024 | 0.22024 | 0.34101 | 0.45399 | 0.61201 | 0.77003 | 0.96679 | 1.1635 | 1.3603 | 2.4337 | 3.5071 | 5.5224 | 6.0068 | 6.4912 | 6.9456 | 7.4 | 7.8573 | 8.3146 | 8.7823 | 9.25 | 9.6935 | 10.137 | 10.5551 | 10.9733 | 11.3914 | 11.8096 | 12.2277 | 12.6459 | 13.064 | 13.4822 | 13.9003 | 14.3185 | 14.7366 | 15.1548 | 15.5729 | 15.9911 | 16.4092 | 16.8274 | 17.2455 | 17.6637 | 18.0818 | 18.5 | 18.9182 | 19.3363 | 19.7545 | 20.1726 | 20.5908 | 21.0089 | 21.4271 | 21.8452 | 22.2634 | 22.6815 | 23.0997 | 23.5178 | 23.936 | 24.3541 | 24.7723 | 25.1904 | 25.6086 | 26.0267 | 26.4449 | 26.863 | 27.2812 | 27.6993 | 28.1175 | 28.5356 | 28.9538 | 29.3719 | 29.7901 | 30.2082 | 30.6264 | 31.0445 | 31.4627 | 31.8808 | 32.299 | 32.7171 | 33.1353 | 33.5534 | 33.9716 | 34.3897 | 34.8079 | 35.226 | 35.6442 | 36.0623 | 36.4805 | 36.8986 | 37.3168 | 37.7349 | 38.1531 | 38.5712 | 38.9894 | 39.4075 | 39.8257 | 40.2438 | 40.662 | 41.0801 | 41.4983 | 41.9164 | 42.3346 | 42.7527 | 43.1709 | 43.589 | 44.0072 | 44.4253 | 44.8435 | 45.2616 | 45.6798 | 46.0979 | 46.5161 | 46.9342 | 47.3524 | 47.7705 | 48.1887 | 48.6068 | 49.025 | 49.4432 | 49.8613 | 50.2795 | 50.6976 | 51.1158 | 51.5339 | 51.9521 | 52.3702 | 52.7884 | 53.2065 | 53.6247 | 54.0428 | 54.461 | 54.8791 | 55.2973 | 55.7154 | 56.1336 | 56.5517 | 56.9699 | 57.388 | 57.8062 | 58.2243 | 58.6425 | 59.0606 | 59.4788 | 59.8969 | 60.3151 | 60.7332 | 61.1514 | 61.5695 | 61.9877 | 62.4058 | 62.824 | 63.2421 | 63.6603 | 64.0784 | 64.4966 | 64.9147 | 65.3329 | 65.751 | 66.1692 | 66.5873 | 67.0055 | 67.4236 | 67.8418 | 68.2599 | 68.6781 | 69.0962 | 69.5144 | 69.9325 | 70.3507 | 70.7688 | 71.187 | 71.6051 | 72.0233 | 72.4414 | 72.8596 | 73.2777 | 73.6959 | 74.114 | 74.5322 | 74.9503 | 75.3685 | 75.7866 | 76.2048 | 76.6229 | 77.0411 | 77.4592 | 77.8774 | 78.2955 | 78.7137 | 79.1318 | 79.55 | 79.9682 | 80.3863 | 80.8045 | 81.2226 | 81.6408 | 82.0589
Enersys Powersafe SBS 15 | 0.23609 | 0.23609 | 0.23609 | 0.23609 | 0.23609 | 0.23609 | 0.23609 | 0.35623 | 0.46667 | 0.62007 | 0.77348 | 0.9601 | 1.1467 | 1.3333 | 2.3782 | 3.423 | 5.4054 | 5.8845 | 6.3636 | 6.8467 | 7.3298 | 7.8069 | 8.284 | 8.7473 | 9.2105 | 9.6777 | 10.1449 | 10.5966 | 11.0482 | 11.4999 | 11.9516 | 12.4032 | 12.8549 | 13.3065 | 13.7582 | 14.2098 | 14.6615 | 15.1132 | 15.5648 | 16.0165 | 16.4681 | 16.9198 | 17.3715 | 17.8231 | 18.2748 | 18.7264 | 19.1781 | 19.6297 | 20.0814 | 20.5331 | 20.9847 | 21.4364 | 21.888 | 22.3397 | 22.7913 | 23.243 | 23.6947 | 24.1463 | 24.598 | 25.0496 | 25.5013 | 25.9529 | 26.4046 | 26.8563 | 27.3079 | 27.7596 | 28.2112 | 28.6629 | 29.1146 | 29.5662 | 30.0179 | 30.4695 | 30.9212 | 31.3728 | 31.8245 | 32.2762 | 32.7278 | 33.1795 | 33.6311 | 34.0828 | 34.5344 | 34.9861 | 35.4378 | 35.8894 | 36.3411 | 36.7927 | 37.2444 | 37.696 | 38.1477 | 38.5994 | 39.051 | 39.5027 | 39.9543 | 40.406 | 40.8577 | 41.3093 | 41.761 | 42.2126 | 42.6643 | 43.1159 | 43.5676 | 44.0193 | 44.4709 | 44.9226 | 45.3742 | 45.8259 | 46.2775 | 46.7292 | 47.1809 | 47.6325 | 48.0842 | 48.5358 | 48.9875 | 49.4392 | 49.8908 | 50.3425 | 50.7941 | 51.2458 | 51.6974 | 52.1491 | 52.6008 | 53.0524 | 53.5041 | 53.9557 | 54.4074 | 54.859 | 55.3107 | 55.7624 | 56.214 | 56.6657 | 57.1173 | 57.569 | 58.0206 | 58.4723 | 58.924 | 59.3756 | 59.8273 | 60.2789 | 60.7306 | 61.1823 | 61.6339 | 62.0856 | 62.5372 | 62.9889 | 63.4405 | 63.8922 | 64.3439 | 64.7955 | 65.2472 | 65.6988 | 66.1505 | 66.6021 | 67.0538 | 67.5055 | 67.9571 | 68.4088 | 68.8604 | 69.3121 | 69.7637 | 70.2154 | 70.6671 | 71.1187 | 71.5704 | 72.022 | 72.4737 | 72.9254 | 73.377 | 73.8287 | 74.2803 | 74.732 | 75.1836 | 75.6353 | 76.087 | 76.5386 | 76.9903 | 77.4419 | 77.8936 | 78.3452 | 78.7969 | 79.2486 | 79.7002 | 80.1519 | 80.6035 | 81.0552 | 81.5068 | 81.9585 | 82.4102 | 82.8618 | 83.3135 | 83.7651 | 84.2168 | 84.6685 | 85.1201 | 85.5718 | 86.0234 | 86.4751 | 86.9267 | 87.3784 | 87.8301
Enersys Powersafe SBS 30 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.36115 | 0.47397 | 0.63338 | 0.79279 | 0.98449 | 1.1762 | 1.3679 | 2.43 | 3.4921 | 5.5115 | 5.999 | 6.4865 | 6.9826 | 7.4788 | 7.9566 | 8.4345 | 8.9148 | 9.395 | 9.755 | 10.1149 | 10.5323 | 10.9496 | 11.3669 | 11.7843 | 12.2016 | 12.6189 | 13.0363 | 13.4536 | 13.8709 | 14.2882 | 14.7056 | 15.1229 | 15.5402 | 15.9576 | 16.3749 | 16.7922 | 17.2095 | 17.6269 | 18.0442 | 18.4615 | 18.8789 | 19.2962 | 19.7135 | 20.1309 | 20.5482 | 20.9655 | 21.3828 | 21.8002 | 22.2175 | 22.6348 | 23.0522 | 23.4695 | 23.8868 | 24.3042 | 24.7215 | 25.1388 | 25.5561 | 25.9735 | 26.3908 | 26.8081 | 27.2255 | 27.6428 | 28.0601 | 28.4775 | 28.8948 | 29.3121 | 29.7294 | 30.1468 | 30.5641 | 30.9814 | 31.3988 | 31.8161 | 32.2334 | 32.6508 | 33.0681 | 33.4854 | 33.9027 | 34.3201 | 34.7374 | 35.1547 | 35.5721 | 35.9894 | 36.4067 | 36.824 | 37.2414 | 37.6587 | 38.076 | 38.4934 | 38.9107 | 39.328 | 39.7454 | 40.1627 | 40.58 | 40.9973 | 41.4147 | 41.832 | 42.2493 | 42.6667 | 43.084 | 43.5013 | 43.9187 | 44.336 | 44.7533 | 45.1706 | 45.588 | 46.0053 | 46.4226 | 46.84 | 47.2573 | 47.6746 | 48.092 | 48.5093 | 48.9266 | 49.3439 | 49.7613 | 50.1786 | 50.5959 | 51.0133 | 51.4306 | 51.8479 | 52.2653 | 52.6826 | 53.0999 | 53.5172 | 53.9346 | 54.3519 | 54.7692 | 55.1866 | 55.6039 | 56.0212 | 56.4385 | 56.8559 | 57.2732 | 57.6905 | 58.1079 | 58.5252 | 58.9425 | 59.3599 | 59.7772 | 60.1945 | 60.6118 | 61.0292 | 61.4465 | 61.8638 | 62.2812 | 62.6985 | 63.1158 | 63.5332 | 63.9505 | 64.3678 | 64.7851 | 65.2025 | 65.6198 | 66.0371 | 66.4545 | 66.8718 | 67.2891 | 67.7065 | 68.1238 | 68.5411 | 68.9584 | 69.3758 | 69.7931 | 70.2104 | 70.6278 | 71.0451 | 71.4624 | 71.8798 | 72.2971 | 72.7144 | 73.1317 | 73.5491 | 73.9664 | 74.3837 | 74.8011 | 75.2184 | 75.6357 | 76.0531 | 76.4704 | 76.8877 | 77.305 | 77.7224 | 78.1397 | 78.557 | 78.9744 | 79.3917 | 79.809 | 80.2263 | 80.6437 | 81.061 | 81.4783 | 81.8957
Enersys Powersafe SBS 31 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.36115 | 0.47397 | 0.63338 | 0.79279 | 0.98449 | 1.1762 | 1.3679 | 2.43 | 3.4921 | 5.5115 | 5.999 | 6.4865 | 6.9826 | 7.4788 | 7.9566 | 8.4345 | 8.9148 | 9.395 | 9.755 | 10.1149 | 10.5323 | 10.9496 | 11.3669 | 11.7843 | 12.2016 | 12.6189 | 13.0363 | 13.4536 | 13.8709 | 14.2882 | 14.7056 | 15.1229 | 15.5402 | 15.9576 | 16.3749 | 16.7922 | 17.2095 | 17.6269 | 18.0442 | 18.4615 | 18.8789 | 19.2962 | 19.7135 | 20.1309 | 20.5482 | 20.9655 | 21.3828 | 21.8002 | 22.2175 | 22.6348 | 23.0522 | 23.4695 | 23.8868 | 24.3042 | 24.7215 | 25.1388 | 25.5561 | 25.9735 | 26.3908 | 26.8081 | 27.2255 | 27.6428 | 28.0601 | 28.4775 | 28.8948 | 29.3121 | 29.7294 | 30.1468 | 30.5641 | 30.9814 | 31.3988 | 31.8161 | 32.2334 | 32.6508 | 33.0681 | 33.4854 | 33.9027 | 34.3201 | 34.7374 | 35.1547 | 35.5721 | 35.9894 | 36.4067 | 36.824 | 37.2414 | 37.6587 | 38.076 | 38.4934 | 38.9107 | 39.328 | 39.7454 | 40.1627 | 40.58 | 40.9973 | 41.4147 | 41.832 | 42.2493 | 42.6667 | 43.084 | 43.5013 | 43.9187 | 44.336 | 44.7533 | 45.1706 | 45.588 | 46.0053 | 46.4226 | 46.84 | 47.2573 | 47.6746 | 48.092 | 48.5093 | 48.9266 | 49.3439 | 49.7613 | 50.1786 | 50.5959 | 51.0133 | 51.4306 | 51.8479 | 52.2653 | 52.6826 | 53.0999 | 53.5172 | 53.9346 | 54.3519 | 54.7692 | 55.1866 | 55.6039 | 56.0212 | 56.4385 | 56.8559 | 57.2732 | 57.6905 | 58.1079 | 58.5252 | 58.9425 | 59.3599 | 59.7772 | 60.1945 | 60.6118 | 61.0292 | 61.4465 | 61.8638 | 62.2812 | 62.6985 | 63.1158 | 63.5332 | 63.9505 | 64.3678 | 64.7851 | 65.2025 | 65.6198 | 66.0371 | 66.4545 | 66.8718 | 67.2891 | 67.7065 | 68.1238 | 68.5411 | 68.9584 | 69.3758 | 69.7931 | 70.2104 | 70.6278 | 71.0451 | 71.4624 | 71.8798 | 72.2971 | 72.7144 | 73.1317 | 73.5491 | 73.9664 | 74.3837 | 74.8011 | 75.2184 | 75.6357 | 76.0531 | 76.4704 | 76.8877 | 77.305 | 77.7224 | 78.1397 | 78.557 | 78.9744 | 79.3917 | 79.809 | 80.2263 | 80.6437 | 81.061 | 81.4783 | 81.8957
Enersys Powersafe SBS 40 | 0.27122 | 0.27122 | 0.27122 | 0.27122 | 0.27122 | 0.27122 | 0.27122 | 0.39067 | 0.50066 | 0.65397 | 0.80728 | 0.99682 | 1.1864 | 1.3759 | 2.4333 | 3.4907 | 5.536 | 6.0349 | 6.5338 | 7.0294 | 7.525 | 7.9328 | 8.3407 | 8.9185 | 9.4962 | 9.8153 | 10.1344 | 10.5517 | 10.969 | 11.3863 | 11.8036 | 12.2209 | 12.6382 | 13.0555 | 13.4728 | 13.8901 | 14.3074 | 14.7247 | 15.142 | 15.5593 | 15.9766 | 16.3939 | 16.8112 | 17.2285 | 17.6458 | 18.0631 | 18.4804 | 18.8977 | 19.315 | 19.7323 | 20.1496 | 20.5669 | 20.9842 | 21.4015 | 21.8188 | 22.2361 | 22.6534 | 23.0707 | 23.488 | 23.9053 | 24.3226 | 24.7399 | 25.1572 | 25.5745 | 25.9918 | 26.4091 | 26.8264 | 27.2437 | 27.661 | 28.0783 | 28.4956 | 28.9129 | 29.3302 | 29.7475 | 30.1648 | 30.5821 | 30.9994 | 31.4167 | 31.834 | 32.2513 | 32.6686 | 33.0859 | 33.5032 | 33.9205 | 34.3378 | 34.7551 | 35.1724 | 35.5897 | 36.007 | 36.4243 | 36.8416 | 37.2589 | 37.6762 | 38.0935 | 38.5108 | 38.9281 | 39.3454 | 39.7627 | 40.1799 | 40.5972 | 41.0145 | 41.4318 | 41.8491 | 42.2664 | 42.6837 | 43.101 | 43.5183 | 43.9356 | 44.3529 | 44.7702 | 45.1875 | 45.6048 | 46.0221 | 46.4394 | 46.8567 | 47.274 | 47.6913 | 48.1086 | 48.5259 | 48.9432 | 49.3605 | 49.7778 | 50.1951 | 50.6124 | 51.0297 | 51.447 | 51.8643 | 52.2816 | 52.6989 | 53.1162 | 53.5335 | 53.9508 | 54.3681 | 54.7854 | 55.2027 | 55.62 | 56.0373 | 56.4546 | 56.8719 | 57.2892 | 57.7065 | 58.1238 | 58.5411 | 58.9584 | 59.3757 | 59.793 | 60.2103 | 60.6276 | 61.0449 | 61.4622 | 61.8795 | 62.2968 | 62.7141 | 63.1314 | 63.5487 | 63.966 | 64.3833 | 64.8006 | 65.2179 | 65.6352 | 66.0525 | 66.4698 | 66.8871 | 67.3044 | 67.7217 | 68.139 | 68.5563 | 68.9736 | 69.3909 | 69.8082 | 70.2255 | 70.6428 | 71.0601 | 71.4774 | 71.8947 | 72.312 | 72.7293 | 73.1466 | 73.5639 | 73.9812 | 74.3985 | 74.8158 | 75.2331 | 75.6504 | 76.0677 | 76.485 | 76.9023 | 77.3196 | 77.7369 | 78.1542 | 78.5715 | 78.9888 | 79.4061 | 79.8234 | 80.2407 | 80.658 | 81.0753 | 81.4926 | 81.9099
Enersys Powersafe SBS 41 | 0.27122 | 0.27122 | 0.27122 | 0.27122 | 0.27122 | 0.27122 | 0.27122 | 0.39067 | 0.50066 | 0.65397 | 0.80728 | 0.99682 | 1.1864 | 1.3759 | 2.4333 | 3.4907 | 5.536 | 6.0349 | 6.5338 | 7.0294 | 7.525 | 7.9328 | 8.3407 | 8.9185 | 9.4962 | 9.8153 | 10.1344 | 10.5517 | 10.969 | 11.3863 | 11.8036 | 12.2209 | 12.6382 | 13.0555 | 13.4728 | 13.8901 | 14.3074 | 14.7247 | 15.142 | 15.5593 | 15.9766 | 16.3939 | 16.8112 | 17.2285 | 17.6458 | 18.0631 | 18.4804 | 18.8977 | 19.315 | 19.7323 | 20.1496 | 20.5669 | 20.9842 | 21.4015 | 21.8188 | 22.2361 | 22.6534 | 23.0707 | 23.488 | 23.9053 | 24.3226 | 24.7399 | 25.1572 | 25.5745 | 25.9918 | 26.4091 | 26.8264 | 27.2437 | 27.661 | 28.0783 | 28.4956 | 28.9129 | 29.3302 | 29.7475 | 30.1648 | 30.5821 | 30.9994 | 31.4167 | 31.834 | 32.2513 | 32.6686 | 33.0859 | 33.5032 | 33.9205 | 34.3378 | 34.7551 | 35.1724 | 35.5897 | 36.007 | 36.4243 | 36.8416 | 37.2589 | 37.6762 | 38.0935 | 38.5108 | 38.9281 | 39.3454 | 39.7627 | 40.1799 | 40.5972 | 41.0145 | 41.4318 | 41.8491 | 42.2664 | 42.6837 | 43.101 | 43.5183 | 43.9356 | 44.3529 | 44.7702 | 45.1875 | 45.6048 | 46.0221 | 46.4394 | 46.8567 | 47.274 | 47.6913 | 48.1086 | 48.5259 | 48.9432 | 49.3605 | 49.7778 | 50.1951 | 50.6124 | 51.0297 | 51.447 | 51.8643 | 52.2816 | 52.6989 | 53.1162 | 53.5335 | 53.9508 | 54.3681 | 54.7854 | 55.2027 | 55.62 | 56.0373 | 56.4546 | 56.8719 | 57.2892 | 57.7065 | 58.1238 | 58.5411 | 58.9584 | 59.3757 | 59.793 | 60.2103 | 60.6276 | 61.0449 | 61.4622 | 61.8795 | 62.2968 | 62.7141 | 63.1314 | 63.5487 | 63.966 | 64.3833 | 64.8006 | 65.2179 | 65.6352 | 66.0525 | 66.4698 | 66.8871 | 67.3044 | 67.7217 | 68.139 | 68.5563 | 68.9736 | 69.3909 | 69.8082 | 70.2255 | 70.6428 | 71.0601 | 71.4774 | 71.8947 | 72.312 | 72.7293 | 73.1466 | 73.5639 | 73.9812 | 74.3985 | 74.8158 | 75.2331 | 75.6504 | 76.0677 | 76.485 | 76.9023 | 77.3196 | 77.7369 | 78.1542 | 78.5715 | 78.9888 | 79.4061 | 79.8234 | 80.2407 | 80.658 | 81.0753 | 81.4926 | 81.9099
Enersys Powersafe SBS 60 | 0.29364 | 0.29364 | 0.29364 | 0.29364 | 0.29364 | 0.29364 | 0.29364 | 0.41301 | 0.52371 | 0.68169 | 0.83967 | 1.0288 | 1.218 | 1.4072 | 2.4433 | 3.4795 | 5.439 | 5.9185 | 6.398 | 6.8748 | 7.3517 | 7.8194 | 8.2871 | 8.7617 | 9.2364 | 9.6982 | 10.16 | 10.5998 | 11.0395 | 11.4793 | 11.919 | 12.3588 | 12.7986 | 13.2383 | 13.6781 | 14.1179 | 14.5576 | 14.9974 | 15.4371 | 15.8769 | 16.3167 | 16.7564 | 17.1962 | 17.6359 | 18.0757 | 18.5155 | 18.9552 | 19.395 | 19.8347 | 20.2745 | 20.7143 | 21.154 | 21.5938 | 22.0336 | 22.4733 | 22.9131 | 23.3528 | 23.7926 | 24.2324 | 24.6721 | 25.1119 | 25.5516 | 25.9914 | 26.4312 | 26.8709 | 27.3107 | 27.7504 | 28.1902 | 28.63 | 29.0697 | 29.5095 | 29.9493 | 30.389 | 30.8288 | 31.2685 | 31.7083 | 32.1481 | 32.5878 | 33.0276 | 33.4673 | 33.9071 | 34.3469 | 34.7866 | 35.2264 | 35.6661 | 36.1059 | 36.5457 | 36.9854 | 37.4252 | 37.865 | 38.3047 | 38.7445 | 39.1842 | 39.624 | 40.0638 | 40.5035 | 40.9433 | 41.383 | 41.8228 | 42.2626 | 42.7023 | 43.1421 | 43.5819 | 44.0216 | 44.4614 | 44.9011 | 45.3409 | 45.7807 | 46.2204 | 46.6602 | 47.0999 | 47.5397 | 47.9795 | 48.4192 | 48.859 | 49.2987 | 49.7385 | 50.1783 | 50.618 | 51.0578 | 51.4976 | 51.9373 | 52.3771 | 52.8168 | 53.2566 | 53.6964 | 54.1361 | 54.5759 | 55.0156 | 55.4554 | 55.8952 | 56.3349 | 56.7747 | 57.2144 | 57.6542 | 58.094 | 58.5337 | 58.9735 | 59.4133 | 59.853 | 60.2928 | 60.7325 | 61.1723 | 61.6121 | 62.0518 | 62.4916 | 62.9313 | 63.3711 | 63.8109 | 64.2506 | 64.6904 | 65.1301 | 65.5699 | 66.0097 | 66.4494 | 66.8892 | 67.329 | 67.7687 | 68.2085 | 68.6482 | 69.088 | 69.5278 | 69.9675 | 70.4073 | 70.847 | 71.2868 | 71.7266 | 72.1663 | 72.6061 | 73.0459 | 73.4856 | 73.9254 | 74.3651 | 74.8049 | 75.2447 | 75.6844 | 76.1242 | 76.5639 | 77.0037 | 77.4435 | 77.8832 | 78.323 | 78.7627 | 79.2025 | 79.6423 | 80.082 | 80.5218 | 80.9616 | 81.4013 | 81.8411 | 82.2808 | 82.7206 | 83.1604 | 83.6001 | 84.0399 | 84.4796 | 84.9194 | 85.3592 | 85.7989
Enersys Powersafe SBS 110 | 0.39655 | 0.39655 | 0.39655 | 0.39655 | 0.39655 | 0.39655 | 0.39655 | 0.5157 | 0.62842 | 0.78552 | 0.94262 | 1.1348 | 1.327 | 1.5192 | 2.5621 | 3.605 | 5.5556 | 6.0264 | 6.4972 | 6.9583 | 7.4194 | 7.8763 | 8.3333 | 8.8038 | 9.2742 | 9.681 | 10.0877 | 10.5123 | 10.9368 | 11.3613 | 11.7858 | 12.2104 | 12.6349 | 13.0594 | 13.484 | 13.9085 | 14.333 | 14.7576 | 15.1821 | 15.6066 | 16.0312 | 16.4557 | 16.8802 | 17.3048 | 17.7293 | 18.1538 | 18.5784 | 19.0029 | 19.4274 | 19.8519 | 20.2765 | 20.701 | 21.1255 | 21.5501 | 21.9746 | 22.3991 | 22.8237 | 23.2482 | 23.6727 | 24.0973 | 24.5218 | 24.9463 | 25.3709 | 25.7954 | 26.2199 | 26.6445 | 27.069 | 27.4935 | 27.918 | 28.3426 | 28.7671 | 29.1916 | 29.6162 | 30.0407 | 30.4652 | 30.8898 | 31.3143 | 31.7388 | 32.1634 | 32.5879 | 33.0124 | 33.437 | 33.8615 | 34.286 | 34.7106 | 35.1351 | 35.5596 | 35.9841 | 36.4087 | 36.8332 | 37.2577 | 37.6823 | 38.1068 | 38.5313 | 38.9559 | 39.3804 | 39.8049 | 40.2295 | 40.654 | 41.0785 | 41.5031 | 41.9276 | 42.3521 | 42.7767 | 43.2012 | 43.6257 | 44.0503 | 44.4748 | 44.8993 | 45.3238 | 45.7484 | 46.1729 | 46.5974 | 47.022 | 47.4465 | 47.871 | 48.2956 | 48.7201 | 49.1446 | 49.5692 | 49.9937 | 50.4182 | 50.8428 | 51.2673 | 51.6918 | 52.1164 | 52.5409 | 52.9654 | 53.3899 | 53.8145 | 54.239 | 54.6635 | 55.0881 | 55.5126 | 55.9371 | 56.3617 | 56.7862 | 57.2107 | 57.6353 | 58.0598 | 58.4843 | 58.9089 | 59.3334 | 59.7579 | 60.1825 | 60.607 | 61.0315 | 61.456 | 61.8806 | 62.3051 | 62.7296 | 63.1542 | 63.5787 | 64.0032 | 64.4278 | 64.8523 | 65.2768 | 65.7014 | 66.1259 | 66.5504 | 66.975 | 67.3995 | 67.824 | 68.2486 | 68.6731 | 69.0976 | 69.5221 | 69.9467 | 70.3712 | 70.7957 | 71.2203 | 71.6448 | 72.0693 | 72.4939 | 72.9184 | 73.3429 | 73.7675 | 74.192 | 74.6165 | 75.0411 | 75.4656 | 75.8901 | 76.3147 | 76.7392 | 77.1637 | 77.5883 | 78.0128 | 78.4373 | 78.8618 | 79.2864 | 79.7109 | 80.1354 | 80.56 | 80.9845 | 81.409 | 81.8336 | 82.2581 | 82.6826 | 83.1072
Enersys Powersafe SBS 130 | 0.35676 | 0.35676 | 0.35676 | 0.35676 | 0.35676 | 0.35676 | 0.35676 | 0.49254 | 0.61395 | 0.77841 | 0.94286 | 1.1384 | 1.334 | 1.5295 | 2.5681 | 3.6066 | 5.5462 | 6.0243 | 6.5025 | 6.9591 | 7.4157 | 7.8851 | 8.3544 | 8.7926 | 9.2308 | 9.6923 | 10.1538 | 10.5972 | 11.0405 | 11.4838 | 11.9271 | 12.3704 | 12.8137 | 13.2571 | 13.7004 | 14.1437 | 14.587 | 15.0303 | 15.4736 | 15.917 | 16.3603 | 16.8036 | 17.2469 | 17.6902 | 18.1335 | 18.5769 | 19.0202 | 19.4635 | 19.9068 | 20.3501 | 20.7934 | 21.2368 | 21.6801 | 22.1234 | 22.5667 | 23.01 | 23.4533 | 23.8967 | 24.34 | 24.7833 | 25.2266 | 25.6699 | 26.1132 | 26.5566 | 26.9999 | 27.4432 | 27.8865 | 28.3298 | 28.7731 | 29.2164 | 29.6598 | 30.1031 | 30.5464 | 30.9897 | 31.433 | 31.8763 | 32.3197 | 32.763 | 33.2063 | 33.6496 | 34.0929 | 34.5362 | 34.9796 | 35.4229 | 35.8662 | 36.3095 | 36.7528 | 37.1961 | 37.6395 | 38.0828 | 38.5261 | 38.9694 | 39.4127 | 39.856 | 40.2994 | 40.7427 | 41.186 | 41.6293 | 42.0726 | 42.5159 | 42.9593 | 43.4026 | 43.8459 | 44.2892 | 44.7325 | 45.1758 | 45.6192 | 46.0625 | 46.5058 | 46.9491 | 47.3924 | 47.8357 | 48.2791 | 48.7224 | 49.1657 | 49.609 | 50.0523 | 50.4956 | 50.9389 | 51.3823 | 51.8256 | 52.2689 | 52.7122 | 53.1555 | 53.5988 | 54.0422 | 54.4855 | 54.9288 | 55.3721 | 55.8154 | 56.2587 | 56.7021 | 57.1454 | 57.5887 | 58.032 | 58.4753 | 58.9186 | 59.362 | 59.8053 | 60.2486 | 60.6919 | 61.1352 | 61.5785 | 62.0219 | 62.4652 | 62.9085 | 63.3518 | 63.7951 | 64.2384 | 64.6818 | 65.1251 | 65.5684 | 66.0117 | 66.455 | 66.8983 | 67.3417 | 67.785 | 68.2283 | 68.6716 | 69.1149 | 69.5582 | 70.0016 | 70.4449 | 70.8882 | 71.3315 | 71.7748 | 72.2181 | 72.6614 | 73.1048 | 73.5481 | 73.9914 | 74.4347 | 74.878 | 75.3213 | 75.7647 | 76.208 | 76.6513 | 77.0946 | 77.5379 | 77.9812 | 78.4246 | 78.8679 | 79.3112 | 79.7545 | 80.1978 | 80.6411 | 81.0845 | 81.5278 | 81.9711 | 82.4144 | 82.8577 | 83.301 | 83.7444 | 84.1877 | 84.631 | 85.0743 | 85.5176 | 85.9609 | 86.4043
Enersys Powersafe SBS 300 | 0.3753 | 0.3753 | 0.3753 | 0.3753 | 0.3753 | 0.3753 | 0.3753 | 0.49839 | 0.62 | 0.81 | 1 | 1.2193 | 1.4385 | 1.6578 | 2.8135 | 3.9693 | 5.9615 | 6.4024 | 6.8433 | 7.2678 | 7.6923 | 8.1398 | 8.5873 | 9.0192 | 9.4512 | 9.791 | 10.1307 | 10.5253 | 10.92 | 11.3146 | 11.7092 | 12.1039 | 12.4985 | 12.8931 | 13.2877 | 13.6824 | 14.077 | 14.4716 | 14.8662 | 15.2609 | 15.6555 | 16.0501 | 16.4447 | 16.8394 | 17.234 | 17.6286 | 18.0233 | 18.4179 | 18.8125 | 19.2071 | 19.6018 | 19.9964 | 20.391 | 20.7856 | 21.1803 | 21.5749 | 21.9695 | 22.3642 | 22.7588 | 23.1534 | 23.548 | 23.9427 | 24.3373 | 24.7319 | 25.1265 | 25.5212 | 25.9158 | 26.3104 | 26.705 | 27.0997 | 27.4943 | 27.8889 | 28.2836 | 28.6782 | 29.0728 | 29.4674 | 29.8621 | 30.2567 | 30.6513 | 31.0459 | 31.4406 | 31.8352 | 32.2298 | 32.6244 | 33.0191 | 33.4137 | 33.8083 | 34.203 | 34.5976 | 34.9922 | 35.3868 | 35.7815 | 36.1761 | 36.5707 | 36.9653 | 37.36 | 37.7546 | 38.1492 | 38.5439 | 38.9385 | 39.3331 | 39.7277 | 40.1224 | 40.517 | 40.9116 | 41.3062 | 41.7009 | 42.0955 | 42.4901 | 42.8847 | 43.2794 | 43.674 | 44.0686 | 44.4633 | 44.8579 | 45.2525 | 45.6471 | 46.0418 | 46.4364 | 46.831 | 47.2256 | 47.6203 | 48.0149 | 48.4095 | 48.8041 | 49.1988 | 49.5934 | 49.988 | 50.3827 | 50.7773 | 51.1719 | 51.5665 | 51.9612 | 52.3558 | 52.7504 | 53.145 | 53.5397 | 53.9343 | 54.3289 | 54.7236 | 55.1182 | 55.5128 | 55.9074 | 56.3021 | 56.6967 | 57.0913 | 57.4859 | 57.8806 | 58.2752 | 58.6698 | 59.0644 | 59.4591 | 59.8537 | 60.2483 | 60.643 | 61.0376 | 61.4322 | 61.8268 | 62.2215 | 62.6161 | 63.0107 | 63.4053 | 63.8 | 64.1946 | 64.5892 | 64.9839 | 65.3785 | 65.7731 | 66.1677 | 66.5624 | 66.957 | 67.3516 | 67.7462 | 68.1409 | 68.5355 | 68.9301 | 69.3247 | 69.7194 | 70.114 | 70.5086 | 70.9033 | 71.2979 | 71.6925 | 72.0871 | 72.4818 | 72.8764 | 73.271 | 73.6656 | 74.0603 | 74.4549 | 74.8495 | 75.2441 | 75.6388 | 76.0334 | 76.428 | 76.8227 | 77.2173 | 77.6119 | 78.0065
Enersys Powersafe SBS 390 | 0.4157 | 0.4157 | 0.4157 | 0.4157 | 0.4157 | 0.4157 | 0.4157 | 0.52709 | 0.63492 | 0.78499 | 0.93506 | 1.1213 | 1.3075 | 1.4938 | 2.5116 | 3.5294 | 5.4711 | 5.9556 | 6.4401 | 6.9161 | 7.3922 | 7.834 | 8.2759 | 8.7533 | 9.2308 | 9.6574 | 10.084 | 10.5272 | 10.9704 | 11.4135 | 11.8567 | 12.2999 | 12.743 | 13.1862 | 13.6294 | 14.0725 | 14.5157 | 14.9589 | 15.402 | 15.8452 | 16.2884 | 16.7315 | 17.1747 | 17.6179 | 18.061 | 18.5042 | 18.9474 | 19.3905 | 19.8337 | 20.2769 | 20.72 | 21.1632 | 21.6064 | 22.0495 | 22.4927 | 22.9359 | 23.379 | 23.8222 | 24.2654 | 24.7085 | 25.1517 | 25.5949 | 26.038 | 26.4812 | 26.9244 | 27.3675 | 27.8107 | 28.2539 | 28.697 | 29.1402 | 29.5834 | 30.0265 | 30.4697 | 30.9129 | 31.356 | 31.7992 | 32.2424 | 32.6855 | 33.1287 | 33.5719 | 34.015 | 34.4582 | 34.9014 | 35.3445 | 35.7877 | 36.2309 | 36.674 | 37.1172 | 37.5604 | 38.0035 | 38.4467 | 38.8899 | 39.333 | 39.7762 | 40.2194 | 40.6625 | 41.1057 | 41.5489 | 41.992 | 42.4352 | 42.8784 | 43.3215 | 43.7647 | 44.2079 | 44.651 | 45.0942 | 45.5374 | 45.9805 | 46.4237 | 46.8669 | 47.31 | 47.7532 | 48.1964 | 48.6395 | 49.0827 | 49.5259 | 49.969 | 50.4122 | 50.8554 | 51.2985 | 51.7417 | 52.1849 | 52.628 | 53.0712 | 53.5144 | 53.9575 | 54.4007 | 54.8439 | 55.287 | 55.7302 | 56.1734 | 56.6165 | 57.0597 | 57.5029 | 57.946 | 58.3892 | 58.8324 | 59.2755 | 59.7187 | 60.1619 | 60.605 | 61.0482 | 61.4914 | 61.9345 | 62.3777 | 62.8209 | 63.264 | 63.7072 | 64.1504 | 64.5935 | 65.0367 | 65.4799 | 65.923 | 66.3662 | 66.8094 | 67.2525 | 67.6957 | 68.1389 | 68.582 | 69.0252 | 69.4684 | 69.9115 | 70.3547 | 70.7979 | 71.241 | 71.6842 | 72.1274 | 72.5705 | 73.0137 | 73.4569 | 73.9 | 74.3432 | 74.7864 | 75.2295 | 75.6727 | 76.1159 | 76.559 | 77.0022 | 77.4454 | 77.8885 | 78.3317 | 78.7749 | 79.218 | 79.6612 | 80.1044 | 80.5475 | 80.9907 | 81.4339 | 81.877 | 82.3202 | 82.7634 | 83.2065 | 83.6497 | 84.0929 | 84.536 | 84.9792 | 85.4224 | 85.8655 | 86.3087
Enersys Powersafe SBS B8 | 0.2089 | 0.2089 | 0.2089 | 0.2089 | 0.2089 | 0.2089 | 0.2089 | 0.36353 | 0.49674 | 0.66848 | 0.84022 | 1.0352 | 1.2302 | 1.4252 | 2.4456 | 3.4659 | 5.4078 | 5.8943 | 6.3808 | 6.874 | 7.3671 | 7.7502 | 8.1333 | 8.6189 | 9.1045 | 9.6019 | 10.0993 | 10.5911 | 11.0829 | 11.5746 | 12.0664 | 12.5582 | 13.0499 | 13.5417 | 14.0335 | 14.5252 | 15.017 | 15.5088 | 16.0005 | 16.4923 | 16.984 | 17.4758 | 17.9676 | 18.4593 | 18.9511 | 19.4429 | 19.9346 | 20.4264 | 20.9182 | 21.4099 | 21.9017 | 22.3935 | 22.8852 | 23.377 | 23.8688 | 24.3605 | 24.8523 | 25.3441 | 25.8358 | 26.3276 | 26.8194 | 27.3111 | 27.8029 | 28.2946 | 28.7864 | 29.2782 | 29.7699 | 30.2617 | 30.7535 | 31.2452 | 31.737 | 32.2288 | 32.7205 | 33.2123 | 33.7041 | 34.1958 | 34.6876 | 35.1794 | 35.6711 | 36.1629 | 36.6547 | 37.1464 | 37.6382 | 38.13 | 38.6217 | 39.1135 | 39.6052 | 40.097 | 40.5888 | 41.0805 | 41.5723 | 42.0641 | 42.5558 | 43.0476 | 43.5394 | 44.0311 | 44.5229 | 45.0147 | 45.5064 | 45.9982 | 46.49 | 46.9817 | 47.4735 | 47.9653 | 48.457 | 48.9488 | 49.4405 | 49.9323 | 50.4241 | 50.9158 | 51.4076 | 51.8994 | 52.3911 | 52.8829 | 53.3747 | 53.8664 | 54.3582 | 54.85 | 55.3417 | 55.8335 | 56.3253 | 56.817 | 57.3088 | 57.8006 | 58.2923 | 58.7841 | 59.2759 | 59.7676 | 60.2594 | 60.7511 | 61.2429 | 61.7347 | 62.2264 | 62.7182 | 63.21 | 63.7017 | 64.1935 | 64.6853 | 65.177 | 65.6688 | 66.1606 | 66.6523 | 67.1441 | 67.6359 | 68.1276 | 68.6194 | 69.1112 | 69.6029 | 70.0947 | 70.5864 | 71.0782 | 71.57 | 72.0617 | 72.5535 | 73.0453 | 73.537 | 74.0288 | 74.5206 | 75.0123 | 75.5041 | 75.9959 | 76.4876 | 76.9794 | 77.4712 | 77.9629 | 78.4547 | 78.9465 | 79.4382 | 79.93 | 80.4218 | 80.9135 | 81.4053 | 81.897 | 82.3888 | 82.8806 | 83.3723 | 83.8641 | 84.3559 | 84.8476 | 85.3394 | 85.8312 | 86.3229 | 86.8147 | 87.3065 | 87.7982 | 88.29 | 88.7818 | 89.2735 | 89.7653 | 90.2571 | 90.7488 | 91.2406 | 91.7324 | 92.2241 | 92.7159 | 93.2076 | 93.6994 | 94.1912 | 94.6829
Enersys Powersafe SBS B10 | 0.29535 | 0.29535 | 0.29535 | 0.29535 | 0.29535 | 0.29535 | 0.29535 | 0.411 | 0.52479 | 0.69049 | 0.85618 | 1.0688 | 1.2815 | 1.4941 | 2.7191 | 3.9441 | 6.2562 | 6.8128 | 7.3694 | 7.9087 | 8.4479 | 8.8365 | 9.2252 | 9.4847 | 9.7442 | 9.9657 | 10.1872 | 10.585 | 10.9827 | 11.3805 | 11.7783 | 12.1761 | 12.5739 | 12.9717 | 13.3694 | 13.7672 | 14.165 | 14.5628 | 14.9606 | 15.3584 | 15.7561 | 16.1539 | 16.5517 | 16.9495 | 17.3473 | 17.7451 | 18.1429 | 18.5406 | 18.9384 | 19.3362 | 19.734 | 20.1318 | 20.5296 | 20.9273 | 21.3251 | 21.7229 | 22.1207 | 22.5185 | 22.9163 | 23.3141 | 23.7118 | 24.1096 | 24.5074 | 24.9052 | 25.303 | 25.7008 | 26.0985 | 26.4963 | 26.8941 | 27.2919 | 27.6897 | 28.0875 | 28.4853 | 28.883 | 29.2808 | 29.6786 | 30.0764 | 30.4742 | 30.872 | 31.2697 | 31.6675 | 32.0653 | 32.4631 | 32.8609 | 33.2587 | 33.6565 | 34.0542 | 34.452 | 34.8498 | 35.2476 | 35.6454 | 36.0432 | 36.4409 | 36.8387 | 37.2365 | 37.6343 | 38.0321 | 38.4299 | 38.8277 | 39.2254 | 39.6232 | 40.021 | 40.4188 | 40.8166 | 41.2144 | 41.6121 | 42.0099 | 42.4077 | 42.8055 | 43.2033 | 43.6011 | 43.9989 | 44.3966 | 44.7944 | 45.1922 | 45.59 | 45.9878 | 46.3856 | 46.7833 | 47.1811 | 47.5789 | 47.9767 | 48.3745 | 48.7723 | 49.1701 | 49.5678 | 49.9656 | 50.3634 | 50.7612 | 51.159 | 51.5568 | 51.9545 | 52.3523 | 52.7501 | 53.1479 | 53.5457 | 53.9435 | 54.3413 | 54.739 | 55.1368 | 55.5346 | 55.9324 | 56.3302 | 56.728 | 57.1257 | 57.5235 | 57.9213 | 58.3191 | 58.7169 | 59.1147 | 59.5125 | 59.9102 | 60.308 | 60.7058 | 61.1036 | 61.5014 | 61.8992 | 62.2969 | 62.6947 | 63.0925 | 63.4903 | 63.8881 | 64.2859 | 64.6837 | 65.0814 | 65.4792 | 65.877 | 66.2748 | 66.6726 | 67.0704 | 67.4681 | 67.8659 | 68.2637 | 68.6615 | 69.0593 | 69.4571 | 69.8549 | 70.2526 | 70.6504 | 71.0482 | 71.446 | 71.8438 | 72.2416 | 72.6393 | 73.0371 | 73.4349 | 73.8327 | 74.2305 | 74.6283 | 75.0261 | 75.4238 | 75.8216 | 76.2194 | 76.6172 | 77.015 | 77.4128 | 77.8105 | 78.2083 | 78.6061
Enersys Powersafe SBS B14 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.43147 | 0.53652 | 0.6818 | 0.82708 | 1.0064 | 1.1857 | 1.365 | 2.3683 | 3.3716 | 5.2735 | 5.7592 | 6.2449 | 6.718 | 7.1911 | 7.6601 | 8.1291 | 8.6013 | 9.0735 | 9.5368 | 10 | 10.4581 | 10.9161 | 11.3742 | 11.8323 | 12.2904 | 12.7484 | 13.2065 | 13.6646 | 14.1227 | 14.5807 | 15.0388 | 15.4969 | 15.955 | 16.413 | 16.8711 | 17.3292 | 17.7873 | 18.2453 | 18.7034 | 19.1615 | 19.6196 | 20.0776 | 20.5357 | 20.9938 | 21.4519 | 21.9099 | 22.368 | 22.8261 | 23.2842 | 23.7422 | 24.2003 | 24.6584 | 25.1165 | 25.5745 | 26.0326 | 26.4907 | 26.9488 | 27.4068 | 27.8649 | 28.323 | 28.7811 | 29.2391 | 29.6972 | 30.1553 | 30.6134 | 31.0714 | 31.5295 | 31.9876 | 32.4457 | 32.9037 | 33.3618 | 33.8199 | 34.278 | 34.736 | 35.1941 | 35.6522 | 36.1102 | 36.5683 | 37.0264 | 37.4845 | 37.9425 | 38.4006 | 38.8587 | 39.3168 | 39.7748 | 40.2329 | 40.691 | 41.1491 | 41.6071 | 42.0652 | 42.5233 | 42.9814 | 43.4394 | 43.8975 | 44.3556 | 44.8137 | 45.2717 | 45.7298 | 46.1879 | 46.646 | 47.104 | 47.5621 | 48.0202 | 48.4783 | 48.9363 | 49.3944 | 49.8525 | 50.3106 | 50.7686 | 51.2267 | 51.6848 | 52.1429 | 52.6009 | 53.059 | 53.5171 | 53.9752 | 54.4332 | 54.8913 | 55.3494 | 55.8075 | 56.2655 | 56.7236 | 57.1817 | 57.6398 | 58.0978 | 58.5559 | 59.014 | 59.472 | 59.9301 | 60.3882 | 60.8463 | 61.3043 | 61.7624 | 62.2205 | 62.6786 | 63.1366 | 63.5947 | 64.0528 | 64.5109 | 64.9689 | 65.427 | 65.8851 | 66.3432 | 66.8012 | 67.2593 | 67.7174 | 68.1755 | 68.6335 | 69.0916 | 69.5497 | 70.0078 | 70.4658 | 70.9239 | 71.382 | 71.8401 | 72.2981 | 72.7562 | 73.2143 | 73.6724 | 74.1304 | 74.5885 | 75.0466 | 75.5047 | 75.9627 | 76.4208 | 76.8789 | 77.337 | 77.795 | 78.2531 | 78.7112 | 79.1693 | 79.6273 | 80.0854 | 80.5435 | 81.0016 | 81.4596 | 81.9177 | 82.3758 | 82.8339 | 83.2919 | 83.75 | 84.2081 | 84.6661 | 85.1242 | 85.5823 | 86.0404 | 86.4984 | 86.9565 | 87.4146 | 87.8727 | 88.3307 | 88.7888
Enersys Powersafe SBS C11 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.49728 | 0.61409 | 0.77676 | 0.93943 | 1.1372 | 1.3349 | 1.5327 | 2.6037 | 3.6747 | 5.6832 | 6.1568 | 6.6304 | 7.0962 | 7.562 | 7.9026 | 8.2432 | 8.6966 | 9.15 | 9.6135 | 10.0771 | 10.5031 | 10.9291 | 11.3552 | 11.7812 | 12.2072 | 12.6332 | 13.0593 | 13.4853 | 13.9113 | 14.3373 | 14.7634 | 15.1894 | 15.6154 | 16.0414 | 16.4674 | 16.8935 | 17.3195 | 17.7455 | 18.1715 | 18.5976 | 19.0236 | 19.4496 | 19.8756 | 20.3017 | 20.7277 | 21.1537 | 21.5797 | 22.0057 | 22.4318 | 22.8578 | 23.2838 | 23.7098 | 24.1359 | 24.5619 | 24.9879 | 25.4139 | 25.84 | 26.266 | 26.692 | 27.118 | 27.5441 | 27.9701 | 28.3961 | 28.8221 | 29.2481 | 29.6742 | 30.1002 | 30.5262 | 30.9522 | 31.3783 | 31.8043 | 32.2303 | 32.6563 | 33.0824 | 33.5084 | 33.9344 | 34.3604 | 34.7865 | 35.2125 | 35.6385 | 36.0645 | 36.4905 | 36.9166 | 37.3426 | 37.7686 | 38.1946 | 38.6207 | 39.0467 | 39.4727 | 39.8987 | 40.3248 | 40.7508 | 41.1768 | 41.6028 | 42.0288 | 42.4549 | 42.8809 | 43.3069 | 43.7329 | 44.159 | 44.585 | 45.011 | 45.437 | 45.8631 | 46.2891 | 46.7151 | 47.1411 | 47.5672 | 47.9932 | 48.4192 | 48.8452 | 49.2712 | 49.6973 | 50.1233 | 50.5493 | 50.9753 | 51.4014 | 51.8274 | 52.2534 | 52.6794 | 53.1055 | 53.5315 | 53.9575 | 54.3835 | 54.8096 | 55.2356 | 55.6616 | 56.0876 | 56.5136 | 56.9397 | 57.3657 | 57.7917 | 58.2177 | 58.6438 | 59.0698 | 59.4958 | 59.9218 | 60.3479 | 60.7739 | 61.1999 | 61.6259 | 62.052 | 62.478 | 62.904 | 63.33 | 63.756 | 64.1821 | 64.6081 | 65.0341 | 65.4601 | 65.8862 | 66.3122 | 66.7382 | 67.1642 | 67.5903 | 68.0163 | 68.4423 | 68.8683 | 69.2943 | 69.7204 | 70.1464 | 70.5724 | 70.9984 | 71.4245 | 71.8505 | 72.2765 | 72.7025 | 73.1286 | 73.5546 | 73.9806 | 74.4066 | 74.8327 | 75.2587 | 75.6847 | 76.1107 | 76.5367 | 76.9628 | 77.3888 | 77.8148 | 78.2408 | 78.6669 | 79.0929 | 79.5189 | 79.9449 | 80.371 | 80.797 | 81.223 | 81.649 | 82.0751 | 82.5011 | 82.9271 | 83.3531
1
Kt: 1.85V/Cell @ 15degC |  | 1s | 5s | 30s | 60s | 3m | 5m | 10m | 15m | 20m | 30m | 40m | 50m | 1h | 1.5h | 3h | 5h | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
Time | 0 | 0.00032777 | 0.0014389 | 0.0083833 | 0.016717 | 0.05005 | 0.083383 | 0.16672 | 0.25005 | 0.33338 | 0.50005 | 0.66672 | 0.83338 | 1 | 1.5 | 3 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200
Enersys Powersafe SBS 8 | 0.23965 | 0.23965 | 0.23965 | 0.23965 | 0.23965 | 0.23965 | 0.23965 | 0.3655 | 0.48297 | 0.64676 | 0.81056 | 1.0132 | 1.2158 | 1.4185 | 2.517 | 3.6156 | 5.6756 | 6.1735 | 6.6714 | 7.1383 | 7.6053 | 8.0666 | 8.5278 | 9.0075 | 9.4872 | 9.9367 | 10.3863 | 10.8147 | 11.2431 | 11.6716 | 12.1 | 12.5284 | 12.9569 | 13.3853 | 13.8137 | 14.2422 | 14.6706 | 15.099 | 15.5275 | 15.9559 | 16.3843 | 16.8128 | 17.2412 | 17.6696 | 18.0981 | 18.5265 | 18.9549 | 19.3834 | 19.8118 | 20.2402 | 20.6687 | 21.0971 | 21.5255 | 21.9539 | 22.3824 | 22.8108 | 23.2392 | 23.6677 | 24.0961 | 24.5245 | 24.953 | 25.3814 | 25.8098 | 26.2383 | 26.6667 | 27.0951 | 27.5236 | 27.952 | 28.3804 | 28.8089 | 29.2373 | 29.6657 | 30.0942 | 30.5226 | 30.951 | 31.3795 | 31.8079 | 32.2363 | 32.6648 | 33.0932 | 33.5216 | 33.9501 | 34.3785 | 34.8069 | 35.2354 | 35.6638 | 36.0922 | 36.5207 | 36.9491 | 37.3775 | 37.806 | 38.2344 | 38.6628 | 39.0913 | 39.5197 | 39.9481 | 40.3766 | 40.805 | 41.2334 | 41.6619 | 42.0903 | 42.5187 | 42.9472 | 43.3756 | 43.804 | 44.2325 | 44.6609 | 45.0893 | 45.5178 | 45.9462 | 46.3746 | 46.8031 | 47.2315 | 47.6599 | 48.0884 | 48.5168 | 48.9452 | 49.3737 | 49.8021 | 50.2305 | 50.659 | 51.0874 | 51.5158 | 51.9443 | 52.3727 | 52.8011 | 53.2296 | 53.658 | 54.0864 | 54.5149 | 54.9433 | 55.3717 | 55.8002 | 56.2286 | 56.657 | 57.0855 | 57.5139 | 57.9423 | 58.3708 | 58.7992 | 59.2276 | 59.6561 | 60.0845 | 60.5129 | 60.9414 | 61.3698 | 61.7982 | 62.2267 | 62.6551 | 63.0835 | 63.512 | 63.9404 | 64.3688 | 64.7973 | 65.2257 | 65.6541 | 66.0826 | 66.511 | 66.9394 | 67.3679 | 67.7963 | 68.2247 | 68.6532 | 69.0816 | 69.51 | 69.9385 | 70.3669 | 70.7953 | 71.2238 | 71.6522 | 72.0806 | 72.5091 | 72.9375 | 73.3659 | 73.7944 | 74.2228 | 74.6512 | 75.0797 | 75.5081 | 75.9365 | 76.365 | 76.7934 | 77.2218 | 77.6502 | 78.0787 | 78.5071 | 78.9355 | 79.364 | 79.7924 | 80.2208 | 80.6493 | 81.0777 | 81.5061 | 81.9346 | 82.363 | 82.7914 | 83.2199 | 83.6483 | 84.0767
Enersys Powersafe SBS 15 | 0.2569 | 0.2569 | 0.2569 | 0.2569 | 0.2569 | 0.2569 | 0.2569 | 0.38182 | 0.49645 | 0.65532 | 0.81419 | 1.0062 | 1.1983 | 1.3903 | 2.4596 | 3.5288 | 5.5554 | 6.0478 | 6.5402 | 7.0367 | 7.5332 | 8.0148 | 8.4964 | 8.9716 | 9.4467 | 9.9205 | 10.3944 | 10.8572 | 11.3199 | 11.7827 | 12.2454 | 12.7082 | 13.171 | 13.6337 | 14.0965 | 14.5593 | 15.022 | 15.4848 | 15.9476 | 16.4103 | 16.8731 | 17.3359 | 17.7986 | 18.2614 | 18.7241 | 19.1869 | 19.6497 | 20.1124 | 20.5752 | 21.038 | 21.5007 | 21.9635 | 22.4263 | 22.889 | 23.3518 | 23.8146 | 24.2773 | 24.7401 | 25.2028 | 25.6656 | 26.1284 | 26.5911 | 27.0539 | 27.5167 | 27.9794 | 28.4422 | 28.905 | 29.3677 | 29.8305 | 30.2932 | 30.756 | 31.2188 | 31.6815 | 32.1443 | 32.6071 | 33.0698 | 33.5326 | 33.9954 | 34.4581 | 34.9209 | 35.3837 | 35.8464 | 36.3092 | 36.7719 | 37.2347 | 37.6975 | 38.1602 | 38.623 | 39.0858 | 39.5485 | 40.0113 | 40.4741 | 40.9368 | 41.3996 | 41.8623 | 42.3251 | 42.7879 | 43.2506 | 43.7134 | 44.1762 | 44.6389 | 45.1017 | 45.5645 | 46.0272 | 46.49 | 46.9528 | 47.4155 | 47.8783 | 48.341 | 48.8038 | 49.2666 | 49.7293 | 50.1921 | 50.6549 | 51.1176 | 51.5804 | 52.0432 | 52.5059 | 52.9687 | 53.4315 | 53.8942 | 54.357 | 54.8197 | 55.2825 | 55.7453 | 56.208 | 56.6708 | 57.1336 | 57.5963 | 58.0591 | 58.5219 | 58.9846 | 59.4474 | 59.9101 | 60.3729 | 60.8357 | 61.2984 | 61.7612 | 62.224 | 62.6867 | 63.1495 | 63.6123 | 64.075 | 64.5378 | 65.0006 | 65.4633 | 65.9261 | 66.3888 | 66.8516 | 67.3144 | 67.7771 | 68.2399 | 68.7027 | 69.1654 | 69.6282 | 70.091 | 70.5537 | 71.0165 | 71.4793 | 71.942 | 72.4048 | 72.8675 | 73.3303 | 73.7931 | 74.2558 | 74.7186 | 75.1814 | 75.6441 | 76.1069 | 76.5697 | 77.0324 | 77.4952 | 77.9579 | 78.4207 | 78.8835 | 79.3462 | 79.809 | 80.2718 | 80.7345 | 81.1973 | 81.6601 | 82.1228 | 82.5856 | 83.0484 | 83.5111 | 83.9739 | 84.4366 | 84.8994 | 85.3622 | 85.8249 | 86.2877 | 86.7505 | 87.2132 | 87.676 | 88.1388 | 88.6015 | 89.0643 | 89.527 | 89.9898
Enersys Powersafe SBS 30 | 0.26115 | 0.26115 | 0.26115 | 0.26115 | 0.26115 | 0.26115 | 0.26115 | 0.38708 | 0.50422 | 0.66937 | 0.83452 | 1.0318 | 1.2291 | 1.4264 | 2.5132 | 3.6001 | 5.6644 | 6.1655 | 6.6665 | 7.1764 | 7.6863 | 8.1685 | 8.6508 | 9.1433 | 9.6359 | 9.9998 | 10.3637 | 10.7913 | 11.2189 | 11.6464 | 12.074 | 12.5016 | 12.9292 | 13.3568 | 13.7844 | 14.212 | 14.6396 | 15.0672 | 15.4948 | 15.9224 | 16.35 | 16.7776 | 17.2051 | 17.6327 | 18.0603 | 18.4879 | 18.9155 | 19.3431 | 19.7707 | 20.1983 | 20.6259 | 21.0535 | 21.4811 | 21.9087 | 22.3362 | 22.7638 | 23.1914 | 23.619 | 24.0466 | 24.4742 | 24.9018 | 25.3294 | 25.757 | 26.1846 | 26.6122 | 27.0398 | 27.4674 | 27.8949 | 28.3225 | 28.7501 | 29.1777 | 29.6053 | 30.0329 | 30.4605 | 30.8881 | 31.3157 | 31.7433 | 32.1709 | 32.5985 | 33.026 | 33.4536 | 33.8812 | 34.3088 | 34.7364 | 35.164 | 35.5916 | 36.0192 | 36.4468 | 36.8744 | 37.302 | 37.7296 | 38.1572 | 38.5847 | 39.0123 | 39.4399 | 39.8675 | 40.2951 | 40.7227 | 41.1503 | 41.5779 | 42.0055 | 42.4331 | 42.8607 | 43.2883 | 43.7158 | 44.1434 | 44.571 | 44.9986 | 45.4262 | 45.8538 | 46.2814 | 46.709 | 47.1366 | 47.5642 | 47.9918 | 48.4194 | 48.847 | 49.2745 | 49.7021 | 50.1297 | 50.5573 | 50.9849 | 51.4125 | 51.8401 | 52.2677 | 52.6953 | 53.1229 | 53.5505 | 53.9781 | 54.4056 | 54.8332 | 55.2608 | 55.6884 | 56.116 | 56.5436 | 56.9712 | 57.3988 | 57.8264 | 58.254 | 58.6816 | 59.1092 | 59.5368 | 59.9643 | 60.3919 | 60.8195 | 61.2471 | 61.6747 | 62.1023 | 62.5299 | 62.9575 | 63.3851 | 63.8127 | 64.2403 | 64.6679 | 65.0954 | 65.523 | 65.9506 | 66.3782 | 66.8058 | 67.2334 | 67.661 | 68.0886 | 68.5162 | 68.9438 | 69.3714 | 69.799 | 70.2266 | 70.6541 | 71.0817 | 71.5093 | 71.9369 | 72.3645 | 72.7921 | 73.2197 | 73.6473 | 74.0749 | 74.5025 | 74.9301 | 75.3577 | 75.7852 | 76.2128 | 76.6404 | 77.068 | 77.4956 | 77.9232 | 78.3508 | 78.7784 | 79.206 | 79.6336 | 80.0612 | 80.4888 | 80.9164 | 81.3439 | 81.7715 | 82.1991 | 82.6267 | 83.0543 | 83.4819 | 83.9095
Enersys Powersafe SBS 31 | 0.26115 | 0.26115 | 0.26115 | 0.26115 | 0.26115 | 0.26115 | 0.26115 | 0.38708 | 0.50422 | 0.66937 | 0.83452 | 1.0318 | 1.2291 | 1.4264 | 2.5132 | 3.6001 | 5.6644 | 6.1655 | 6.6665 | 7.1764 | 7.6863 | 8.1685 | 8.6508 | 9.1433 | 9.6359 | 9.9998 | 10.3637 | 10.7913 | 11.2189 | 11.6464 | 12.074 | 12.5016 | 12.9292 | 13.3568 | 13.7844 | 14.212 | 14.6396 | 15.0672 | 15.4948 | 15.9224 | 16.35 | 16.7776 | 17.2051 | 17.6327 | 18.0603 | 18.4879 | 18.9155 | 19.3431 | 19.7707 | 20.1983 | 20.6259 | 21.0535 | 21.4811 | 21.9087 | 22.3362 | 22.7638 | 23.1914 | 23.619 | 24.0466 | 24.4742 | 24.9018 | 25.3294 | 25.757 | 26.1846 | 26.6122 | 27.0398 | 27.4674 | 27.8949 | 28.3225 | 28.7501 | 29.1777 | 29.6053 | 30.0329 | 30.4605 | 30.8881 | 31.3157 | 31.7433 | 32.1709 | 32.5985 | 33.026 | 33.4536 | 33.8812 | 34.3088 | 34.7364 | 35.164 | 35.5916 | 36.0192 | 36.4468 | 36.8744 | 37.302 | 37.7296 | 38.1572 | 38.5847 | 39.0123 | 39.4399 | 39.8675 | 40.2951 | 40.7227 | 41.1503 | 41.5779 | 42.0055 | 42.4331 | 42.8607 | 43.2883 | 43.7158 | 44.1434 | 44.571 | 44.9986 | 45.4262 | 45.8538 | 46.2814 | 46.709 | 47.1366 | 47.5642 | 47.9918 | 48.4194 | 48.847 | 49.2745 | 49.7021 | 50.1297 | 50.5573 | 50.9849 | 51.4125 | 51.8401 | 52.2677 | 52.6953 | 53.1229 | 53.5505 | 53.9781 | 54.4056 | 54.8332 | 55.2608 | 55.6884 | 56.116 | 56.5436 | 56.9712 | 57.3988 | 57.8264 | 58.254 | 58.6816 | 59.1092 | 59.5368 | 59.9643 | 60.3919 | 60.8195 | 61.2471 | 61.6747 | 62.1023 | 62.5299 | 62.9575 | 63.3851 | 63.8127 | 64.2403 | 64.6679 | 65.0954 | 65.523 | 65.9506 | 66.3782 | 66.8058 | 67.2334 | 67.661 | 68.0886 | 68.5162 | 68.9438 | 69.3714 | 69.799 | 70.2266 | 70.6541 | 71.0817 | 71.5093 | 71.9369 | 72.3645 | 72.7921 | 73.2197 | 73.6473 | 74.0749 | 74.5025 | 74.9301 | 75.3577 | 75.7852 | 76.2128 | 76.6404 | 77.068 | 77.4956 | 77.9232 | 78.3508 | 78.7784 | 79.206 | 79.6336 | 80.0612 | 80.4888 | 80.9164 | 81.3439 | 81.7715 | 82.1991 | 82.6267 | 83.0543 | 83.4819 | 83.9095
Enersys Powersafe SBS 40 | 0.29513 | 0.29513 | 0.29513 | 0.29513 | 0.29513 | 0.29513 | 0.29513 | 0.41873 | 0.53262 | 0.6912 | 0.84977 | 1.0448 | 1.2397 | 1.4347 | 2.5167 | 3.5987 | 5.6896 | 6.2023 | 6.7151 | 7.2244 | 7.7338 | 8.1442 | 8.5546 | 9.1471 | 9.7397 | 10.0617 | 10.3836 | 10.8112 | 11.2387 | 11.6663 | 12.0939 | 12.5214 | 12.949 | 13.3765 | 13.8041 | 14.2317 | 14.6592 | 15.0868 | 15.5143 | 15.9419 | 16.3695 | 16.797 | 17.2246 | 17.6521 | 18.0797 | 18.5073 | 18.9348 | 19.3624 | 19.7899 | 20.2175 | 20.6451 | 21.0726 | 21.5002 | 21.9278 | 22.3553 | 22.7829 | 23.2104 | 23.638 | 24.0656 | 24.4931 | 24.9207 | 25.3482 | 25.7758 | 26.2034 | 26.6309 | 27.0585 | 27.486 | 27.9136 | 28.3412 | 28.7687 | 29.1963 | 29.6238 | 30.0514 | 30.479 | 30.9065 | 31.3341 | 31.7616 | 32.1892 | 32.6168 | 33.0443 | 33.4719 | 33.8995 | 34.327 | 34.7546 | 35.1821 | 35.6097 | 36.0373 | 36.4648 | 36.8924 | 37.3199 | 37.7475 | 38.1751 | 38.6026 | 39.0302 | 39.4577 | 39.8853 | 40.3129 | 40.7404 | 41.168 | 41.5955 | 42.0231 | 42.4507 | 42.8782 | 43.3058 | 43.7333 | 44.1609 | 44.5885 | 45.016 | 45.4436 | 45.8711 | 46.2987 | 46.7263 | 47.1538 | 47.5814 | 48.009 | 48.4365 | 48.8641 | 49.2916 | 49.7192 | 50.1468 | 50.5743 | 51.0019 | 51.4294 | 51.857 | 52.2846 | 52.7121 | 53.1397 | 53.5672 | 53.9948 | 54.4224 | 54.8499 | 55.2775 | 55.705 | 56.1326 | 56.5602 | 56.9877 | 57.4153 | 57.8428 | 58.2704 | 58.698 | 59.1255 | 59.5531 | 59.9806 | 60.4082 | 60.8358 | 61.2633 | 61.6909 | 62.1185 | 62.546 | 62.9736 | 63.4011 | 63.8287 | 64.2563 | 64.6838 | 65.1114 | 65.5389 | 65.9665 | 66.3941 | 66.8216 | 67.2492 | 67.6767 | 68.1043 | 68.5319 | 68.9594 | 69.387 | 69.8145 | 70.2421 | 70.6697 | 71.0972 | 71.5248 | 71.9523 | 72.3799 | 72.8075 | 73.235 | 73.6626 | 74.0901 | 74.5177 | 74.9453 | 75.3728 | 75.8004 | 76.228 | 76.6555 | 77.0831 | 77.5106 | 77.9382 | 78.3658 | 78.7933 | 79.2209 | 79.6484 | 80.076 | 80.5036 | 80.9311 | 81.3587 | 81.7862 | 82.2138 | 82.6414 | 83.0689 | 83.4965 | 83.924
Enersys Powersafe SBS 41 | 0.29513 | 0.29513 | 0.29513 | 0.29513 | 0.29513 | 0.29513 | 0.29513 | 0.41873 | 0.53262 | 0.6912 | 0.84977 | 1.0448 | 1.2397 | 1.4347 | 2.5167 | 3.5987 | 5.6896 | 6.2023 | 6.7151 | 7.2244 | 7.7338 | 8.1442 | 8.5546 | 9.1471 | 9.7397 | 10.0617 | 10.3836 | 10.8112 | 11.2387 | 11.6663 | 12.0939 | 12.5214 | 12.949 | 13.3765 | 13.8041 | 14.2317 | 14.6592 | 15.0868 | 15.5143 | 15.9419 | 16.3695 | 16.797 | 17.2246 | 17.6521 | 18.0797 | 18.5073 | 18.9348 | 19.3624 | 19.7899 | 20.2175 | 20.6451 | 21.0726 | 21.5002 | 21.9278 | 22.3553 | 22.7829 | 23.2104 | 23.638 | 24.0656 | 24.4931 | 24.9207 | 25.3482 | 25.7758 | 26.2034 | 26.6309 | 27.0585 | 27.486 | 27.9136 | 28.3412 | 28.7687 | 29.1963 | 29.6238 | 30.0514 | 30.479 | 30.9065 | 31.3341 | 31.7616 | 32.1892 | 32.6168 | 33.0443 | 33.4719 | 33.8995 | 34.327 | 34.7546 | 35.1821 | 35.6097 | 36.0373 | 36.4648 | 36.8924 | 37.3199 | 37.7475 | 38.1751 | 38.6026 | 39.0302 | 39.4577 | 39.8853 | 40.3129 | 40.7404 | 41.168 | 41.5955 | 42.0231 | 42.4507 | 42.8782 | 43.3058 | 43.7333 | 44.1609 | 44.5885 | 45.016 | 45.4436 | 45.8711 | 46.2987 | 46.7263 | 47.1538 | 47.5814 | 48.009 | 48.4365 | 48.8641 | 49.2916 | 49.7192 | 50.1468 | 50.5743 | 51.0019 | 51.4294 | 51.857 | 52.2846 | 52.7121 | 53.1397 | 53.5672 | 53.9948 | 54.4224 | 54.8499 | 55.2775 | 55.705 | 56.1326 | 56.5602 | 56.9877 | 57.4153 | 57.8428 | 58.2704 | 58.698 | 59.1255 | 59.5531 | 59.9806 | 60.4082 | 60.8358 | 61.2633 | 61.6909 | 62.1185 | 62.546 | 62.9736 | 63.4011 | 63.8287 | 64.2563 | 64.6838 | 65.1114 | 65.5389 | 65.9665 | 66.3941 | 66.8216 | 67.2492 | 67.6767 | 68.1043 | 68.5319 | 68.9594 | 69.387 | 69.8145 | 70.2421 | 70.6697 | 71.0972 | 71.5248 | 71.9523 | 72.3799 | 72.8075 | 73.235 | 73.6626 | 74.0901 | 74.5177 | 74.9453 | 75.3728 | 75.8004 | 76.228 | 76.6555 | 77.0831 | 77.5106 | 77.9382 | 78.3658 | 78.7933 | 79.2209 | 79.6484 | 80.076 | 80.5036 | 80.9311 | 81.3587 | 81.7862 | 82.2138 | 82.6414 | 83.0689 | 83.4965 | 83.924
Enersys Powersafe SBS 60 | 0.31952 | 0.31952 | 0.31952 | 0.31952 | 0.31952 | 0.31952 | 0.31952 | 0.44267 | 0.55714 | 0.7205 | 0.88386 | 1.0784 | 1.2729 | 1.4674 | 2.5272 | 3.5871 | 5.5899 | 6.0827 | 6.5755 | 7.0656 | 7.5557 | 8.0276 | 8.4996 | 8.9864 | 9.4732 | 9.9415 | 10.4098 | 10.8604 | 11.311 | 11.7616 | 12.2121 | 12.6627 | 13.1133 | 13.5639 | 14.0144 | 14.465 | 14.9156 | 15.3662 | 15.8167 | 16.2673 | 16.7179 | 17.1685 | 17.619 | 18.0696 | 18.5202 | 18.9708 | 19.4213 | 19.8719 | 20.3225 | 20.7731 | 21.2236 | 21.6742 | 22.1248 | 22.5754 | 23.0259 | 23.4765 | 23.9271 | 24.3777 | 24.8282 | 25.2788 | 25.7294 | 26.18 | 26.6305 | 27.0811 | 27.5317 | 27.9823 | 28.4328 | 28.8834 | 29.334 | 29.7846 | 30.2351 | 30.6857 | 31.1363 | 31.5869 | 32.0374 | 32.488 | 32.9386 | 33.3892 | 33.8397 | 34.2903 | 34.7409 | 35.1915 | 35.642 | 36.0926 | 36.5432 | 36.9938 | 37.4443 | 37.8949 | 38.3455 | 38.7961 | 39.2466 | 39.6972 | 40.1478 | 40.5984 | 41.0489 | 41.4995 | 41.9501 | 42.4007 | 42.8512 | 43.3018 | 43.7524 | 44.203 | 44.6535 | 45.1041 | 45.5547 | 46.0053 | 46.4558 | 46.9064 | 47.357 | 47.8076 | 48.2581 | 48.7087 | 49.1593 | 49.6099 | 50.0604 | 50.511 | 50.9616 | 51.4122 | 51.8627 | 52.3133 | 52.7639 | 53.2145 | 53.665 | 54.1156 | 54.5662 | 55.0168 | 55.4673 | 55.9179 | 56.3685 | 56.8191 | 57.2696 | 57.7202 | 58.1708 | 58.6214 | 59.0719 | 59.5225 | 59.9731 | 60.4237 | 60.8742 | 61.3248 | 61.7754 | 62.226 | 62.6765 | 63.1271 | 63.5777 | 64.0283 | 64.4788 | 64.9294 | 65.38 | 65.8306 | 66.2811 | 66.7317 | 67.1823 | 67.6329 | 68.0834 | 68.534 | 68.9846 | 69.4352 | 69.8857 | 70.3363 | 70.7869 | 71.2375 | 71.688 | 72.1386 | 72.5892 | 73.0398 | 73.4903 | 73.9409 | 74.3915 | 74.8421 | 75.2926 | 75.7432 | 76.1938 | 76.6444 | 77.0949 | 77.5455 | 77.9961 | 78.4467 | 78.8972 | 79.3478 | 79.7984 | 80.249 | 80.6995 | 81.1501 | 81.6007 | 82.0513 | 82.5018 | 82.9524 | 83.403 | 83.8536 | 84.3041 | 84.7547 | 85.2053 | 85.6559 | 86.1064 | 86.557 | 87.0076 | 87.4582 | 87.9087
Enersys Powersafe SBS 110 | 0.4315 | 0.4315 | 0.4315 | 0.4315 | 0.4315 | 0.4315 | 0.4315 | 0.55273 | 0.66853 | 0.83038 | 0.99223 | 1.1895 | 1.3868 | 1.5841 | 2.6503 | 3.7165 | 5.7097 | 6.1936 | 6.6775 | 7.1514 | 7.6252 | 8.0861 | 8.547 | 9.0295 | 9.512 | 9.9239 | 10.3358 | 10.7707 | 11.2057 | 11.6407 | 12.0757 | 12.5106 | 12.9456 | 13.3806 | 13.8155 | 14.2505 | 14.6855 | 15.1205 | 15.5554 | 15.9904 | 16.4254 | 16.8603 | 17.2953 | 17.7303 | 18.1653 | 18.6002 | 19.0352 | 19.4702 | 19.9051 | 20.3401 | 20.7751 | 21.2101 | 21.645 | 22.08 | 22.515 | 22.9499 | 23.3849 | 23.8199 | 24.2548 | 24.6898 | 25.1248 | 25.5598 | 25.9947 | 26.4297 | 26.8647 | 27.2996 | 27.7346 | 28.1696 | 28.6046 | 29.0395 | 29.4745 | 29.9095 | 30.3444 | 30.7794 | 31.2144 | 31.6494 | 32.0843 | 32.5193 | 32.9543 | 33.3892 | 33.8242 | 34.2592 | 34.6942 | 35.1291 | 35.5641 | 35.9991 | 36.434 | 36.869 | 37.304 | 37.7389 | 38.1739 | 38.6089 | 39.0439 | 39.4788 | 39.9138 | 40.3488 | 40.7837 | 41.2187 | 41.6537 | 42.0887 | 42.5236 | 42.9586 | 43.3936 | 43.8285 | 44.2635 | 44.6985 | 45.1335 | 45.5684 | 46.0034 | 46.4384 | 46.8733 | 47.3083 | 47.7433 | 48.1783 | 48.6132 | 49.0482 | 49.4832 | 49.9181 | 50.3531 | 50.7881 | 51.223 | 51.658 | 52.093 | 52.528 | 52.9629 | 53.3979 | 53.8329 | 54.2678 | 54.7028 | 55.1378 | 55.5728 | 56.0077 | 56.4427 | 56.8777 | 57.3126 | 57.7476 | 58.1826 | 58.6176 | 59.0525 | 59.4875 | 59.9225 | 60.3574 | 60.7924 | 61.2274 | 61.6623 | 62.0973 | 62.5323 | 62.9673 | 63.4022 | 63.8372 | 64.2722 | 64.7071 | 65.1421 | 65.5771 | 66.0121 | 66.447 | 66.882 | 67.317 | 67.7519 | 68.1869 | 68.6219 | 69.0569 | 69.4918 | 69.9268 | 70.3618 | 70.7967 | 71.2317 | 71.6667 | 72.1017 | 72.5366 | 72.9716 | 73.4066 | 73.8415 | 74.2765 | 74.7115 | 75.1464 | 75.5814 | 76.0164 | 76.4514 | 76.8863 | 77.3213 | 77.7563 | 78.1912 | 78.6262 | 79.0612 | 79.4962 | 79.9311 | 80.3661 | 80.8011 | 81.236 | 81.671 | 82.106 | 82.541 | 82.9759 | 83.4109 | 83.8459 | 84.2808 | 84.7158 | 85.1508
Enersys Powersafe SBS 130 | 0.3882 | 0.3882 | 0.3882 | 0.3882 | 0.3882 | 0.3882 | 0.3882 | 0.52791 | 0.65314 | 0.82281 | 0.99248 | 1.1933 | 1.3941 | 1.5949 | 2.6565 | 3.7181 | 5.7001 | 6.1915 | 6.6829 | 7.1522 | 7.6215 | 8.0951 | 8.5686 | 9.0181 | 9.4675 | 9.9355 | 10.4035 | 10.8577 | 11.312 | 11.7662 | 12.2204 | 12.6746 | 13.1288 | 13.5831 | 14.0373 | 14.4915 | 14.9457 | 15.3999 | 15.8541 | 16.3084 | 16.7626 | 17.2168 | 17.671 | 18.1252 | 18.5794 | 19.0337 | 19.4879 | 19.9421 | 20.3963 | 20.8505 | 21.3048 | 21.759 | 22.2132 | 22.6674 | 23.1216 | 23.5758 | 24.0301 | 24.4843 | 24.9385 | 25.3927 | 25.8469 | 26.3011 | 26.7554 | 27.2096 | 27.6638 | 28.118 | 28.5722 | 29.0265 | 29.4807 | 29.9349 | 30.3891 | 30.8433 | 31.2975 | 31.7518 | 32.206 | 32.6602 | 33.1144 | 33.5686 | 34.0228 | 34.4771 | 34.9313 | 35.3855 | 35.8397 | 36.2939 | 36.7481 | 37.2024 | 37.6566 | 38.1108 | 38.565 | 39.0192 | 39.4735 | 39.9277 | 40.3819 | 40.8361 | 41.2903 | 41.7445 | 42.1988 | 42.653 | 43.1072 | 43.5614 | 44.0156 | 44.4698 | 44.9241 | 45.3783 | 45.8325 | 46.2867 | 46.7409 | 47.1952 | 47.6494 | 48.1036 | 48.5578 | 49.012 | 49.4662 | 49.9205 | 50.3747 | 50.8289 | 51.2831 | 51.7373 | 52.1915 | 52.6458 | 53.1 | 53.5542 | 54.0084 | 54.4626 | 54.9169 | 55.3711 | 55.8253 | 56.2795 | 56.7337 | 57.1879 | 57.6422 | 58.0964 | 58.5506 | 59.0048 | 59.459 | 59.9132 | 60.3675 | 60.8217 | 61.2759 | 61.7301 | 62.1843 | 62.6386 | 63.0928 | 63.547 | 64.0012 | 64.4554 | 64.9096 | 65.3639 | 65.8181 | 66.2723 | 66.7265 | 67.1807 | 67.6349 | 68.0892 | 68.5434 | 68.9976 | 69.4518 | 69.906 | 70.3602 | 70.8145 | 71.2687 | 71.7229 | 72.1771 | 72.6313 | 73.0856 | 73.5398 | 73.994 | 74.4482 | 74.9024 | 75.3566 | 75.8109 | 76.2651 | 76.7193 | 77.1735 | 77.6277 | 78.0819 | 78.5362 | 78.9904 | 79.4446 | 79.8988 | 80.353 | 80.8073 | 81.2615 | 81.7157 | 82.1699 | 82.6241 | 83.0783 | 83.5326 | 83.9868 | 84.441 | 84.8952 | 85.3494 | 85.8036 | 86.2579 | 86.7121 | 87.1663 | 87.6205 | 88.0747 | 88.529
Enersys Powersafe SBS 300 | 0.40838 | 0.40838 | 0.40838 | 0.40838 | 0.40838 | 0.40838 | 0.40838 | 0.53418 | 0.65957 | 0.8561 | 1.0526 | 1.278 | 1.5033 | 1.7286 | 2.9103 | 4.092 | 6.127 | 6.5801 | 7.0332 | 7.4695 | 7.9058 | 8.3566 | 8.8074 | 9.2505 | 9.6936 | 10.0367 | 10.3798 | 10.7842 | 11.1885 | 11.5928 | 11.9972 | 12.4015 | 12.8058 | 13.2102 | 13.6145 | 14.0188 | 14.4231 | 14.8275 | 15.2318 | 15.6361 | 16.0405 | 16.4448 | 16.8491 | 17.2535 | 17.6578 | 18.0621 | 18.4665 | 18.8708 | 19.2751 | 19.6794 | 20.0838 | 20.4881 | 20.8924 | 21.2968 | 21.7011 | 22.1054 | 22.5098 | 22.9141 | 23.3184 | 23.7228 | 24.1271 | 24.5314 | 24.9357 | 25.3401 | 25.7444 | 26.1487 | 26.5531 | 26.9574 | 27.3617 | 27.7661 | 28.1704 | 28.5747 | 28.9791 | 29.3834 | 29.7877 | 30.192 | 30.5964 | 31.0007 | 31.405 | 31.8094 | 32.2137 | 32.618 | 33.0224 | 33.4267 | 33.831 | 34.2354 | 34.6397 | 35.044 | 35.4483 | 35.8527 | 36.257 | 36.6613 | 37.0657 | 37.47 | 37.8743 | 38.2787 | 38.683 | 39.0873 | 39.4917 | 39.896 | 40.3003 | 40.7046 | 41.109 | 41.5133 | 41.9176 | 42.322 | 42.7263 | 43.1306 | 43.535 | 43.9393 | 44.3436 | 44.748 | 45.1523 | 45.5566 | 45.9609 | 46.3653 | 46.7696 | 47.1739 | 47.5783 | 47.9826 | 48.3869 | 48.7913 | 49.1956 | 49.5999 | 50.0043 | 50.4086 | 50.8129 | 51.2172 | 51.6216 | 52.0259 | 52.4302 | 52.8346 | 53.2389 | 53.6432 | 54.0476 | 54.4519 | 54.8562 | 55.2606 | 55.6649 | 56.0692 | 56.4735 | 56.8779 | 57.2822 | 57.6865 | 58.0909 | 58.4952 | 58.8995 | 59.3039 | 59.7082 | 60.1125 | 60.5169 | 60.9212 | 61.3255 | 61.7298 | 62.1342 | 62.5385 | 62.9428 | 63.3472 | 63.7515 | 64.1558 | 64.5602 | 64.9645 | 65.3688 | 65.7732 | 66.1775 | 66.5818 | 66.9861 | 67.3905 | 67.7948 | 68.1991 | 68.6035 | 69.0078 | 69.4121 | 69.8165 | 70.2208 | 70.6251 | 71.0295 | 71.4338 | 71.8381 | 72.2424 | 72.6468 | 73.0511 | 73.4554 | 73.8598 | 74.2641 | 74.6684 | 75.0728 | 75.4771 | 75.8814 | 76.2858 | 76.6901 | 77.0944 | 77.4987 | 77.9031 | 78.3074 | 78.7117 | 79.1161 | 79.5204 | 79.9247
Enersys Powersafe SBS 390 | 0.45234 | 0.45234 | 0.45234 | 0.45234 | 0.45234 | 0.45234 | 0.45234 | 0.56494 | 0.67545 | 0.82986 | 0.98428 | 1.1754 | 1.3665 | 1.5576 | 2.5981 | 3.6386 | 5.6229 | 6.1209 | 6.6188 | 7.1081 | 7.5973 | 8.0427 | 8.4881 | 8.9778 | 9.4675 | 9.8997 | 10.332 | 10.7861 | 11.2401 | 11.6942 | 12.1483 | 12.6023 | 13.0564 | 13.5105 | 13.9645 | 14.4186 | 14.8726 | 15.3267 | 15.7808 | 16.2348 | 16.6889 | 17.143 | 17.597 | 18.0511 | 18.5052 | 18.9592 | 19.4133 | 19.8674 | 20.3214 | 20.7755 | 21.2295 | 21.6836 | 22.1377 | 22.5917 | 23.0458 | 23.4999 | 23.9539 | 24.408 | 24.8621 | 25.3161 | 25.7702 | 26.2243 | 26.6783 | 27.1324 | 27.5864 | 28.0405 | 28.4946 | 28.9486 | 29.4027 | 29.8568 | 30.3108 | 30.7649 | 31.219 | 31.673 | 32.1271 | 32.5812 | 33.0352 | 33.4893 | 33.9433 | 34.3974 | 34.8515 | 35.3055 | 35.7596 | 36.2137 | 36.6677 | 37.1218 | 37.5759 | 38.0299 | 38.484 | 38.9381 | 39.3921 | 39.8462 | 40.3002 | 40.7543 | 41.2084 | 41.6624 | 42.1165 | 42.5706 | 43.0246 | 43.4787 | 43.9328 | 44.3868 | 44.8409 | 45.295 | 45.749 | 46.2031 | 46.6571 | 47.1112 | 47.5653 | 48.0193 | 48.4734 | 48.9275 | 49.3815 | 49.8356 | 50.2897 | 50.7437 | 51.1978 | 51.6519 | 52.1059 | 52.56 | 53.014 | 53.4681 | 53.9222 | 54.3762 | 54.8303 | 55.2844 | 55.7384 | 56.1925 | 56.6466 | 57.1006 | 57.5547 | 58.0088 | 58.4628 | 58.9169 | 59.3709 | 59.825 | 60.2791 | 60.7331 | 61.1872 | 61.6413 | 62.0953 | 62.5494 | 63.0035 | 63.4575 | 63.9116 | 64.3657 | 64.8197 | 65.2738 | 65.7278 | 66.1819 | 66.636 | 67.09 | 67.5441 | 67.9982 | 68.4522 | 68.9063 | 69.3604 | 69.8144 | 70.2685 | 70.7226 | 71.1766 | 71.6307 | 72.0847 | 72.5388 | 72.9929 | 73.4469 | 73.901 | 74.3551 | 74.8091 | 75.2632 | 75.7173 | 76.1713 | 76.6254 | 77.0795 | 77.5335 | 77.9876 | 78.4416 | 78.8957 | 79.3498 | 79.8038 | 80.2579 | 80.712 | 81.166 | 81.6201 | 82.0742 | 82.5282 | 82.9823 | 83.4364 | 83.8904 | 84.3445 | 84.7985 | 85.2526 | 85.7067 | 86.1607 | 86.6148 | 87.0689 | 87.5229 | 87.977 | 88.4311
Enersys Powersafe SBS B8 | 0.22732 | 0.22732 | 0.22732 | 0.22732 | 0.22732 | 0.22732 | 0.22732 | 0.38963 | 0.52845 | 0.70645 | 0.88444 | 1.085 | 1.2856 | 1.4862 | 2.5296 | 3.5731 | 5.5579 | 6.0578 | 6.5578 | 7.0647 | 7.5716 | 7.9567 | 8.3419 | 8.8399 | 9.3379 | 9.8428 | 10.3477 | 10.8515 | 11.3554 | 11.8593 | 12.3631 | 12.867 | 13.3708 | 13.8747 | 14.3785 | 14.8824 | 15.3863 | 15.8901 | 16.394 | 16.8978 | 17.4017 | 17.9055 | 18.4094 | 18.9133 | 19.4171 | 19.921 | 20.4248 | 20.9287 | 21.4326 | 21.9364 | 22.4403 | 22.9441 | 23.448 | 23.9518 | 24.4557 | 24.9596 | 25.4634 | 25.9673 | 26.4711 | 26.975 | 27.4788 | 27.9827 | 28.4866 | 28.9904 | 29.4943 | 29.9981 | 30.502 | 31.0058 | 31.5097 | 32.0136 | 32.5174 | 33.0213 | 33.5251 | 34.029 | 34.5329 | 35.0367 | 35.5406 | 36.0444 | 36.5483 | 37.0521 | 37.556 | 38.0599 | 38.5637 | 39.0676 | 39.5714 | 40.0753 | 40.5791 | 41.083 | 41.5869 | 42.0907 | 42.5946 | 43.0984 | 43.6023 | 44.1061 | 44.61 | 45.1139 | 45.6177 | 46.1216 | 46.6254 | 47.1293 | 47.6332 | 48.137 | 48.6409 | 49.1447 | 49.6486 | 50.1524 | 50.6563 | 51.1602 | 51.664 | 52.1679 | 52.6717 | 53.1756 | 53.6794 | 54.1833 | 54.6872 | 55.191 | 55.6949 | 56.1987 | 56.7026 | 57.2065 | 57.7103 | 58.2142 | 58.718 | 59.2219 | 59.7257 | 60.2296 | 60.7335 | 61.2373 | 61.7412 | 62.245 | 62.7489 | 63.2527 | 63.7566 | 64.2605 | 64.7643 | 65.2682 | 65.772 | 66.2759 | 66.7797 | 67.2836 | 67.7875 | 68.2913 | 68.7952 | 69.299 | 69.8029 | 70.3068 | 70.8106 | 71.3145 | 71.8183 | 72.3222 | 72.826 | 73.3299 | 73.8338 | 74.3376 | 74.8415 | 75.3453 | 75.8492 | 76.353 | 76.8569 | 77.3608 | 77.8646 | 78.3685 | 78.8723 | 79.3762 | 79.88 | 80.3839 | 80.8878 | 81.3916 | 81.8955 | 82.3993 | 82.9032 | 83.4071 | 83.9109 | 84.4148 | 84.9186 | 85.4225 | 85.9263 | 86.4302 | 86.9341 | 87.4379 | 87.9418 | 88.4456 | 88.9495 | 89.4533 | 89.9572 | 90.4611 | 90.9649 | 91.4688 | 91.9726 | 92.4765 | 92.9803 | 93.4842 | 93.9881 | 94.4919 | 94.9958 | 95.4996 | 96.0035 | 96.5074 | 97.0112
Enersys Powersafe SBS B10 | 0.32138 | 0.32138 | 0.32138 | 0.32138 | 0.32138 | 0.32138 | 0.32138 | 0.44052 | 0.55829 | 0.72977 | 0.90124 | 1.1202 | 1.3391 | 1.558 | 2.812 | 4.0661 | 6.4298 | 7.0018 | 7.5739 | 8.1281 | 8.6823 | 9.072 | 9.4617 | 9.7279 | 9.9941 | 10.2159 | 10.4377 | 10.8452 | 11.2528 | 11.6604 | 12.0679 | 12.4755 | 12.8831 | 13.2906 | 13.6982 | 14.1058 | 14.5133 | 14.9209 | 15.3285 | 15.736 | 16.1436 | 16.5512 | 16.9587 | 17.3663 | 17.7739 | 18.1814 | 18.589 | 18.9966 | 19.4041 | 19.8117 | 20.2193 | 20.6268 | 21.0344 | 21.442 | 21.8495 | 22.2571 | 22.6647 | 23.0722 | 23.4798 | 23.8874 | 24.2949 | 24.7025 | 25.1101 | 25.5176 | 25.9252 | 26.3327 | 26.7403 | 27.1479 | 27.5554 | 27.963 | 28.3706 | 28.7781 | 29.1857 | 29.5933 | 30.0008 | 30.4084 | 30.816 | 31.2235 | 31.6311 | 32.0387 | 32.4462 | 32.8538 | 33.2614 | 33.6689 | 34.0765 | 34.4841 | 34.8916 | 35.2992 | 35.7068 | 36.1143 | 36.5219 | 36.9295 | 37.337 | 37.7446 | 38.1522 | 38.5597 | 38.9673 | 39.3749 | 39.7824 | 40.19 | 40.5976 | 41.0051 | 41.4127 | 41.8203 | 42.2278 | 42.6354 | 43.043 | 43.4505 | 43.8581 | 44.2657 | 44.6732 | 45.0808 | 45.4884 | 45.8959 | 46.3035 | 46.7111 | 47.1186 | 47.5262 | 47.9338 | 48.3413 | 48.7489 | 49.1565 | 49.564 | 49.9716 | 50.3792 | 50.7867 | 51.1943 | 51.6019 | 52.0094 | 52.417 | 52.8246 | 53.2321 | 53.6397 | 54.0472 | 54.4548 | 54.8624 | 55.2699 | 55.6775 | 56.0851 | 56.4926 | 56.9002 | 57.3078 | 57.7153 | 58.1229 | 58.5305 | 58.938 | 59.3456 | 59.7532 | 60.1607 | 60.5683 | 60.9759 | 61.3834 | 61.791 | 62.1986 | 62.6061 | 63.0137 | 63.4213 | 63.8288 | 64.2364 | 64.644 | 65.0515 | 65.4591 | 65.8667 | 66.2742 | 66.6818 | 67.0894 | 67.4969 | 67.9045 | 68.3121 | 68.7196 | 69.1272 | 69.5348 | 69.9423 | 70.3499 | 70.7575 | 71.165 | 71.5726 | 71.9802 | 72.3877 | 72.7953 | 73.2029 | 73.6104 | 74.018 | 74.4256 | 74.8331 | 75.2407 | 75.6483 | 76.0558 | 76.4634 | 76.871 | 77.2785 | 77.6861 | 78.0937 | 78.5012 | 78.9088 | 79.3164 | 79.7239 | 80.1315 | 80.539
Enersys Powersafe SBS B14 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.46245 | 0.57077 | 0.72069 | 0.87061 | 1.0549 | 1.2391 | 1.4234 | 2.4496 | 3.4759 | 5.4198 | 5.919 | 6.4182 | 6.9045 | 7.3907 | 7.8641 | 8.3376 | 8.8219 | 9.3062 | 9.776 | 10.2459 | 10.7152 | 11.1846 | 11.6539 | 12.1233 | 12.5926 | 13.0619 | 13.5313 | 14.0006 | 14.4699 | 14.9393 | 15.4086 | 15.878 | 16.3473 | 16.8166 | 17.286 | 17.7553 | 18.2247 | 18.694 | 19.1633 | 19.6327 | 20.102 | 20.5714 | 21.0407 | 21.51 | 21.9794 | 22.4487 | 22.918 | 23.3874 | 23.8567 | 24.3261 | 24.7954 | 25.2647 | 25.7341 | 26.2034 | 26.6728 | 27.1421 | 27.6114 | 28.0808 | 28.5501 | 29.0194 | 29.4888 | 29.9581 | 30.4275 | 30.8968 | 31.3661 | 31.8355 | 32.3048 | 32.7742 | 33.2435 | 33.7128 | 34.1822 | 34.6515 | 35.1209 | 35.5902 | 36.0595 | 36.5289 | 36.9982 | 37.4675 | 37.9369 | 38.4062 | 38.8756 | 39.3449 | 39.8142 | 40.2836 | 40.7529 | 41.2223 | 41.6916 | 42.1609 | 42.6303 | 43.0996 | 43.5689 | 44.0383 | 44.5076 | 44.977 | 45.4463 | 45.9156 | 46.385 | 46.8543 | 47.3237 | 47.793 | 48.2623 | 48.7317 | 49.201 | 49.6703 | 50.1397 | 50.609 | 51.0784 | 51.5477 | 52.017 | 52.4864 | 52.9557 | 53.4251 | 53.8944 | 54.3637 | 54.8331 | 55.3024 | 55.7718 | 56.2411 | 56.7104 | 57.1798 | 57.6491 | 58.1184 | 58.5878 | 59.0571 | 59.5265 | 59.9958 | 60.4651 | 60.9345 | 61.4038 | 61.8732 | 62.3425 | 62.8118 | 63.2812 | 63.7505 | 64.2198 | 64.6892 | 65.1585 | 65.6279 | 66.0972 | 66.5665 | 67.0359 | 67.5052 | 67.9746 | 68.4439 | 68.9132 | 69.3826 | 69.8519 | 70.3213 | 70.7906 | 71.2599 | 71.7293 | 72.1986 | 72.6679 | 73.1373 | 73.6066 | 74.076 | 74.5453 | 75.0146 | 75.484 | 75.9533 | 76.4227 | 76.892 | 77.3613 | 77.8307 | 78.3 | 78.7693 | 79.2387 | 79.708 | 80.1774 | 80.6467 | 81.116 | 81.5854 | 82.0547 | 82.5241 | 82.9934 | 83.4627 | 83.9321 | 84.4014 | 84.8707 | 85.3401 | 85.8094 | 86.2788 | 86.7481 | 87.2174 | 87.6868 | 88.1561 | 88.6255 | 89.0948 | 89.5641 | 90.0335 | 90.5028 | 90.9722
Enersys Powersafe SBS C11 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.53299 | 0.65329 | 0.82108 | 0.98887 | 1.192 | 1.3951 | 1.5982 | 2.6933 | 3.7883 | 5.8409 | 6.3277 | 6.8144 | 7.2931 | 7.7718 | 8.1132 | 8.4546 | 8.9196 | 9.3846 | 9.8548 | 10.3249 | 10.7614 | 11.1979 | 11.6344 | 12.0709 | 12.5074 | 12.9439 | 13.3804 | 13.8169 | 14.2534 | 14.6899 | 15.1264 | 15.5629 | 15.9994 | 16.4359 | 16.8724 | 17.3089 | 17.7454 | 18.1819 | 18.6184 | 19.0549 | 19.4914 | 19.9279 | 20.3644 | 20.8009 | 21.2374 | 21.6739 | 22.1104 | 22.5469 | 22.9834 | 23.4199 | 23.8564 | 24.2929 | 24.7294 | 25.1659 | 25.6024 | 26.0389 | 26.4754 | 26.9119 | 27.3484 | 27.7849 | 28.2214 | 28.6579 | 29.0944 | 29.5309 | 29.9674 | 30.4039 | 30.8404 | 31.2769 | 31.7134 | 32.1499 | 32.5864 | 33.0229 | 33.4594 | 33.8959 | 34.3324 | 34.7689 | 35.2054 | 35.6419 | 36.0784 | 36.5149 | 36.9514 | 37.3879 | 37.8244 | 38.2609 | 38.6974 | 39.1339 | 39.5704 | 40.0068 | 40.4433 | 40.8798 | 41.3163 | 41.7528 | 42.1893 | 42.6258 | 43.0623 | 43.4988 | 43.9353 | 44.3718 | 44.8083 | 45.2448 | 45.6813 | 46.1178 | 46.5543 | 46.9908 | 47.4273 | 47.8638 | 48.3003 | 48.7368 | 49.1733 | 49.6098 | 50.0463 | 50.4828 | 50.9193 | 51.3558 | 51.7923 | 52.2288 | 52.6653 | 53.1018 | 53.5383 | 53.9748 | 54.4113 | 54.8478 | 55.2843 | 55.7208 | 56.1573 | 56.5938 | 57.0303 | 57.4668 | 57.9033 | 58.3398 | 58.7763 | 59.2128 | 59.6493 | 60.0858 | 60.5223 | 60.9588 | 61.3953 | 61.8318 | 62.2683 | 62.7048 | 63.1413 | 63.5778 | 64.0143 | 64.4508 | 64.8873 | 65.3238 | 65.7603 | 66.1968 | 66.6333 | 67.0698 | 67.5063 | 67.9428 | 68.3793 | 68.8158 | 69.2523 | 69.6888 | 70.1253 | 70.5618 | 70.9983 | 71.4348 | 71.8713 | 72.3078 | 72.7443 | 73.1808 | 73.6173 | 74.0538 | 74.4903 | 74.9268 | 75.3633 | 75.7998 | 76.2363 | 76.6728 | 77.1093 | 77.5458 | 77.9823 | 78.4188 | 78.8553 | 79.2918 | 79.7283 | 80.1648 | 80.6013 | 81.0378 | 81.4743 | 81.9108 | 82.3473 | 82.7838 | 83.2203 | 83.6568 | 84.0933 | 84.5298 | 84.9663 | 85.4028
1
Kt: 1.85V/Cell @ 5degC |  | 1s | 5s | 30s | 60s | 3m | 5m | 10m | 15m | 20m | 30m | 40m | 50m | 1h | 1.5h | 3h | 5h | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
Time | 0 | 0.00032777 | 0.0014389 | 0.0083833 | 0.016717 | 0.05005 | 0.083383 | 0.16672 | 0.25005 | 0.33338 | 0.50005 | 0.66672 | 0.83338 | 1 | 1.5 | 3 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200
Enersys Powersafe SBS 8 | 0.28865 | 0.28865 | 0.28865 | 0.28865 | 0.28865 | 0.28865 | 0.28865 | 0.42895 | 0.5591 | 0.7379 | 0.9167 | 1.1365 | 1.3564 | 1.5762 | 2.7518 | 3.9273 | 6.136 | 6.6742 | 7.2125 | 7.7173 | 8.2222 | 8.6746 | 9.1269 | 9.6403 | 10.1537 | 10.6222 | 11.0908 | 11.5483 | 12.0058 | 12.4633 | 12.9208 | 13.3783 | 13.8358 | 14.2933 | 14.7508 | 15.2083 | 15.6657 | 16.1232 | 16.5807 | 17.0382 | 17.4957 | 17.9532 | 18.4107 | 18.8682 | 19.3257 | 19.7832 | 20.2407 | 20.6982 | 21.1557 | 21.6132 | 22.0707 | 22.5282 | 22.9857 | 23.4432 | 23.9007 | 24.3582 | 24.8157 | 25.2731 | 25.7306 | 26.1881 | 26.6456 | 27.1031 | 27.5606 | 28.0181 | 28.4756 | 28.9331 | 29.3906 | 29.8481 | 30.3056 | 30.7631 | 31.2206 | 31.6781 | 32.1356 | 32.5931 | 33.0506 | 33.5081 | 33.9656 | 34.4231 | 34.8805 | 35.338 | 35.7955 | 36.253 | 36.7105 | 37.168 | 37.6255 | 38.083 | 38.5405 | 38.998 | 39.4555 | 39.913 | 40.3705 | 40.828 | 41.2855 | 41.743 | 42.2005 | 42.658 | 43.1155 | 43.573 | 44.0305 | 44.488 | 44.9454 | 45.4029 | 45.8604 | 46.3179 | 46.7754 | 47.2329 | 47.6904 | 48.1479 | 48.6054 | 49.0629 | 49.5204 | 49.9779 | 50.4354 | 50.8929 | 51.3504 | 51.8079 | 52.2654 | 52.7229 | 53.1804 | 53.6379 | 54.0954 | 54.5528 | 55.0103 | 55.4678 | 55.9253 | 56.3828 | 56.8403 | 57.2978 | 57.7553 | 58.2128 | 58.6703 | 59.1278 | 59.5853 | 60.0428 | 60.5003 | 60.9578 | 61.4153 | 61.8728 | 62.3303 | 62.7878 | 63.2453 | 63.7028 | 64.1602 | 64.6177 | 65.0752 | 65.5327 | 65.9902 | 66.4477 | 66.9052 | 67.3627 | 67.8202 | 68.2777 | 68.7352 | 69.1927 | 69.6502 | 70.1077 | 70.5652 | 71.0227 | 71.4802 | 71.9377 | 72.3952 | 72.8527 | 73.3102 | 73.7676 | 74.2251 | 74.6826 | 75.1401 | 75.5976 | 76.0551 | 76.5126 | 76.9701 | 77.4276 | 77.8851 | 78.3426 | 78.8001 | 79.2576 | 79.7151 | 80.1726 | 80.6301 | 81.0876 | 81.5451 | 82.0026 | 82.4601 | 82.9176 | 83.375 | 83.8325 | 84.29 | 84.7475 | 85.205 | 85.6625 | 86.12 | 86.5775 | 87.035 | 87.4925 | 87.95 | 88.4075 | 88.865 | 89.3225 | 89.78
Enersys Powersafe SBS 15 | 0.30942 | 0.30942 | 0.30942 | 0.30942 | 0.30942 | 0.30942 | 0.30942 | 0.44809 | 0.57471 | 0.74776 | 0.92081 | 1.1289 | 1.3369 | 1.545 | 2.6891 | 3.8331 | 6.006 | 6.5384 | 7.0707 | 7.6075 | 8.1443 | 8.6188 | 9.0933 | 9.6018 | 10.1103 | 10.6049 | 11.0995 | 11.5936 | 12.0878 | 12.5819 | 13.0761 | 13.5703 | 14.0644 | 14.5586 | 15.0527 | 15.5469 | 16.041 | 16.5352 | 17.0293 | 17.5235 | 18.0177 | 18.5118 | 19.006 | 19.5001 | 19.9943 | 20.4884 | 20.9826 | 21.4767 | 21.9709 | 22.465 | 22.9592 | 23.4534 | 23.9475 | 24.4417 | 24.9358 | 25.43 | 25.9241 | 26.4183 | 26.9124 | 27.4066 | 27.9008 | 28.3949 | 28.8891 | 29.3832 | 29.8774 | 30.3715 | 30.8657 | 31.3598 | 31.854 | 32.3482 | 32.8423 | 33.3365 | 33.8306 | 34.3248 | 34.8189 | 35.3131 | 35.8072 | 36.3014 | 36.7955 | 37.2897 | 37.7839 | 38.278 | 38.7722 | 39.2663 | 39.7605 | 40.2546 | 40.7488 | 41.2429 | 41.7371 | 42.2313 | 42.7254 | 43.2196 | 43.7137 | 44.2079 | 44.702 | 45.1962 | 45.6903 | 46.1845 | 46.6786 | 47.1728 | 47.667 | 48.1611 | 48.6553 | 49.1494 | 49.6436 | 50.1377 | 50.6319 | 51.126 | 51.6202 | 52.1144 | 52.6085 | 53.1027 | 53.5968 | 54.091 | 54.5851 | 55.0793 | 55.5734 | 56.0676 | 56.5617 | 57.0559 | 57.5501 | 58.0442 | 58.5384 | 59.0325 | 59.5267 | 60.0208 | 60.515 | 61.0091 | 61.5033 | 61.9975 | 62.4916 | 62.9858 | 63.4799 | 63.9741 | 64.4682 | 64.9624 | 65.4565 | 65.9507 | 66.4449 | 66.939 | 67.4332 | 67.9273 | 68.4215 | 68.9156 | 69.4098 | 69.9039 | 70.3981 | 70.8922 | 71.3864 | 71.8806 | 72.3747 | 72.8689 | 73.363 | 73.8572 | 74.3513 | 74.8455 | 75.3396 | 75.8338 | 76.328 | 76.8221 | 77.3163 | 77.8104 | 78.3046 | 78.7987 | 79.2929 | 79.787 | 80.2812 | 80.7753 | 81.2695 | 81.7637 | 82.2578 | 82.752 | 83.2461 | 83.7403 | 84.2344 | 84.7286 | 85.2227 | 85.7169 | 86.2111 | 86.7052 | 87.1994 | 87.6935 | 88.1877 | 88.6818 | 89.176 | 89.6701 | 90.1643 | 90.6584 | 91.1526 | 91.6468 | 92.1409 | 92.6351 | 93.1292 | 93.6234 | 94.1175 | 94.6117 | 95.1058 | 95.6 | 96.0942
Enersys Powersafe SBS 30 | 0.31455 | 0.31455 | 0.31455 | 0.31455 | 0.31455 | 0.31455 | 0.31455 | 0.45428 | 0.5837 | 0.76375 | 0.9438 | 1.1575 | 1.3713 | 1.585 | 2.7478 | 3.9105 | 6.1239 | 6.6655 | 7.2072 | 7.7585 | 8.3097 | 8.7841 | 9.2585 | 9.7857 | 10.3129 | 10.6898 | 11.0667 | 11.5233 | 11.9799 | 12.4365 | 12.8931 | 13.3497 | 13.8063 | 14.2629 | 14.7195 | 15.1761 | 15.6326 | 16.0892 | 16.5458 | 17.0024 | 17.459 | 17.9156 | 18.3722 | 18.8288 | 19.2854 | 19.742 | 20.1986 | 20.6552 | 21.1118 | 21.5684 | 22.025 | 22.4816 | 22.9382 | 23.3948 | 23.8514 | 24.308 | 24.7646 | 25.2212 | 25.6778 | 26.1344 | 26.591 | 27.0476 | 27.5042 | 27.9608 | 28.4174 | 28.874 | 29.3306 | 29.7872 | 30.2438 | 30.7004 | 31.157 | 31.6135 | 32.0701 | 32.5267 | 32.9833 | 33.4399 | 33.8965 | 34.3531 | 34.8097 | 35.2663 | 35.7229 | 36.1795 | 36.6361 | 37.0927 | 37.5493 | 38.0059 | 38.4625 | 38.9191 | 39.3757 | 39.8323 | 40.2889 | 40.7455 | 41.2021 | 41.6587 | 42.1153 | 42.5719 | 43.0285 | 43.4851 | 43.9417 | 44.3983 | 44.8549 | 45.3115 | 45.7681 | 46.2247 | 46.6813 | 47.1379 | 47.5944 | 48.051 | 48.5076 | 48.9642 | 49.4208 | 49.8774 | 50.334 | 50.7906 | 51.2472 | 51.7038 | 52.1604 | 52.617 | 53.0736 | 53.5302 | 53.9868 | 54.4434 | 54.9 | 55.3566 | 55.8132 | 56.2698 | 56.7264 | 57.183 | 57.6396 | 58.0962 | 58.5528 | 59.0094 | 59.466 | 59.9226 | 60.3792 | 60.8358 | 61.2924 | 61.749 | 62.2056 | 62.6622 | 63.1188 | 63.5753 | 64.0319 | 64.4885 | 64.9451 | 65.4017 | 65.8583 | 66.3149 | 66.7715 | 67.2281 | 67.6847 | 68.1413 | 68.5979 | 69.0545 | 69.5111 | 69.9677 | 70.4243 | 70.8809 | 71.3375 | 71.7941 | 72.2507 | 72.7073 | 73.1639 | 73.6205 | 74.0771 | 74.5337 | 74.9903 | 75.4469 | 75.9035 | 76.3601 | 76.8167 | 77.2733 | 77.7299 | 78.1865 | 78.6431 | 79.0997 | 79.5562 | 80.0128 | 80.4694 | 80.926 | 81.3826 | 81.8392 | 82.2958 | 82.7524 | 83.209 | 83.6656 | 84.1222 | 84.5788 | 85.0354 | 85.492 | 85.9486 | 86.4052 | 86.8618 | 87.3184 | 87.775 | 88.2316 | 88.6882 | 89.1448 | 89.6014
Enersys Powersafe SBS 31 | 0.31455 | 0.31455 | 0.31455 | 0.31455 | 0.31455 | 0.31455 | 0.31455 | 0.45428 | 0.5837 | 0.76375 | 0.9438 | 1.1575 | 1.3713 | 1.585 | 2.7478 | 3.9105 | 6.1239 | 6.6655 | 7.2072 | 7.7585 | 8.3097 | 8.7841 | 9.2585 | 9.7857 | 10.3129 | 10.6898 | 11.0667 | 11.5233 | 11.9799 | 12.4365 | 12.8931 | 13.3497 | 13.8063 | 14.2629 | 14.7195 | 15.1761 | 15.6326 | 16.0892 | 16.5458 | 17.0024 | 17.459 | 17.9156 | 18.3722 | 18.8288 | 19.2854 | 19.742 | 20.1986 | 20.6552 | 21.1118 | 21.5684 | 22.025 | 22.4816 | 22.9382 | 23.3948 | 23.8514 | 24.308 | 24.7646 | 25.2212 | 25.6778 | 26.1344 | 26.591 | 27.0476 | 27.5042 | 27.9608 | 28.4174 | 28.874 | 29.3306 | 29.7872 | 30.2438 | 30.7004 | 31.157 | 31.6135 | 32.0701 | 32.5267 | 32.9833 | 33.4399 | 33.8965 | 34.3531 | 34.8097 | 35.2663 | 35.7229 | 36.1795 | 36.6361 | 37.0927 | 37.5493 | 38.0059 | 38.4625 | 38.9191 | 39.3757 | 39.8323 | 40.2889 | 40.7455 | 41.2021 | 41.6587 | 42.1153 | 42.5719 | 43.0285 | 43.4851 | 43.9417 | 44.3983 | 44.8549 | 45.3115 | 45.7681 | 46.2247 | 46.6813 | 47.1379 | 47.5944 | 48.051 | 48.5076 | 48.9642 | 49.4208 | 49.8774 | 50.334 | 50.7906 | 51.2472 | 51.7038 | 52.1604 | 52.617 | 53.0736 | 53.5302 | 53.9868 | 54.4434 | 54.9 | 55.3566 | 55.8132 | 56.2698 | 56.7264 | 57.183 | 57.6396 | 58.0962 | 58.5528 | 59.0094 | 59.466 | 59.9226 | 60.3792 | 60.8358 | 61.2924 | 61.749 | 62.2056 | 62.6622 | 63.1188 | 63.5753 | 64.0319 | 64.4885 | 64.9451 | 65.4017 | 65.8583 | 66.3149 | 66.7715 | 67.2281 | 67.6847 | 68.1413 | 68.5979 | 69.0545 | 69.5111 | 69.9677 | 70.4243 | 70.8809 | 71.3375 | 71.7941 | 72.2507 | 72.7073 | 73.1639 | 73.6205 | 74.0771 | 74.5337 | 74.9903 | 75.4469 | 75.9035 | 76.3601 | 76.8167 | 77.2733 | 77.7299 | 78.1865 | 78.6431 | 79.0997 | 79.5562 | 80.0128 | 80.4694 | 80.926 | 81.3826 | 81.8392 | 82.2958 | 82.7524 | 83.209 | 83.6656 | 84.1222 | 84.5788 | 85.0354 | 85.492 | 85.9486 | 86.4052 | 86.8618 | 87.3184 | 87.775 | 88.2316 | 88.6882 | 89.1448 | 89.6014
Enersys Powersafe SBS 40 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.49141 | 0.61658 | 0.78881 | 0.96105 | 1.1721 | 1.3832 | 1.5943 | 2.7517 | 3.909 | 6.1511 | 6.7054 | 7.2598 | 7.8104 | 8.3611 | 8.7583 | 9.1556 | 9.7898 | 10.424 | 10.756 | 11.088 | 11.5445 | 12.0011 | 12.4577 | 12.9142 | 13.3708 | 13.8274 | 14.2839 | 14.7405 | 15.197 | 15.6536 | 16.1102 | 16.5667 | 17.0233 | 17.4799 | 17.9364 | 18.393 | 18.8496 | 19.3061 | 19.7627 | 20.2192 | 20.6758 | 21.1324 | 21.5889 | 22.0455 | 22.5021 | 22.9586 | 23.4152 | 23.8718 | 24.3283 | 24.7849 | 25.2414 | 25.698 | 26.1546 | 26.6111 | 27.0677 | 27.5243 | 27.9808 | 28.4374 | 28.894 | 29.3505 | 29.8071 | 30.2636 | 30.7202 | 31.1768 | 31.6333 | 32.0899 | 32.5465 | 33.003 | 33.4596 | 33.9162 | 34.3727 | 34.8293 | 35.2858 | 35.7424 | 36.199 | 36.6555 | 37.1121 | 37.5687 | 38.0252 | 38.4818 | 38.9384 | 39.3949 | 39.8515 | 40.308 | 40.7646 | 41.2212 | 41.6777 | 42.1343 | 42.5909 | 43.0474 | 43.504 | 43.9606 | 44.4171 | 44.8737 | 45.3302 | 45.7868 | 46.2434 | 46.6999 | 47.1565 | 47.6131 | 48.0696 | 48.5262 | 48.9828 | 49.4393 | 49.8959 | 50.3524 | 50.809 | 51.2656 | 51.7221 | 52.1787 | 52.6353 | 53.0918 | 53.5484 | 54.005 | 54.4615 | 54.9181 | 55.3746 | 55.8312 | 56.2878 | 56.7443 | 57.2009 | 57.6575 | 58.114 | 58.5706 | 59.0272 | 59.4837 | 59.9403 | 60.3968 | 60.8534 | 61.31 | 61.7665 | 62.2231 | 62.6797 | 63.1362 | 63.5928 | 64.0494 | 64.5059 | 64.9625 | 65.419 | 65.8756 | 66.3322 | 66.7887 | 67.2453 | 67.7019 | 68.1584 | 68.615 | 69.0716 | 69.5281 | 69.9847 | 70.4412 | 70.8978 | 71.3544 | 71.8109 | 72.2675 | 72.7241 | 73.1806 | 73.6372 | 74.0938 | 74.5503 | 75.0069 | 75.4634 | 75.92 | 76.3766 | 76.8331 | 77.2897 | 77.7463 | 78.2028 | 78.6594 | 79.116 | 79.5725 | 80.0291 | 80.4856 | 80.9422 | 81.3988 | 81.8553 | 82.3119 | 82.7685 | 83.225 | 83.6816 | 84.1382 | 84.5947 | 85.0513 | 85.5078 | 85.9644 | 86.421 | 86.8775 | 87.3341 | 87.7907 | 88.2472 | 88.7038 | 89.1604 | 89.6169
Enersys Powersafe SBS 41 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.35547 | 0.49141 | 0.61658 | 0.78881 | 0.96105 | 1.1721 | 1.3832 | 1.5943 | 2.7517 | 3.909 | 6.1511 | 6.7054 | 7.2598 | 7.8104 | 8.3611 | 8.7583 | 9.1556 | 9.7898 | 10.424 | 10.756 | 11.088 | 11.5445 | 12.0011 | 12.4577 | 12.9142 | 13.3708 | 13.8274 | 14.2839 | 14.7405 | 15.197 | 15.6536 | 16.1102 | 16.5667 | 17.0233 | 17.4799 | 17.9364 | 18.393 | 18.8496 | 19.3061 | 19.7627 | 20.2192 | 20.6758 | 21.1324 | 21.5889 | 22.0455 | 22.5021 | 22.9586 | 23.4152 | 23.8718 | 24.3283 | 24.7849 | 25.2414 | 25.698 | 26.1546 | 26.6111 | 27.0677 | 27.5243 | 27.9808 | 28.4374 | 28.894 | 29.3505 | 29.8071 | 30.2636 | 30.7202 | 31.1768 | 31.6333 | 32.0899 | 32.5465 | 33.003 | 33.4596 | 33.9162 | 34.3727 | 34.8293 | 35.2858 | 35.7424 | 36.199 | 36.6555 | 37.1121 | 37.5687 | 38.0252 | 38.4818 | 38.9384 | 39.3949 | 39.8515 | 40.308 | 40.7646 | 41.2212 | 41.6777 | 42.1343 | 42.5909 | 43.0474 | 43.504 | 43.9606 | 44.4171 | 44.8737 | 45.3302 | 45.7868 | 46.2434 | 46.6999 | 47.1565 | 47.6131 | 48.0696 | 48.5262 | 48.9828 | 49.4393 | 49.8959 | 50.3524 | 50.809 | 51.2656 | 51.7221 | 52.1787 | 52.6353 | 53.0918 | 53.5484 | 54.005 | 54.4615 | 54.9181 | 55.3746 | 55.8312 | 56.2878 | 56.7443 | 57.2009 | 57.6575 | 58.114 | 58.5706 | 59.0272 | 59.4837 | 59.9403 | 60.3968 | 60.8534 | 61.31 | 61.7665 | 62.2231 | 62.6797 | 63.1362 | 63.5928 | 64.0494 | 64.5059 | 64.9625 | 65.419 | 65.8756 | 66.3322 | 66.7887 | 67.2453 | 67.7019 | 68.1584 | 68.615 | 69.0716 | 69.5281 | 69.9847 | 70.4412 | 70.8978 | 71.3544 | 71.8109 | 72.2675 | 72.7241 | 73.1806 | 73.6372 | 74.0938 | 74.5503 | 75.0069 | 75.4634 | 75.92 | 76.3766 | 76.8331 | 77.2897 | 77.7463 | 78.2028 | 78.6594 | 79.116 | 79.5725 | 80.0291 | 80.4856 | 80.9422 | 81.3988 | 81.8553 | 82.3119 | 82.7685 | 83.225 | 83.6816 | 84.1382 | 84.5947 | 85.0513 | 85.5078 | 85.9644 | 86.421 | 86.8775 | 87.3341 | 87.7907 | 88.2472 | 88.7038 | 89.1604 | 89.6169
Enersys Powersafe SBS 60 | 0.38485 | 0.38485 | 0.38485 | 0.38485 | 0.38485 | 0.38485 | 0.38485 | 0.51951 | 0.64496 | 0.82229 | 0.99961 | 1.2099 | 1.4203 | 1.6306 | 2.7635 | 3.8964 | 6.0433 | 6.5761 | 7.1089 | 7.6387 | 8.1685 | 8.6326 | 9.0967 | 9.6177 | 10.1387 | 10.6273 | 11.116 | 11.5971 | 12.0783 | 12.5594 | 13.0405 | 13.5217 | 14.0028 | 14.4839 | 14.9651 | 15.4462 | 15.9274 | 16.4085 | 16.8896 | 17.3708 | 17.8519 | 18.3331 | 18.8142 | 19.2953 | 19.7765 | 20.2576 | 20.7388 | 21.2199 | 21.701 | 22.1822 | 22.6633 | 23.1445 | 23.6256 | 24.1067 | 24.5879 | 25.069 | 25.5501 | 26.0313 | 26.5124 | 26.9936 | 27.4747 | 27.9558 | 28.437 | 28.9181 | 29.3993 | 29.8804 | 30.3615 | 30.8427 | 31.3238 | 31.805 | 32.2861 | 32.7672 | 33.2484 | 33.7295 | 34.2107 | 34.6918 | 35.1729 | 35.6541 | 36.1352 | 36.6163 | 37.0975 | 37.5786 | 38.0598 | 38.5409 | 39.022 | 39.5032 | 39.9843 | 40.4655 | 40.9466 | 41.4277 | 41.9089 | 42.39 | 42.8712 | 43.3523 | 43.8334 | 44.3146 | 44.7957 | 45.2769 | 45.758 | 46.2391 | 46.7203 | 47.2014 | 47.6826 | 48.1637 | 48.6448 | 49.126 | 49.6071 | 50.0882 | 50.5694 | 51.0505 | 51.5317 | 52.0128 | 52.4939 | 52.9751 | 53.4562 | 53.9374 | 54.4185 | 54.8996 | 55.3808 | 55.8619 | 56.3431 | 56.8242 | 57.3053 | 57.7865 | 58.2676 | 58.7488 | 59.2299 | 59.711 | 60.1922 | 60.6733 | 61.1544 | 61.6356 | 62.1167 | 62.5979 | 63.079 | 63.5601 | 64.0413 | 64.5224 | 65.0036 | 65.4847 | 65.9658 | 66.447 | 66.9281 | 67.4093 | 67.8904 | 68.3715 | 68.8527 | 69.3338 | 69.815 | 70.2961 | 70.7772 | 71.2584 | 71.7395 | 72.2206 | 72.7018 | 73.1829 | 73.6641 | 74.1452 | 74.6263 | 75.1075 | 75.5886 | 76.0698 | 76.5509 | 77.032 | 77.5132 | 77.9943 | 78.4755 | 78.9566 | 79.4377 | 79.9189 | 80.4 | 80.8812 | 81.3623 | 81.8434 | 82.3246 | 82.8057 | 83.2868 | 83.768 | 84.2491 | 84.7303 | 85.2114 | 85.6925 | 86.1737 | 86.6548 | 87.136 | 87.6171 | 88.0982 | 88.5794 | 89.0605 | 89.5417 | 90.0228 | 90.5039 | 90.9851 | 91.4662 | 91.9474 | 92.4285 | 92.9096 | 93.3908 | 93.8719
Enersys Powersafe SBS 110 | 0.51973 | 0.51973 | 0.51973 | 0.51973 | 0.51973 | 0.51973 | 0.51973 | 0.64867 | 0.77391 | 0.94804 | 1.1222 | 1.3349 | 1.5476 | 1.7603 | 2.8986 | 4.037 | 6.1728 | 6.696 | 7.2191 | 7.7314 | 8.2437 | 8.6956 | 9.1475 | 9.6638 | 10.1802 | 10.6086 | 11.0369 | 11.5014 | 11.9658 | 12.4303 | 12.8948 | 13.3593 | 13.8238 | 14.2882 | 14.7527 | 15.2172 | 15.6817 | 16.1461 | 16.6106 | 17.0751 | 17.5396 | 18.004 | 18.4685 | 18.933 | 19.3975 | 19.8619 | 20.3264 | 20.7909 | 21.2554 | 21.7199 | 22.1843 | 22.6488 | 23.1133 | 23.5778 | 24.0422 | 24.5067 | 24.9712 | 25.4357 | 25.9001 | 26.3646 | 26.8291 | 27.2936 | 27.7581 | 28.2225 | 28.687 | 29.1515 | 29.616 | 30.0804 | 30.5449 | 31.0094 | 31.4739 | 31.9383 | 32.4028 | 32.8673 | 33.3318 | 33.7962 | 34.2607 | 34.7252 | 35.1897 | 35.6542 | 36.1186 | 36.5831 | 37.0476 | 37.5121 | 37.9765 | 38.441 | 38.9055 | 39.37 | 39.8344 | 40.2989 | 40.7634 | 41.2279 | 41.6923 | 42.1568 | 42.6213 | 43.0858 | 43.5503 | 44.0147 | 44.4792 | 44.9437 | 45.4082 | 45.8726 | 46.3371 | 46.8016 | 47.2661 | 47.7305 | 48.195 | 48.6595 | 49.124 | 49.5885 | 50.0529 | 50.5174 | 50.9819 | 51.4464 | 51.9108 | 52.3753 | 52.8398 | 53.3043 | 53.7687 | 54.2332 | 54.6977 | 55.1622 | 55.6266 | 56.0911 | 56.5556 | 57.0201 | 57.4846 | 57.949 | 58.4135 | 58.878 | 59.3425 | 59.8069 | 60.2714 | 60.7359 | 61.2004 | 61.6648 | 62.1293 | 62.5938 | 63.0583 | 63.5228 | 63.9872 | 64.4517 | 64.9162 | 65.3807 | 65.8451 | 66.3096 | 66.7741 | 67.2386 | 67.703 | 68.1675 | 68.632 | 69.0965 | 69.5609 | 70.0254 | 70.4899 | 70.9544 | 71.4189 | 71.8833 | 72.3478 | 72.8123 | 73.2768 | 73.7412 | 74.2057 | 74.6702 | 75.1347 | 75.5991 | 76.0636 | 76.5281 | 76.9926 | 77.4571 | 77.9215 | 78.386 | 78.8505 | 79.315 | 79.7794 | 80.2439 | 80.7084 | 81.1729 | 81.6373 | 82.1018 | 82.5663 | 83.0308 | 83.4952 | 83.9597 | 84.4242 | 84.8887 | 85.3532 | 85.8176 | 86.2821 | 86.7466 | 87.2111 | 87.6755 | 88.14 | 88.6045 | 89.069 | 89.5334 | 89.9979 | 90.4624 | 90.9269
Enersys Powersafe SBS 130 | 0.46757 | 0.46757 | 0.46757 | 0.46757 | 0.46757 | 0.46757 | 0.46757 | 0.61954 | 0.7561 | 0.93927 | 1.1224 | 1.3391 | 1.5557 | 1.7724 | 2.9055 | 4.0387 | 6.1625 | 6.6937 | 7.225 | 7.7323 | 8.2397 | 8.7052 | 9.1706 | 9.6516 | 10.1326 | 10.6209 | 11.1092 | 11.5943 | 12.0793 | 12.5643 | 13.0494 | 13.5344 | 14.0194 | 14.5044 | 14.9895 | 15.4745 | 15.9595 | 16.4446 | 16.9296 | 17.4146 | 17.8996 | 18.3847 | 18.8697 | 19.3547 | 19.8398 | 20.3248 | 20.8098 | 21.2948 | 21.7799 | 22.2649 | 22.7499 | 23.235 | 23.72 | 24.205 | 24.69 | 25.1751 | 25.6601 | 26.1451 | 26.6302 | 27.1152 | 27.6002 | 28.0852 | 28.5703 | 29.0553 | 29.5403 | 30.0254 | 30.5104 | 30.9954 | 31.4805 | 31.9655 | 32.4505 | 32.9355 | 33.4206 | 33.9056 | 34.3906 | 34.8757 | 35.3607 | 35.8457 | 36.3307 | 36.8158 | 37.3008 | 37.7858 | 38.2709 | 38.7559 | 39.2409 | 39.7259 | 40.211 | 40.696 | 41.181 | 41.6661 | 42.1511 | 42.6361 | 43.1211 | 43.6062 | 44.0912 | 44.5762 | 45.0613 | 45.5463 | 46.0313 | 46.5163 | 47.0014 | 47.4864 | 47.9714 | 48.4565 | 48.9415 | 49.4265 | 49.9115 | 50.3966 | 50.8816 | 51.3666 | 51.8517 | 52.3367 | 52.8217 | 53.3067 | 53.7918 | 54.2768 | 54.7618 | 55.2469 | 55.7319 | 56.2169 | 56.7019 | 57.187 | 57.672 | 58.157 | 58.6421 | 59.1271 | 59.6121 | 60.0972 | 60.5822 | 61.0672 | 61.5522 | 62.0373 | 62.5223 | 63.0073 | 63.4924 | 63.9774 | 64.4624 | 64.9474 | 65.4325 | 65.9175 | 66.4025 | 66.8876 | 67.3726 | 67.8576 | 68.3426 | 68.8277 | 69.3127 | 69.7977 | 70.2828 | 70.7678 | 71.2528 | 71.7378 | 72.2229 | 72.7079 | 73.1929 | 73.678 | 74.163 | 74.648 | 75.133 | 75.6181 | 76.1031 | 76.5881 | 77.0732 | 77.5582 | 78.0432 | 78.5282 | 79.0133 | 79.4983 | 79.9833 | 80.4684 | 80.9534 | 81.4384 | 81.9234 | 82.4085 | 82.8935 | 83.3785 | 83.8636 | 84.3486 | 84.8336 | 85.3186 | 85.8037 | 86.2887 | 86.7737 | 87.2588 | 87.7438 | 88.2288 | 88.7139 | 89.1989 | 89.6839 | 90.1689 | 90.654 | 91.139 | 91.624 | 92.1091 | 92.5941 | 93.0791 | 93.5641 | 94.0492 | 94.5342
Enersys Powersafe SBS 300 | 0.49188 | 0.49188 | 0.49188 | 0.49188 | 0.49188 | 0.49188 | 0.49188 | 0.62691 | 0.76355 | 0.97701 | 1.1905 | 1.434 | 1.6774 | 1.9209 | 3.1829 | 4.4449 | 6.6239 | 7.1138 | 7.6036 | 8.0753 | 8.547 | 8.9866 | 9.4262 | 9.9004 | 10.3746 | 10.7292 | 11.0839 | 11.5157 | 11.9475 | 12.3792 | 12.811 | 13.2427 | 13.6745 | 14.1062 | 14.538 | 14.9698 | 15.4015 | 15.8333 | 16.265 | 16.6968 | 17.1286 | 17.5603 | 17.9921 | 18.4238 | 18.8556 | 19.2873 | 19.7191 | 20.1509 | 20.5826 | 21.0144 | 21.4461 | 21.8779 | 22.3096 | 22.7414 | 23.1732 | 23.6049 | 24.0367 | 24.4684 | 24.9002 | 25.332 | 25.7637 | 26.1955 | 26.6272 | 27.059 | 27.4907 | 27.9225 | 28.3543 | 28.786 | 29.2178 | 29.6495 | 30.0813 | 30.513 | 30.9448 | 31.3766 | 31.8083 | 32.2401 | 32.6718 | 33.1036 | 33.5354 | 33.9671 | 34.3989 | 34.8306 | 35.2624 | 35.6941 | 36.1259 | 36.5577 | 36.9894 | 37.4212 | 37.8529 | 38.2847 | 38.7165 | 39.1482 | 39.58 | 40.0117 | 40.4435 | 40.8752 | 41.307 | 41.7388 | 42.1705 | 42.6023 | 43.034 | 43.4658 | 43.8975 | 44.3293 | 44.7611 | 45.1928 | 45.6246 | 46.0563 | 46.4881 | 46.9199 | 47.3516 | 47.7834 | 48.2151 | 48.6469 | 49.0786 | 49.5104 | 49.9422 | 50.3739 | 50.8057 | 51.2374 | 51.6692 | 52.101 | 52.5327 | 52.9645 | 53.3962 | 53.828 | 54.2597 | 54.6915 | 55.1233 | 55.555 | 55.9868 | 56.4185 | 56.8503 | 57.282 | 57.7138 | 58.1456 | 58.5773 | 59.0091 | 59.4408 | 59.8726 | 60.3044 | 60.7361 | 61.1679 | 61.5996 | 62.0314 | 62.4631 | 62.8949 | 63.3267 | 63.7584 | 64.1902 | 64.6219 | 65.0537 | 65.4854 | 65.9172 | 66.349 | 66.7807 | 67.2125 | 67.6442 | 68.076 | 68.5078 | 68.9395 | 69.3713 | 69.803 | 70.2348 | 70.6665 | 71.0983 | 71.5301 | 71.9618 | 72.3936 | 72.8253 | 73.2571 | 73.6889 | 74.1206 | 74.5524 | 74.9841 | 75.4159 | 75.8476 | 76.2794 | 76.7112 | 77.1429 | 77.5747 | 78.0064 | 78.4382 | 78.8699 | 79.3017 | 79.7335 | 80.1652 | 80.597 | 81.0287 | 81.4605 | 81.8923 | 82.324 | 82.7558 | 83.1875 | 83.6193 | 84.051 | 84.4828 | 84.9146 | 85.3463
Enersys Powersafe SBS 390 | 0.54483 | 0.54483 | 0.54483 | 0.54483 | 0.54483 | 0.54483 | 0.54483 | 0.663 | 0.78192 | 0.94755 | 1.1132 | 1.3191 | 1.525 | 1.7309 | 2.8416 | 3.9523 | 6.079 | 6.6173 | 7.1556 | 7.6846 | 8.2136 | 8.649 | 9.0844 | 9.6085 | 10.1326 | 10.5827 | 11.0329 | 11.5177 | 12.0026 | 12.4875 | 12.9723 | 13.4572 | 13.9421 | 14.4269 | 14.9118 | 15.3966 | 15.8815 | 16.3664 | 16.8512 | 17.3361 | 17.821 | 18.3058 | 18.7907 | 19.2756 | 19.7604 | 20.2453 | 20.7302 | 21.215 | 21.6999 | 22.1848 | 22.6696 | 23.1545 | 23.6394 | 24.1242 | 24.6091 | 25.0939 | 25.5788 | 26.0637 | 26.5485 | 27.0334 | 27.5183 | 28.0031 | 28.488 | 28.9729 | 29.4577 | 29.9426 | 30.4275 | 30.9123 | 31.3972 | 31.8821 | 32.3669 | 32.8518 | 33.3367 | 33.8215 | 34.3064 | 34.7913 | 35.2761 | 35.761 | 36.2458 | 36.7307 | 37.2156 | 37.7004 | 38.1853 | 38.6702 | 39.155 | 39.6399 | 40.1248 | 40.6096 | 41.0945 | 41.5794 | 42.0642 | 42.5491 | 43.034 | 43.5188 | 44.0037 | 44.4886 | 44.9734 | 45.4583 | 45.9431 | 46.428 | 46.9129 | 47.3977 | 47.8826 | 48.3675 | 48.8523 | 49.3372 | 49.8221 | 50.3069 | 50.7918 | 51.2767 | 51.7615 | 52.2464 | 52.7313 | 53.2161 | 53.701 | 54.1859 | 54.6707 | 55.1556 | 55.6405 | 56.1253 | 56.6102 | 57.095 | 57.5799 | 58.0648 | 58.5496 | 59.0345 | 59.5194 | 60.0042 | 60.4891 | 60.974 | 61.4588 | 61.9437 | 62.4286 | 62.9134 | 63.3983 | 63.8832 | 64.368 | 64.8529 | 65.3378 | 65.8226 | 66.3075 | 66.7924 | 67.2772 | 67.7621 | 68.2469 | 68.7318 | 69.2167 | 69.7015 | 70.1864 | 70.6713 | 71.1561 | 71.641 | 72.1259 | 72.6107 | 73.0956 | 73.5805 | 74.0653 | 74.5502 | 75.0351 | 75.5199 | 76.0048 | 76.4897 | 76.9745 | 77.4594 | 77.9442 | 78.4291 | 78.914 | 79.3988 | 79.8837 | 80.3686 | 80.8534 | 81.3383 | 81.8232 | 82.308 | 82.7929 | 83.2778 | 83.7626 | 84.2475 | 84.7324 | 85.2172 | 85.7021 | 86.187 | 86.6718 | 87.1567 | 87.6416 | 88.1264 | 88.6113 | 89.0961 | 89.581 | 90.0659 | 90.5507 | 91.0356 | 91.5205 | 92.0053 | 92.4902 | 92.9751 | 93.4599 | 93.9448 | 94.4297
Enersys Powersafe SBS B8 | 0.27379 | 0.27379 | 0.27379 | 0.27379 | 0.27379 | 0.27379 | 0.27379 | 0.45727 | 0.61175 | 0.80601 | 1.0003 | 1.2173 | 1.4344 | 1.6515 | 2.7663 | 3.8812 | 6.0087 | 6.5492 | 7.0897 | 7.6377 | 8.1857 | 8.5568 | 8.9279 | 9.4609 | 9.9939 | 10.5218 | 11.0496 | 11.5876 | 12.1257 | 12.6637 | 13.2017 | 13.7398 | 14.2778 | 14.8159 | 15.3539 | 15.8919 | 16.43 | 16.968 | 17.506 | 18.0441 | 18.5821 | 19.1201 | 19.6582 | 20.1962 | 20.7343 | 21.2723 | 21.8103 | 22.3484 | 22.8864 | 23.4244 | 23.9625 | 24.5005 | 25.0385 | 25.5766 | 26.1146 | 26.6527 | 27.1907 | 27.7287 | 28.2668 | 28.8048 | 29.3428 | 29.8809 | 30.4189 | 30.9569 | 31.495 | 32.033 | 32.5711 | 33.1091 | 33.6471 | 34.1852 | 34.7232 | 35.2612 | 35.7993 | 36.3373 | 36.8753 | 37.4134 | 37.9514 | 38.4895 | 39.0275 | 39.5655 | 40.1036 | 40.6416 | 41.1796 | 41.7177 | 42.2557 | 42.7937 | 43.3318 | 43.8698 | 44.4079 | 44.9459 | 45.4839 | 46.022 | 46.56 | 47.098 | 47.6361 | 48.1741 | 48.7121 | 49.2502 | 49.7882 | 50.3263 | 50.8643 | 51.4023 | 51.9404 | 52.4784 | 53.0164 | 53.5545 | 54.0925 | 54.6305 | 55.1686 | 55.7066 | 56.2446 | 56.7827 | 57.3207 | 57.8588 | 58.3968 | 58.9348 | 59.4729 | 60.0109 | 60.5489 | 61.087 | 61.625 | 62.163 | 62.7011 | 63.2391 | 63.7772 | 64.3152 | 64.8532 | 65.3913 | 65.9293 | 66.4673 | 67.0054 | 67.5434 | 68.0814 | 68.6195 | 69.1575 | 69.6956 | 70.2336 | 70.7716 | 71.3097 | 71.8477 | 72.3857 | 72.9238 | 73.4618 | 73.9998 | 74.5379 | 75.0759 | 75.614 | 76.152 | 76.69 | 77.2281 | 77.7661 | 78.3041 | 78.8422 | 79.3802 | 79.9182 | 80.4563 | 80.9943 | 81.5324 | 82.0704 | 82.6084 | 83.1465 | 83.6845 | 84.2225 | 84.7606 | 85.2986 | 85.8366 | 86.3747 | 86.9127 | 87.4508 | 87.9888 | 88.5268 | 89.0649 | 89.6029 | 90.1409 | 90.679 | 91.217 | 91.755 | 92.2931 | 92.8311 | 93.3692 | 93.9072 | 94.4452 | 94.9833 | 95.5213 | 96.0593 | 96.5974 | 97.1354 | 97.6734 | 98.2115 | 98.7495 | 99.2875 | 99.8256 | 100.3636 | 100.9017 | 101.4397 | 101.9777 | 102.5158 | 103.0538 | 103.5918
Enersys Powersafe SBS B10 | 0.38709 | 0.38709 | 0.38709 | 0.38709 | 0.38709 | 0.38709 | 0.38709 | 0.51699 | 0.6463 | 0.83278 | 1.0193 | 1.2566 | 1.494 | 1.7313 | 3.074 | 4.4167 | 6.9513 | 7.5698 | 8.1883 | 8.7874 | 9.3865 | 9.7565 | 10.1264 | 10.4113 | 10.6962 | 10.921 | 11.1457 | 11.5809 | 12.0161 | 12.4513 | 12.8865 | 13.3218 | 13.757 | 14.1922 | 14.6274 | 15.0626 | 15.4978 | 15.933 | 16.3683 | 16.8035 | 17.2387 | 17.6739 | 18.1091 | 18.5443 | 18.9795 | 19.4147 | 19.85 | 20.2852 | 20.7204 | 21.1556 | 21.5908 | 22.026 | 22.4612 | 22.8964 | 23.3317 | 23.7669 | 24.2021 | 24.6373 | 25.0725 | 25.5077 | 25.9429 | 26.3781 | 26.8134 | 27.2486 | 27.6838 | 28.119 | 28.5542 | 28.9894 | 29.4246 | 29.8598 | 30.2951 | 30.7303 | 31.1655 | 31.6007 | 32.0359 | 32.4711 | 32.9063 | 33.3416 | 33.7768 | 34.212 | 34.6472 | 35.0824 | 35.5176 | 35.9528 | 36.388 | 36.8233 | 37.2585 | 37.6937 | 38.1289 | 38.5641 | 38.9993 | 39.4345 | 39.8697 | 40.305 | 40.7402 | 41.1754 | 41.6106 | 42.0458 | 42.481 | 42.9162 | 43.3514 | 43.7867 | 44.2219 | 44.6571 | 45.0923 | 45.5275 | 45.9627 | 46.3979 | 46.8332 | 47.2684 | 47.7036 | 48.1388 | 48.574 | 49.0092 | 49.4444 | 49.8796 | 50.3149 | 50.7501 | 51.1853 | 51.6205 | 52.0557 | 52.4909 | 52.9261 | 53.3613 | 53.7966 | 54.2318 | 54.667 | 55.1022 | 55.5374 | 55.9726 | 56.4078 | 56.843 | 57.2783 | 57.7135 | 58.1487 | 58.5839 | 59.0191 | 59.4543 | 59.8895 | 60.3248 | 60.76 | 61.1952 | 61.6304 | 62.0656 | 62.5008 | 62.936 | 63.3712 | 63.8065 | 64.2417 | 64.6769 | 65.1121 | 65.5473 | 65.9825 | 66.4177 | 66.8529 | 67.2882 | 67.7234 | 68.1586 | 68.5938 | 69.029 | 69.4642 | 69.8994 | 70.3346 | 70.7699 | 71.2051 | 71.6403 | 72.0755 | 72.5107 | 72.9459 | 73.3811 | 73.8163 | 74.2516 | 74.6868 | 75.122 | 75.5572 | 75.9924 | 76.4276 | 76.8628 | 77.2981 | 77.7333 | 78.1685 | 78.6037 | 79.0389 | 79.4741 | 79.9093 | 80.3445 | 80.7798 | 81.215 | 81.6502 | 82.0854 | 82.5206 | 82.9558 | 83.391 | 83.8262 | 84.2615 | 84.6967 | 85.1319 | 85.5671 | 86.0023
Enersys Powersafe SBS B14 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.54273 | 0.66074 | 0.82268 | 0.98462 | 1.1837 | 1.3827 | 1.5817 | 2.6787 | 3.7756 | 5.8594 | 6.3991 | 6.9388 | 7.4645 | 7.9902 | 8.4567 | 8.9233 | 9.4416 | 9.96 | 10.4504 | 10.9409 | 11.4421 | 11.9433 | 12.4444 | 12.9456 | 13.4468 | 13.948 | 14.4491 | 14.9503 | 15.4515 | 15.9527 | 16.4539 | 16.955 | 17.4562 | 17.9574 | 18.4586 | 18.9597 | 19.4609 | 19.9621 | 20.4633 | 20.9644 | 21.4656 | 21.9668 | 22.468 | 22.9691 | 23.4703 | 23.9715 | 24.4727 | 24.9738 | 25.475 | 25.9762 | 26.4774 | 26.9785 | 27.4797 | 27.9809 | 28.4821 | 28.9832 | 29.4844 | 29.9856 | 30.4868 | 30.9879 | 31.4891 | 31.9903 | 32.4915 | 32.9926 | 33.4938 | 33.995 | 34.4962 | 34.9973 | 35.4985 | 35.9997 | 36.5009 | 37.0021 | 37.5032 | 38.0044 | 38.5056 | 39.0068 | 39.5079 | 40.0091 | 40.5103 | 41.0115 | 41.5126 | 42.0138 | 42.515 | 43.0162 | 43.5173 | 44.0185 | 44.5197 | 45.0209 | 45.522 | 46.0232 | 46.5244 | 47.0256 | 47.5267 | 48.0279 | 48.5291 | 49.0303 | 49.5314 | 50.0326 | 50.5338 | 51.035 | 51.5361 | 52.0373 | 52.5385 | 53.0397 | 53.5408 | 54.042 | 54.5432 | 55.0444 | 55.5456 | 56.0467 | 56.5479 | 57.0491 | 57.5503 | 58.0514 | 58.5526 | 59.0538 | 59.555 | 60.0561 | 60.5573 | 61.0585 | 61.5597 | 62.0608 | 62.562 | 63.0632 | 63.5644 | 64.0655 | 64.5667 | 65.0679 | 65.5691 | 66.0702 | 66.5714 | 67.0726 | 67.5738 | 68.0749 | 68.5761 | 69.0773 | 69.5785 | 70.0796 | 70.5808 | 71.082 | 71.5832 | 72.0843 | 72.5855 | 73.0867 | 73.5879 | 74.089 | 74.5902 | 75.0914 | 75.5926 | 76.0938 | 76.5949 | 77.0961 | 77.5973 | 78.0985 | 78.5996 | 79.1008 | 79.602 | 80.1032 | 80.6043 | 81.1055 | 81.6067 | 82.1079 | 82.609 | 83.1102 | 83.6114 | 84.1126 | 84.6137 | 85.1149 | 85.6161 | 86.1173 | 86.6184 | 87.1196 | 87.6208 | 88.122 | 88.6231 | 89.1243 | 89.6255 | 90.1267 | 90.6278 | 91.129 | 91.6302 | 92.1314 | 92.6325 | 93.1337 | 93.6349 | 94.1361 | 94.6373 | 95.1384 | 95.6396 | 96.1408 | 96.642 | 97.1431
Enersys Powersafe SBS C11 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.62551 | 0.75627 | 0.93732 | 1.1184 | 1.3376 | 1.5568 | 1.776 | 2.9455 | 4.115 | 6.3147 | 6.8409 | 7.3671 | 7.8847 | 8.4022 | 8.7254 | 9.0486 | 9.5462 | 10.0439 | 10.5346 | 11.0253 | 11.4914 | 11.9575 | 12.4236 | 12.8897 | 13.3558 | 13.8219 | 14.288 | 14.7541 | 15.2202 | 15.6864 | 16.1525 | 16.6186 | 17.0847 | 17.5508 | 18.0169 | 18.483 | 18.9491 | 19.4152 | 19.8813 | 20.3474 | 20.8135 | 21.2797 | 21.7458 | 22.2119 | 22.678 | 23.1441 | 23.6102 | 24.0763 | 24.5424 | 25.0085 | 25.4746 | 25.9407 | 26.4069 | 26.873 | 27.3391 | 27.8052 | 28.2713 | 28.7374 | 29.2035 | 29.6696 | 30.1357 | 30.6018 | 31.0679 | 31.5341 | 32.0002 | 32.4663 | 32.9324 | 33.3985 | 33.8646 | 34.3307 | 34.7968 | 35.2629 | 35.729 | 36.1951 | 36.6612 | 37.1274 | 37.5935 | 38.0596 | 38.5257 | 38.9918 | 39.4579 | 39.924 | 40.3901 | 40.8562 | 41.3223 | 41.7884 | 42.2546 | 42.7207 | 43.1868 | 43.6529 | 44.119 | 44.5851 | 45.0512 | 45.5173 | 45.9834 | 46.4495 | 46.9156 | 47.3818 | 47.8479 | 48.314 | 48.7801 | 49.2462 | 49.7123 | 50.1784 | 50.6445 | 51.1106 | 51.5767 | 52.0428 | 52.5089 | 52.9751 | 53.4412 | 53.9073 | 54.3734 | 54.8395 | 55.3056 | 55.7717 | 56.2378 | 56.7039 | 57.17 | 57.6361 | 58.1023 | 58.5684 | 59.0345 | 59.5006 | 59.9667 | 60.4328 | 60.8989 | 61.365 | 61.8311 | 62.2972 | 62.7633 | 63.2294 | 63.6956 | 64.1617 | 64.6278 | 65.0939 | 65.56 | 66.0261 | 66.4922 | 66.9583 | 67.4244 | 67.8905 | 68.3566 | 68.8228 | 69.2889 | 69.755 | 70.2211 | 70.6872 | 71.1533 | 71.6194 | 72.0855 | 72.5516 | 73.0177 | 73.4838 | 73.95 | 74.4161 | 74.8822 | 75.3483 | 75.8144 | 76.2805 | 76.7466 | 77.2127 | 77.6788 | 78.1449 | 78.611 | 79.0771 | 79.5433 | 80.0094 | 80.4755 | 80.9416 | 81.4077 | 81.8738 | 82.3399 | 82.806 | 83.2721 | 83.7382 | 84.2043 | 84.6705 | 85.1366 | 85.6027 | 86.0688 | 86.5349 | 87.001 | 87.4671 | 87.9332 | 88.3993 | 88.8654 | 89.3315 | 89.7976 | 90.2638 | 90.7299 | 91.196

## Data_Enersys_VRLA (hidden)
Enersys Powersafe SBS 8 | [5 empty] | 12V
Ref (Ah): | 7.4 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC) |  |  | 20oC Factor | 15oC Factor | 5oC Factor
0
0.083333 | 33.6 | 0.22024 | 0.23965 | 0.28865 |  |  | 1 | 0.919 | 0.763
0.16667 | 21.7 | 0.34101 | 0.3655 | 0.42895 |  |  | 1 | 0.933 | 0.795
0.25 | 16.3 | 0.45399 | 0.48297 | 0.5591 |  |  | 1 | 0.94 | 0.812
0.33333 | 13.2 | 0.56061 | 0.59386 | 0.68035 |  |  | 1 | 0.944 | 0.824
0.41667 | 11.1 | 0.66667 | 0.70323 | 0.80032 |  |  | 1 | 0.948 | 0.833
0.5 | 9.61 | 0.77003 | 0.81056 | 0.9167 |  |  | 1 | 0.95 | 0.84
0.58333 | 8.49 | 0.87161 | 0.9146 | 1.0315 |  |  | 1 | 0.953 | 0.845
0.66667 | 7.62 | 0.97113 | 1.018 | 1.1425 |  |  | 1 | 0.954 | 0.85
0.75 | 6.92 | 1.0694 | 1.1186 | 1.2522 |  |  | 1 | 0.956 | 0.854
1 | 5.44 | 1.3603 | 1.4185 | 1.5762 |  |  | 1 | 0.959 | 0.863
2 | 3.01 | 2.4585 | 2.5424 | 2.7811 |  |  | 1 | 0.967 | 0.884
3 | 2.11 | 3.5071 | 3.6156 | 3.9273 |  |  | 1 | 0.97 | 0.893
4 | 1.63 | 4.5399 | 4.6707 | 5.0443 |  |  | 1 | 0.972 | 0.9
5 | 1.34 | 5.5224 | 5.6756 | 6.136 |  |  | 1 | 0.973 | 0.9
6 | 1.14 | 6.4912 | 6.6714 | 7.2125 |  |  | 1 | 0.973 | 0.9
7 | 1 | 7.4 | 7.6053 | 8.2222 |  |  | 1 | 0.973 | 0.9
8 | 0.89 | 8.3146 | 8.5278 | 9.1269 |  |  | 1 | 0.975 | 0.911
9 | 0.8 | 9.25 | 9.4872 | 10.1537 |  |  | 1 | 0.975 | 0.911
10 | 0.73 | 10.137 | 10.3863 | 11.0908 |  |  | 1 | 0.976 | 0.914
20 | 0.4 | 18.5 | 18.9549 | 20.2407 |  |  | 1 | 0.976 | 0.914
Enersys Powersafe SBS 15 | [5 empty] | 12V
Ref (Ah): | 14 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 59.3 | 0.23609 | 0.2569 | 0.30942
0.16667 | 39.3 | 0.35623 | 0.38182 | 0.44809
0.25 | 30 | 0.46667 | 0.49645 | 0.57471
0.33333 | 24.5 | 0.57143 | 0.60533 | 0.69348
0.41667 | 20.8 | 0.67308 | 0.71 | 0.80802
0.5 | 18.1 | 0.77348 | 0.81419 | 0.92081
0.58333 | 16.1 | 0.86957 | 0.91245 | 1.0291
0.66667 | 14.5 | 0.96552 | 1.0121 | 1.1359
0.75 | 13.2 | 1.0606 | 1.1094 | 1.2419
1 | 10.5 | 1.3333 | 1.3903 | 1.545
2 | 5.83 | 2.4014 | 2.4833 | 2.7165
3 | 4.09 | 3.423 | 3.5288 | 3.8331
4 | 3.17 | 4.4164 | 4.5436 | 4.9071
5 | 2.59 | 5.4054 | 5.5554 | 6.006
6 | 2.2 | 6.3636 | 6.5402 | 7.0707
7 | 1.91 | 7.3298 | 7.5332 | 8.1443
8 | 1.69 | 8.284 | 8.4964 | 9.0933
9 | 1.52 | 9.2105 | 9.4467 | 10.1103
10 | 1.38 | 10.1449 | 10.3944 | 11.0995
20 | 0.73 | 19.1781 | 19.6497 | 20.9826
Enersys Powersafe SBS 30 | [5 empty] | 12V
Ref (Ah): | 26.4 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 110 | 0.24 | 0.26115 | 0.31455
0.16667 | 73.1 | 0.36115 | 0.38708 | 0.45428
0.25 | 55.7 | 0.47397 | 0.50422 | 0.5837
0.33333 | 45.4 | 0.5815 | 0.61599 | 0.7057
0.41667 | 38.2 | 0.6911 | 0.72901 | 0.82965
0.5 | 33.3 | 0.79279 | 0.83452 | 0.9438
0.58333 | 29.6 | 0.89189 | 0.93588 | 1.0555
0.66667 | 26.6 | 0.99248 | 1.0403 | 1.1676
0.75 | 24.3 | 1.0864 | 1.1364 | 1.2722
1 | 19.3 | 1.3679 | 1.4264 | 1.585
2 | 10.8 | 2.4444 | 2.5279 | 2.7652
3 | 7.56 | 3.4921 | 3.6001 | 3.9105
4 | 5.85 | 4.5128 | 4.6428 | 5.0142
5 | 4.79 | 5.5115 | 5.6644 | 6.1239
6 | 4.07 | 6.4865 | 6.6665 | 7.2072
7 | 3.53 | 7.4788 | 7.6863 | 8.3097
8 | 3.13 | 8.4345 | 8.6508 | 9.2585
9 | 2.81 | 9.395 | 9.6359 | 10.3129
10 | 2.61 | 10.1149 | 10.3637 | 11.0667
20 | 1.43 | 18.4615 | 18.9155 | 20.1986
Enersys Powersafe SBS 31 | [5 empty] | 10V
Ref (Ah): | 26.4 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 110 | 0.24 | 0.26115 | 0.31455
0.16667 | 73.1 | 0.36115 | 0.38708 | 0.45428
0.25 | 55.7 | 0.47397 | 0.50422 | 0.5837
0.33333 | 45.4 | 0.5815 | 0.61599 | 0.7057
0.41667 | 38.2 | 0.6911 | 0.72901 | 0.82965
0.5 | 33.3 | 0.79279 | 0.83452 | 0.9438
0.58333 | 29.6 | 0.89189 | 0.93588 | 1.0555
0.66667 | 26.6 | 0.99248 | 1.0403 | 1.1676
0.75 | 24.3 | 1.0864 | 1.1364 | 1.2722
1 | 19.3 | 1.3679 | 1.4264 | 1.585
2 | 10.8 | 2.4444 | 2.5279 | 2.7652
3 | 7.56 | 3.4921 | 3.6001 | 3.9105
4 | 5.85 | 4.5128 | 4.6428 | 5.0142
5 | 4.79 | 5.5115 | 5.6644 | 6.1239
6 | 4.07 | 6.4865 | 6.6665 | 7.2072
7 | 3.53 | 7.4788 | 7.6863 | 8.3097
8 | 3.13 | 8.4345 | 8.6508 | 9.2585
9 | 2.81 | 9.395 | 9.6359 | 10.3129
10 | 2.61 | 10.1149 | 10.3637 | 11.0667
20 | 1.43 | 18.4615 | 18.9155 | 20.1986
Enersys Powersafe SBS 40 | [5 empty] | 12V
Ref (Ah): | 37.7 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 139 | 0.27122 | 0.29513 | 0.35547
0.16667 | 96.5 | 0.39067 | 0.41873 | 0.49141
0.25 | 75.3 | 0.50066 | 0.53262 | 0.61658
0.33333 | 62.2 | 0.60611 | 0.64206 | 0.73557
0.41667 | 53.3 | 0.70732 | 0.74612 | 0.84912
0.5 | 46.7 | 0.80728 | 0.84977 | 0.96105
0.58333 | 41.7 | 0.90408 | 0.94866 | 1.0699
0.66667 | 37.6 | 1.0027 | 1.051 | 1.1796
0.75 | 34.4 | 1.0959 | 1.1464 | 1.2833
1 | 27.4 | 1.3759 | 1.4347 | 1.5943
2 | 15.4 | 2.4481 | 2.5316 | 2.7693
3 | 10.8 | 3.4907 | 3.5987 | 3.909
4 | 8.33 | 4.5258 | 4.6562 | 5.0287
5 | 6.81 | 5.536 | 5.6896 | 6.1511
6 | 5.77 | 6.5338 | 6.7151 | 7.2598
7 | 5.01 | 7.525 | 7.7338 | 8.3611
8 | 4.52 | 8.3407 | 8.5546 | 9.1556
9 | 3.97 | 9.4962 | 9.7397 | 10.424
10 | 3.72 | 10.1344 | 10.3836 | 11.088
20 | 2.04 | 18.4804 | 18.9348 | 20.2192
Enersys Powersafe SBS 41 | [5 empty] | 10V
Ref (Ah): | 37.7 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 139 | 0.27122 | 0.29513 | 0.35547
0.16667 | 96.5 | 0.39067 | 0.41873 | 0.49141
0.25 | 75.3 | 0.50066 | 0.53262 | 0.61658
0.33333 | 62.2 | 0.60611 | 0.64206 | 0.73557
0.41667 | 53.3 | 0.70732 | 0.74612 | 0.84912
0.5 | 46.7 | 0.80728 | 0.84977 | 0.96105
0.58333 | 41.7 | 0.90408 | 0.94866 | 1.0699
0.66667 | 37.6 | 1.0027 | 1.051 | 1.1796
0.75 | 34.4 | 1.0959 | 1.1464 | 1.2833
1 | 27.4 | 1.3759 | 1.4347 | 1.5943
2 | 15.4 | 2.4481 | 2.5316 | 2.7693
3 | 10.8 | 3.4907 | 3.5987 | 3.909
4 | 8.33 | 4.5258 | 4.6562 | 5.0287
5 | 6.81 | 5.536 | 5.6896 | 6.1511
6 | 5.77 | 6.5338 | 6.7151 | 7.2598
7 | 5.01 | 7.525 | 7.7338 | 8.3611
8 | 4.52 | 8.3407 | 8.5546 | 9.1556
9 | 3.97 | 9.4962 | 9.7397 | 10.424
10 | 3.72 | 10.1344 | 10.3836 | 11.088
20 | 2.04 | 18.4804 | 18.9348 | 20.2192
Enersys Powersafe SBS 60 | [5 empty] | 12V
Ref (Ah): | 50.8 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 173 | 0.29364 | 0.31952 | 0.38485
0.16667 | 123 | 0.41301 | 0.44267 | 0.51951
0.25 | 97 | 0.52371 | 0.55714 | 0.64496
0.33333 | 80.7 | 0.62949 | 0.66683 | 0.76395
0.41667 | 68.7 | 0.73945 | 0.78001 | 0.88769
0.5 | 60.5 | 0.83967 | 0.88386 | 0.99961
0.58333 | 54.2 | 0.93727 | 0.98349 | 1.1092
0.66667 | 49.1 | 1.0346 | 1.0845 | 1.2172
0.75 | 45 | 1.1289 | 1.1808 | 1.3219
1 | 36.1 | 1.4072 | 1.4674 | 1.6306
2 | 20.6 | 2.466 | 2.5502 | 2.7896
3 | 14.6 | 3.4795 | 3.5871 | 3.8964
4 | 11.4 | 4.4561 | 4.5845 | 4.9513
5 | 9.34 | 5.439 | 5.5899 | 6.0433
6 | 7.94 | 6.398 | 6.5755 | 7.1089
7 | 6.91 | 7.3517 | 7.5557 | 8.1685
8 | 6.13 | 8.2871 | 8.4996 | 9.0967
9 | 5.5 | 9.2364 | 9.4732 | 10.1387
10 | 5 | 10.16 | 10.4098 | 11.116
20 | 2.68 | 18.9552 | 19.4213 | 20.7388
Enersys Powersafe SBS 110 | [5 empty] | 6V
Ref (Ah): | 115 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 290 | 0.39655 | 0.4315 | 0.51973
0.16667 | 223 | 0.5157 | 0.55273 | 0.64867
0.25 | 183 | 0.62842 | 0.66853 | 0.77391
0.33333 | 156 | 0.73718 | 0.78091 | 0.89464
0.41667 | 137 | 0.83942 | 0.88546 | 1.0077
0.5 | 122 | 0.94262 | 0.99223 | 1.1222
0.58333 | 110 | 1.0455 | 1.097 | 1.2372
0.66667 | 101 | 1.1386 | 1.1935 | 1.3395
0.75 | 92.9 | 1.2379 | 1.2949 | 1.4495
1 | 75.7 | 1.5192 | 1.5841 | 1.7603
2 | 44.4 | 2.5901 | 2.6785 | 2.93
3 | 31.9 | 3.605 | 3.7165 | 4.037
4 | 25.1 | 4.5817 | 4.7137 | 5.0907
5 | 20.7 | 5.5556 | 5.7097 | 6.1728
6 | 17.7 | 6.4972 | 6.6775 | 7.2191
7 | 15.5 | 7.4194 | 7.6252 | 8.2437
8 | 13.8 | 8.3333 | 8.547 | 9.1475
9 | 12.4 | 9.2742 | 9.512 | 10.1802
10 | 11.4 | 10.0877 | 10.3358 | 11.0369
20 | 6.19 | 18.5784 | 19.0352 | 20.3264
Enersys Powersafe SBS 130 | [5 empty] | 6V
Ref (Ah): | 132 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 370 | 0.35676 | 0.3882 | 0.46757
0.16667 | 268 | 0.49254 | 0.52791 | 0.61954
0.25 | 215 | 0.61395 | 0.65314 | 0.7561
0.33333 | 181 | 0.72928 | 0.77254 | 0.88505
0.41667 | 157 | 0.84076 | 0.88688 | 1.0093
0.5 | 140 | 0.94286 | 0.99248 | 1.1224
0.58333 | 126 | 1.0476 | 1.0993 | 1.2398
0.66667 | 115 | 1.1478 | 1.2032 | 1.3504
0.75 | 106 | 1.2453 | 1.3026 | 1.4582
1 | 86.3 | 1.5295 | 1.5949 | 1.7724
2 | 50.8 | 2.5984 | 2.6871 | 2.9394
3 | 36.6 | 3.6066 | 3.7181 | 4.0387
4 | 28.8 | 4.5833 | 4.7154 | 5.0926
5 | 23.8 | 5.5462 | 5.7001 | 6.1625
6 | 20.3 | 6.5025 | 6.6829 | 7.225
7 | 17.8 | 7.4157 | 7.6215 | 8.2397
8 | 15.8 | 8.3544 | 8.5686 | 9.1706
9 | 14.3 | 9.2308 | 9.4675 | 10.1326
10 | 13 | 10.1538 | 10.4035 | 11.1092
20 | 6.94 | 19.0202 | 19.4879 | 20.8098
Enersys Powersafe SBS 300 | [5 empty] | 2V
Ref (Ah): | 310 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 826 | 0.3753 | 0.40838 | 0.49188
0.16667 | 622 | 0.49839 | 0.53418 | 0.62691
0.25 | 500 | 0.62 | 0.65957 | 0.76355
0.33333 | 413 | 0.75061 | 0.79513 | 0.91093
0.41667 | 357 | 0.86835 | 0.91598 | 1.0424
0.5 | 310 | 1 | 1.0526 | 1.1905
0.58333 | 282 | 1.0993 | 1.1535 | 1.3009
0.66667 | 255 | 1.2157 | 1.2743 | 1.4302
0.75 | 239 | 1.2971 | 1.3568 | 1.5188
1 | 187 | 1.6578 | 1.7286 | 1.9209
2 | 109 | 2.844 | 2.9411 | 3.2172
3 | 78.1 | 3.9693 | 4.092 | 4.4449
4 | 62 | 5 | 5.144 | 5.5556
5 | 52 | 5.9615 | 6.127 | 6.6239
6 | 45.3 | 6.8433 | 7.0332 | 7.6036
7 | 40.3 | 7.6923 | 7.9058 | 8.547
8 | 36.1 | 8.5873 | 8.8074 | 9.4262
9 | 32.8 | 9.4512 | 9.6936 | 10.3746
10 | 30.6 | 10.1307 | 10.3798 | 11.0839
20 | 17.2 | 18.0233 | 18.4665 | 19.7191
Enersys Powersafe SBS 390 | [5 empty] | 2V
Ref (Ah): | 360 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 866 | 0.4157 | 0.45234 | 0.54483
0.16667 | 683 | 0.52709 | 0.56494 | 0.663
0.25 | 567 | 0.63492 | 0.67545 | 0.78192
0.33333 | 488 | 0.7377 | 0.78147 | 0.89527
0.41667 | 429 | 0.83916 | 0.88519 | 1.0074
0.5 | 385 | 0.93506 | 0.98428 | 1.1132
0.58333 | 349 | 1.0315 | 1.0824 | 1.2207
0.66667 | 319 | 1.1285 | 1.1829 | 1.3277
0.75 | 295 | 1.2203 | 1.2765 | 1.429
1 | 241 | 1.4938 | 1.5576 | 1.7309
2 | 142 | 2.5352 | 2.6217 | 2.8679
3 | 102 | 3.5294 | 3.6386 | 3.9523
4 | 79.7 | 4.5169 | 4.6471 | 5.0188
5 | 65.8 | 5.4711 | 5.6229 | 6.079
6 | 55.9 | 6.4401 | 6.6188 | 7.1556
7 | 48.7 | 7.3922 | 7.5973 | 8.2136
8 | 43.5 | 8.2759 | 8.4881 | 9.0844
9 | 39 | 9.2308 | 9.4675 | 10.1326
10 | 35.7 | 10.084 | 10.332 | 11.0329
20 | 19 | 18.9474 | 19.4133 | 20.7302
Enersys Powersafe SBS B8 | [5 empty] | 12V
Ref (Ah): | 30.5 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 146 | 0.2089 | 0.22732 | 0.27379
0.16667 | 83.9 | 0.36353 | 0.38963 | 0.45727
0.25 | 61.4 | 0.49674 | 0.52845 | 0.61175
0.33333 | 49.3 | 0.61866 | 0.65536 | 0.7508
0.41667 | 41.6 | 0.73317 | 0.77339 | 0.88016
0.5 | 36.3 | 0.84022 | 0.88444 | 1.0003
0.58333 | 32.3 | 0.94427 | 0.99084 | 1.1175
0.66667 | 29.2 | 1.0445 | 1.0949 | 1.2288
0.75 | 26.6 | 1.1466 | 1.1994 | 1.3426
1 | 21.4 | 1.4252 | 1.4862 | 1.6515
2 | 12.3 | 2.4797 | 2.5643 | 2.8051
3 | 8.8 | 3.4659 | 3.5731 | 3.8812
4 | 6.87 | 4.4396 | 4.5675 | 4.9329
5 | 5.64 | 5.4078 | 5.5579 | 6.0087
6 | 4.78 | 6.3808 | 6.5578 | 7.0897
7 | 4.14 | 7.3671 | 7.5716 | 8.1857
8 | 3.75 | 8.1333 | 8.3419 | 8.9279
9 | 3.35 | 9.1045 | 9.3379 | 9.9939
10 | 3.02 | 10.0993 | 10.3477 | 11.0496
20 | 1.53 | 19.9346 | 20.4248 | 21.8103
Enersys Powersafe SBS B10 | [5 empty] | 12V
Ref (Ah): | 38.1 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 129 | 0.29535 | 0.32138 | 0.38709
0.16667 | 92.7 | 0.411 | 0.44052 | 0.51699
0.25 | 72.6 | 0.52479 | 0.55829 | 0.6463
0.33333 | 59.9 | 0.63606 | 0.67379 | 0.77192
0.41667 | 51 | 0.74706 | 0.78804 | 0.89683
0.5 | 44.5 | 0.85618 | 0.90124 | 1.0193
0.58333 | 39.5 | 0.96456 | 1.0121 | 1.1415
0.66667 | 35.5 | 1.0732 | 1.125 | 1.2626
0.75 | 32.3 | 1.1796 | 1.2339 | 1.3812
1 | 25.5 | 1.4941 | 1.558 | 1.7313
2 | 13.9 | 2.741 | 2.8345 | 3.1007
3 | 9.66 | 3.9441 | 4.0661 | 4.4167
4 | 7.45 | 5.1141 | 5.2614 | 5.6823
5 | 6.09 | 6.2562 | 6.4298 | 6.9513
6 | 5.17 | 7.3694 | 7.5739 | 8.1883
7 | 4.51 | 8.4479 | 8.6823 | 9.3865
8 | 4.13 | 9.2252 | 9.4617 | 10.1264
9 | 3.91 | 9.7442 | 9.9941 | 10.6962
10 | 3.74 | 10.1872 | 10.4377 | 11.1457
20 | 2.1 | 18.1429 | 18.589 | 19.85
Enersys Powersafe SBS B14 | [5 empty] | 12V
Ref (Ah): | 61.7 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 193 | 0.31969 | 0.34787 | 0.41899
0.16667 | 143 | 0.43147 | 0.46245 | 0.54273
0.25 | 115 | 0.53652 | 0.57077 | 0.66074
0.33333 | 97 | 0.63608 | 0.67382 | 0.77194
0.41667 | 84.2 | 0.73278 | 0.77297 | 0.87969
0.5 | 74.6 | 0.82708 | 0.87061 | 0.98462
0.58333 | 67.1 | 0.91952 | 0.96487 | 1.0882
0.66667 | 61.1 | 1.0098 | 1.0585 | 1.188
0.75 | 56.1 | 1.0998 | 1.1504 | 1.2878
1 | 45.2 | 1.365 | 1.4234 | 1.5817
2 | 25.9 | 2.3822 | 2.4635 | 2.6948
3 | 18.3 | 3.3716 | 3.4759 | 3.7756
4 | 14.2 | 4.3451 | 4.4702 | 4.8279
5 | 11.7 | 5.2735 | 5.4198 | 5.8594
6 | 9.88 | 6.2449 | 6.4182 | 6.9388
7 | 8.58 | 7.1911 | 7.3907 | 7.9902
8 | 7.59 | 8.1291 | 8.3376 | 8.9233
9 | 6.8 | 9.0735 | 9.3062 | 9.96
10 | 6.17 | 10 | 10.2459 | 10.9409
20 | 3.22 | 19.1615 | 19.6327 | 20.9644
Enersys Powersafe SBS C11 | [5 empty] | 12V
Ref (Ah): | 91.5 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 248 | 0.36895 | 0.40147 | 0.48355
0.16667 | 184 | 0.49728 | 0.53299 | 0.62551
0.25 | 149 | 0.61409 | 0.65329 | 0.75627
0.33333 | 126 | 0.72619 | 0.76927 | 0.8813
0.41667 | 110 | 0.83182 | 0.87745 | 0.99858
0.5 | 97.4 | 0.93943 | 0.98887 | 1.1184
0.58333 | 87.8 | 1.0421 | 1.0935 | 1.2333
0.66667 | 80.1 | 1.1423 | 1.1974 | 1.3439
0.75 | 73.7 | 1.2415 | 1.2987 | 1.4538
1 | 59.7 | 1.5327 | 1.5982 | 1.776
2 | 34.8 | 2.6293 | 2.719 | 2.9743
3 | 24.9 | 3.6747 | 3.7883 | 4.115
4 | 19.6 | 4.6684 | 4.8028 | 5.1871
5 | 16.1 | 5.6832 | 5.8409 | 6.3147
6 | 13.8 | 6.6304 | 6.8144 | 7.3671
7 | 12.1 | 7.562 | 7.7718 | 8.4022
8 | 11.1 | 8.2432 | 8.4546 | 9.0486
9 | 10 | 9.15 | 9.3846 | 10.0439
10 | 9.08 | 10.0771 | 10.3249 | 11.0253
20 | 4.92 | 18.5976 | 19.0549 | 20.3474

## Calculations (hidden)
NOTE: Column A must be sorted in ascending order!
Monobloc Data |  | Duty Summary |  |  | IEEE 485 Calculation Method (Kt: 1.85V/Cell @ 20degC) | [6 empty] | Switchgear Tripping & Closing
Monobloc Types | Ah Capacity | Description | Current A1…A8 (amps) | Duration M1 ..M8 (hours) | Period | Load (A) | Change in Load (A) | Duration of Period (hours) | Time to end of section (hours) | Capacity Rating Factor Kt | Required Section Size (Ah) | Maximum Tripping Burden (Watts) | Maximum Tripping Duration (hours) | Maximum Closing Burden (Watts) | Maximum Closing Duration (Hours)
Enersys Powersafe SBS 130 | 132 | Period 1 | 0.26978 | 72 | Period 1 | [6 empty] | 300 | 0.06 | 0 | 0
Enersys Powersafe SBS 41 | 37.7 | Period 2 | 11.0612 | 1.6667e-05 | 1 | 0.26978 | 0.26978 | 72 | 72 | 61.8795 | 16.6941 | 0 | 0 | 0 | 0
|  | Period 3 | 0.26978 | 0 | [5 empty] | Total (1) | 16.6941 | 0 | 0 | 0 | 0
|  | Period 4 | 0 | 0 | Period 2 | [6 empty] | 300 | 1.6667e-05 | 0 | 0
Enersys Powersafe SBS 110 | 115 | Period 5 | 0 | 0 | 1 | 0.26978 | 0.26978 | 72 | 72 | 61.8795 | 16.6941
Enersys Powersafe SBS 130 | 132 | Period 6 | 0 | 0 | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.27122 | 2.9269
Enersys Powersafe SBS 15 | 14 | Period 7 | 0 | 0 | [5 empty] | Total (2) | 19.621
Enersys Powersafe SBS 30 | 26.4 | Period 8 | 0 | 0 | Period 3
Enersys Powersafe SBS 300 | 310 |  |  |  | 1 | 0.26978 | 0.26978 | 72 | 72 | 61.8795 | 16.6941
Enersys Powersafe SBS 31 | 26.4 |  |  |  | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.27122 | 2.9269
Enersys Powersafe SBS 390 | 360 |  |  |  | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
Enersys Powersafe SBS 40 | 37.7 | [8 empty] | Total (3) | 19.621
Enersys Powersafe SBS 41 | 37.7 |  |  |  | Period 4
Enersys Powersafe SBS 60 | 50.8 |  |  |  | 1 | 0.26978 | 0.26978 | 72 | 72 | 61.8795 | 16.6941
Enersys Powersafe SBS 8 | 7.4 |  |  |  | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.27122 | 2.9269
Enersys Powersafe SBS B10 | 38.1 |  |  |  | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
Enersys Powersafe SBS B14 | 61.7 |  |  |  | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
Enersys Powersafe SBS B8 | 30.5 | [8 empty] | Total (4) | 19.621
Enersys Powersafe SBS C11 | 91.5 |  |  |  | Period 5
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 61.8795 | 16.6941
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.27122 | 2.9269
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (5) | 19.621
Period 6
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 61.8795 | 16.6941
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.27122 | 2.9269
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (6) | 19.621
Period 7
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 61.8795 | 16.6941
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.27122 | 2.9269
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (7) | 19.621
Period 8
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 61.8795 | 16.6941
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.27122 | 2.9269
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 8 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (8) | 19.621
IEEE 485 Calculation Method (Kt: 1.85V/Cell @ 15degC)
[5 empty] | Period | Load (A) | Change in Load (A) | Duration of Period (hours) | Time to end of section (hours) | Capacity Rating Factor Kt | Required Section Size (Ah)
Period 1
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 63.4011 | 17.1046
[10 empty] | Total (1) | 17.1046
Period 2
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 63.4011 | 17.1046
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.29513 | 3.1848
[10 empty] | Total (2) | 20.2895
Period 3
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 63.4011 | 17.1046
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.29513 | 3.1848
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (3) | 20.2895
Period 4
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 63.4011 | 17.1046
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.29513 | 3.1848
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (4) | 20.2895
Period 5
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 63.4011 | 17.1046
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.29513 | 3.1848
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (5) | 20.2895
Period 6
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 63.4011 | 17.1046
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.29513 | 3.1848
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (6) | 20.2895
Period 7
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 63.4011 | 17.1046
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.29513 | 3.1848
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (7) | 20.2895
Period 8
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 63.4011 | 17.1046
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.29513 | 3.1848
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 8 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (8) | 20.2895
IEEE 485 Calculation Method (Kt: 1.85V/Cell @ 5degC)
[5 empty] | Period | Load (A) | Change in Load (A) | Duration of Period (hours) | Time to end of section (hours) | Capacity Rating Factor Kt | Required Section Size (Ah)
Period 1
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 67.7019 | 18.2649
[10 empty] | Total (1) | 18.2649
Period 2
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 67.7019 | 18.2649
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.35547 | 3.836
[10 empty] | Total (2) | 22.1009
Period 3
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 67.7019 | 18.2649
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.35547 | 3.836
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (3) | 22.1009
Period 4
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 67.7019 | 18.2649
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.35547 | 3.836
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (4) | 22.1009
Period 5
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 67.7019 | 18.2649
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.35547 | 3.836
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (5) | 22.1009
Period 6
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 67.7019 | 18.2649
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.35547 | 3.836
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (6) | 22.1009
Period 7
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 67.7019 | 18.2649
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.35547 | 3.836
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (7) | 22.1009
Period 8
[5 empty] | 1 | 0.26978 | 0.26978 | 72 | 72 | 67.7019 | 18.2649
[5 empty] | 2 | 11.0612 | 10.7914 | 1.6667e-05 | 1.6667e-05 | 0.35547 | 3.836
[5 empty] | 3 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 11.0612 | 0 | 0 | 0 | 0 | 0
[5 empty] | 8 | 11.0612 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (8) | 22.1009