## Schedule 1 (Approved Devices)
Manufacturer | Model | Variant | Hardware version | Software / firmware version | Functions | Auxilliary supply voltage | Restrictions | Notes | Technology | Assessment type | Assessment reference | First approved issue
A-Eberle | EOR-3DS | EOR-3DS-B04-H23-C21.Fxx-U10.Dxx-T0-P0-V0-K0 Refer to notes for additional guidance |  |  | ASC Earth Fault Indicator | 24-110V | For use with Compensated Earth Networks | Includes voltage transducer and ASC position transducer. xx within model number refers to optional connection cable length. Available options 0.3m, 1.5m, 3.0m. Lead length to be specified by relay panel supplier e.g. F15 = lead length 1.5m | Numeric | NGED | Available on request | 13
A-Eberle | REG-DP | REG-DP-B01-I0-H1-K0-E90-D2-X31-X18-XW0-Y1-U0-G2-A2 |  |  | ASC Resonance Controller | 24-110V | For use with Compensated Earth Networks |  | Numeric | NGED | Available on request | 13
Eaton Cooper Power Systems | CL-7 |  |  | 1.10.0 | VR |  | Only for use with Cooper Power System Voltage Regulators |  | Numeric | NGED |  | 10 or earlier
Fanox | SIA-C |  | R2.30 | 3.08/1.03 | 3OC, 3OCIT, E, EIT | Self-powered via CT inputs | Only for use on 6.6kV and 11kV network switchgear (e.g. RMUs etc.) |  | Numeric | ENA | NoC 201, issue 1 | 10 or earlier
Fundamentals | SuperTAPP SG | FP1034 – AGGG000PDS-L06-20-01A | 06 | SW: 10.02.2 TQ SW: 29 | TCC, TCM | AC 87.5 - 137.5V | Two-Winding Application | 4 Voltage & 3 Current Inputs 15 Digital Inputs & 12 Digital Outputs | Numeric | NGED |  | 12
Fundamentals | SuperTAPP SG | FP1034 – AGGGG00PDS-L06-20-01A | 06 | SW: 10.02.2 TQ SW: 29 | TCC, TCM | AC 87.5 - 137.5V | Two-Winding Application | 4 Voltage & 3 Current Inputs 20 Digital Inputs & 16 Digital Outputs | Numeric | NGED |  | 13
Fundamentals | SuperTAPP SG | FP1034 – AGGG00FPDS-L06-20-01A | 06 | SW: 10.02.2 TQ SW: 29 | TCC, TCM | AC 87.5 - 137.5V | Two-Winding Application | 4 Voltage & 10 Current Inputs 15 Digital Inputs & 12 Digital Outputs | Numeric | NGED |  | 12
Fundamentals | SuperTAPP SG | FP1034-AGGG00DPDS-L06-20-01A | 06 | SW: 10.02.2 TQ SW: 29 | TCC, TCM | AC 87.5 - 137.5V | Three-Winding Application | 8 Voltage & 6 Current Inputs 15 Digital Inputs & 12 Digital Outputs | Numeric | NGED |  | 12
Fundamentals | SuperTAPP SG | FP1034-AGGGG0DPDS-L06-20-01A | 06 | SW: 10.02.2 TQ SW: 29 | TCC, TCM | AC 87.5 - 137.5V | Three-Winding Application | 8 Voltage & 6 Current Inputs 20 Digital Inputs & 16 Digital Outputs | Numeric | NGED |  | 13
GE Vernova | Agile P14DB1 | P14DB11C4C0620A | A | 62 | 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, NVD, TCS, BBCK, AI |  | Relay shall not be used for NVD derived from capacitive cones or bushings. |  | Numeric | ENA | NoC 186, issue 4 | 10 or earlier
GE Vernova | Agile P14DB2 | P14DB21C4C0620A | A | 62 | 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, SEF, NVD, TCS, BBCK, AI |  | Relay shall not be used for NVD derived from capacitive cones or bushings. |  | Numeric | ENA | NoC 186, issue 4 | 10 or earlier
GE Vernova | Agile P14DL1 | P14DL11C4C0620A | A | 62 | 3OC, 3OCIT, 3DOCIT, 3DOCIT(LB), 3DOCIT(VC), E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, BBCK, AI |  |  | Relay includes load blinding and voltage controlled directional overcurrent features. | Numeric | ENA | NoC 186, issue 4 | 10 or earlier
GE Vernova | Agile P14DZ2 | P14DZ21C4C0620A | A | 62 | 3OC, 3OCIT, 3DOCIT, 3DOCIT(LB), 3DOCIT(VC), E, EIT, DEIT, SEF, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, BBCK, AI |  | For use with Schneider Genie Evo switchgear only. | Relay includes load blinding and voltage controlled directional overcurrent features. | Numeric | ENA | NoC 186, issue 4 | 10 or earlier
GE Vernova | Agile P14NB1 | P14NB11C4C0620A | A | 62 | 3OC, 3OCIT, EIT, TCS, BBCK, AI, SBEF |  |  |  | Numeric | ENA | NoC 185, issue 4 | 10 or earlier
GE Vernova | Agile P14NB2 | P14NB21C4C0620A | A | 62 | 3OC, 3OCIT, EIT, SEF, TCS, BBCK, AI |  |  |  | Numeric | ENA | NoC 185, issue 4 | 10 or earlier
GE Vernova | Agile P14NZ2 | P14NZ21C4C0620A | A | 62 | 3OC, 3OCIT, E, EIT, SEF, AR, TCS, BBCK, AI |  |  |  | Numeric | ENA | NoC 185, issue 4 | 10 or earlier
GE Vernova | Agile P94VB | P94VB11A4B0620A | A | 62 | VTS, NVD, 3OV, 3UV, 3OF, 3UF, LFDD |  | Relay shall not be used for NVD derived from capacitive cones or bushings. |  | Numeric | ENA | NoC 187, issue 4 | 11
GE Vernova | Agile P94VP | P94VP11A4B0620A | A | 62 | VTS, 3OV, 3UV, 3OF, 3UF, LFDD, SC |  | Relay shall not be used for NVD |  | Numeric | ENA | NoC 187, issue 4 | 11
GE Vernova | Micom P142 | P142811B4S0910P | P | 91 | 3OC, 3OCIT, E, EIT, SEF, AR, AR(LLC), TCS, BBCK, AI | 110Vd.c. |  | Without interMiCOM. Relay, software and logic configuration set up specifically for NGED auto-reclose application. | Numeric | ENA | NoC 101, Issue 12 | 13
GE Vernova | Micom P142 | P14281FB4S0910P | P | 91 | 3OC, 3OCIT, E, EIT, SEF, AR, AR(LLC), TCS, BBCK, AI, IT | 110Vd.c. |  | With interMiCOM. Relay, software and logic configuration set up specifically for NGED auto-reclose application. | Numeric | ENA | NoC 101, Issue 12 | 13
GE Vernova | Micom P145 | P145811A4S0910M | M | 91 | 3OC, 3OCIT, 3DOCIT, DEIT, E, EIT, SEF, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, BBCK | 110Vd.c. |  |  | Numeric | ENA | NoC 101, Issue 12 | 13
GE Vernova | Micom P443 | P44381xx4S0910M | M | 91 | Z, 3DOCIT, 3OCIT, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), BBCK, TCS, VTS |  | For use on 132kV system only. | Mho & quad characteristics. | Numeric | ENA | NoC 128, Issue 8 | 12
GE Vernova | Micom P445 | P445811B4S0490P | P | 49 | Z, 3DOCIT, 3OCIT, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), BBCK, TCS, VTS |  | Only for use on 33kV and 66kV systems. | Mho Phase Characteristic and Mho/Quadrilateral E/F Characteristic. | Numeric | ENA | NoC 142, Issue 7 | 12
GE Vernova | Micom P54B | P54B81FA4S0920P | P | 92 | CD, 3DOCIT, 3OC, 3OCIT, DEIT, E, EIT, AR, TCS, VTS | 110Vd.c. | Not compatible with existing Micom P54x Line Differential Relays For use with 850nm multi-mode fibre. | Multi-Ended Line Differential - Capable of Protecting up to 6 Ends 8 Binary Inputs & 8 Binary Outputs | Numeric | ENA | NoC 234, Issue 1 | 13
GE Vernova | Micom P54B | P54B81FC4S0920P | P | 92 | CD, 3DOCIT, 3OC, 3OCIT, DEIT, E, EIT, AR, TCS, VTS | 110Vd.c. | Not compatible with existing Micom P54x Line Differential Relays For use with 1300nm single-mode fibre. | Multi-Ended Line Differential - Capable of Protecting up to 6 Ends 8 Binary Inputs & 8 Binary Outputs | Numeric | ENA | NoC 234, Issue 1 | 13
GE Vernova | Micom P54C | P54C81FA4S0920M | M | 92 | CD, 3DOCIT, 3OC, 3OCIT, DEIT, E, EIT, SEF, AR, TCS, VTS | 110Vd.c. | Not compatible with existing Micom P54x Line Differential Relays For use with 850nm multi-mode fibre. | Multi-Ended Line Differential - Capable of Protecting up to 6 Ends 16 Binary Inputs & 16 Binary Outputs | Numeric | ENA | NoC 234, Issue 1 | 13
GE Vernova | Micom P54C | P54C81FC4S0920M | M | 92 | CD, 3DOCIT, 3OC, 3OCIT, DEIT, E, EIT, SEF, AR, TCS, VTS | 110Vd.c. | Not compatible with existing Micom P54x Line Differential Relays For use with 1300nm single-mode fibre. | Multi-Ended Line Differential - Capable of Protecting up to 6 Ends 16 Binary Inputs & 16 Binary Outputs | Numeric | ENA | NoC 234, Issue 1 | 13
GE Vernova | Micom P54E | P54E81FA4S0920M | M | 92 | CD, 3DOCIT, 3OC, 3OCIT, DEIT, E, EIT, SEF, AR, TCS, VTS | 110Vd.c. | Not compatible with existing Micom P54x Line Differential Relays For use with 850nm multi-mode fibre. | Multi-Ended Line Differential - Capable of Protecting up to 6 Ends 24 Binary Inputs & 32 Binary Outputs | Numeric | ENA | NoC 234, Issue 1 | 13
GE Vernova | Micom P54E | P54E81FC4S0920M | M | 92 | CD, 3DOCIT, 3OC, 3OCIT, DEIT, E, EIT, SEF, AR, TCS, VTS | 110Vd.c. | Not compatible with existing Micom P54x Line Differential Relays For use with 1300nm single-mode fibre. | Multi-Ended Line Differential - Capable of Protecting up to 6 Ends 24 Binary Inputs & 32 Binary Outputs | Numeric | ENA | NoC 234, Issue 1 | 13
GE Vernova | Micom P541 | P541814A4S0300J | J | 30 | CD, 3OC, 3OCIT, E, EIT, TCS | 110Vd.c. | For use with 850nm multi-mode fibre. | Last Order Date December 14th 2027 | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P541 | P541814C4S0300J | J | 30 | CD, 3OC, 3OCIT, E, EIT, TCS | 110Vd.c. | For use with 1300nm single-mode fibre. | Last Order Date December 14th 2027 | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P542 | P542814A4S0300J | J | 30 | CD, 3OC, 3OCIT, E, EIT, AR, TCS | 110Vd.c. | For use with 850nm multi-mode fibre. | Last Order Date December 14th 2027 | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P542 | P542814C4S0300J | J | 30 | CD, 3OC, 3OCIT, E, EIT, AR, TCS | 110Vd.c. | For use with 1300nm single-mode fibre. | Last Order Date December 14th 2027 | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P543 | P543814A4S0570K | K | 57 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS | 110Vd.c. | For use with 850nm multi-mode fibre. | This model is officially obsolete from manufacturer, latest version is currently undergoing ENA assessment. The obsolete version can continue to be purchased for NGED under an OPRA Vendor to quote OPRA Reference 13714971304 upon placement of order | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P543 | P543814A4S0610M | M | 61 | CD, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS | 110Vd.c. | For use with 850nm multi-mode fibre. Firmware version 61 does not include distance protection. | This model had been withdrawn by the manufacturer but has now been reinstated to the product line. | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P543 | P543814C4S0570K | K | 57 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS | 110Vd.c. | For use with 1300nm single-mode fibre. | This model is officially obsolete from manufacturer, latest version is currently undergoing ENA assessment. The obsolete version can continue to be purchased for NGED under an OPRA Vendor to quote OPRA Reference 13950689518 upon placement of order | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P543 | P543814C4S0610M | M | 61 | CD, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS | 110Vd.c. | For use with 1300nm single-mode fibre. Firmware version 61 does not include distance protection. | This model had been withdrawn by the manufacturer but has now been reinstated to the product line. | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P545 | P545814A4S0570K | K | 57 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, TCS, VTS | 110Vd.c. | For use with 850nm multi-mode fibre. | This model is officially obsolete from manufacturer, latest version is currently undergoing ENA assessment. The obsolete version can continue to be purchased for NGED under an OPRA Vendor to quote OPRA Reference 13950689344 upon placement of order | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P545 | P545814C4S0570K | K | 57 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, TCS, VTS | 110Vd.c. | For use with 1300nm single-mode fibre. | This model is officially obsolete from manufacturer, latest version is currently undergoing ENA assessment. The obsolete version can continue to be purchased for NGED under an OPRA Vendor to quote OPRA Reference 13950812213 upon placement of order | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P546 | P546814A4S0710M | M | 71 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, TCS, VTS |  | For use with 850nm multi-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P546 | P546814C4S0710M | M | 71 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, TCS, VTS |  | For use with 1300nm single-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Vernova | Micom P642 | P642811D4S0910P | P | 91 | BD, REF, 3OC, 3OCIT, E, EIT, VTS, CTS |  | For use with 2 winding transformers. A suitable panel-mounted metrosil and series stabilising resistor shall be provided for each REF zone. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. |  | Numeric | ENA | NoC 153, Issue 5 | 13
GE Vernova | Micom P643 | P643811A4S0910M | M | 91 | BD, REF, 3OC, 3OCIT, E, EIT, VTS, CTS |  | For use with 3 winding transformers. A suitable panel-mounted metrosil and series stabilising resistor shall be provided for each REF zone. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. |  | Numeric | ENA | NoC 153, Issue 6 | 13
GE Vernova | DIP.NET | 7XX-B-1X-A-SXXR4.3 |  | R4.3 | IT | 48 - 125Vd.c. | Not compatible with Existing DIP5000/DIP53 devices | With LCD Screen Vendor to supply additional SPF Transceiver Module in line with below options | Numeric | NGED | Available on request | 13
GE Vernova | DIP.NET SPF Transceiver Module | ALSFP00-MM-20 | [5 empty] | Standard multi-mode module - SFP connector for C37.94 | N/A |  |  | 13
GE Vernova | DIP.NET SPF Transceiver Module | ALSFP00-L1.2e | [5 empty] | Standard single-mode module - Max. Distance: 100 Km, 1550nm | N/A |  |  | 13
GE Vernova | MMLG02 |  |  |  | RTB |  |  | Intercompatible with Siemens 7XG22 (RMLG02) | N/A |  |  | 10 or earlier
GE Vernova | BA300 |  |  |  | BA |  |  |  | Electronic |  |  | 10 or earlier
GE Vernova | MBCI 01 (Translay 'S') |  |  |  | PW |  | For use with NGED owned pilots. Pilots shall be supervised. Isolation requirements shall be determined with reference to ACE 19. Other scheme components shall be selected in accordance with this schedule and the manufacturer's application note. | Main relay of Translay 'S' scheme. | Electronic | ENA | Approval Notice 39 | 10 or earlier
GE Vernova | MCAA11 | MCAA11R1BU9032C |  |  | TI | 110Vd.c. | For use with high burden MVAJ10x or MVAJ20x relays | 3M & 1B S/R contacts & H/R flag. ITEST = 0.37A Diagram 01MCAA111001 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MCAA11 | MCAA11R1BU9036C |  |  | TI | 110Vd.c. | For use with high burden MVAJ10x or MVAJ20x relays | 4M S/R contacts & H/R flag. ITEST = 0.37A Diagram 01MCAA111001 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MCAA11 | MCAA11R1BU9037C |  |  | TI | 110Vd.c. | For use with high burden MVAJ10x or MVAJ20x relays | 2M & 2B S/R contacts & H/R flag. ITEST = 0.37A Diagram 01MCAA111001 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MCAA12 | MCAA12R1BU9002C |  |  | TI | 110Vd.c. | For use with Brush Quantum and Horizon switchgear. | 1M/1B S/R & 1M/1B H/R contacts & H/R flag. Inon = 0.227A, ITEST = 0.14A Diagram 01MCAA1203 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MCAA12 | MCAA12R1BU9003C |  |  | TI | 110Vd.c. | For use with high burden MVAJ10x or MVAJ20x relays | 1M/1B S/R & 1M/1B H/R contacts & H/R flag. ITEST = 0.37A Diagram 01MCAA1203 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MCAA12 | MCAA12R1BU9004C |  |  | TI | 110Vd.c. | For use with Schneider WS switchgear (Trip Coil 25VA) and Ormazabal 33kV switchgear | 2M S/R & 1M / 1B H/R contacts & H/R flag. Inon = 0.15A, ITEST = 0.0083A Diagram 01MCAA1203 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MCAA12 | MCAA12R1BU9008C |  |  | TI | 110Vd.c. | For use with Siemens NX Plus Switchgear For use with Schneider Genie EVO Switchgear | 2M S/R & 1M/1B H/R contacts & H/R flag. ITEST = 0.34A | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MCAG14 |  |  |  | BEF |  | A suitable panel-mounted metrosil and series stabilising resistor shall be provided. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. | Single-pole current-calibrated high impedance relay | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MCAG34 |  |  |  | 3BBOC |  | Suitable panel-mounted metrosils and series stabilising resistors shall be provided. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. | Three-pole current-calibrated high impedance relay | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MFAC14 |  |  |  | REF |  | A suitable panel-mounted metrosil and shunt setting resistor shall be provided. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. | Single-pole voltage-calibrated high impedance relay | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MRTP 01 |  |  |  | PWS | 240Va.c. and 110Vd.c. | For use with MBCI 01 in Translay 'S' scheme. For 5kV pilot applications. | Supervision relay and send-end injection filter for Translay 'S' scheme with integrated monitoring of a.c. supply. | Electronic | ENA | Approval Notice 9 | 10 or earlier
GE Vernova | MRTP 02 |  |  |  | PWS |  | For use with MBCI 01 in Translay 'S' scheme. For 5kV pilot applications. | Receive-end injection filter for Translay 'S' scheme. | Electronic | ENA | Approval Notice 9 | 10 or earlier
GE Vernova | MVAA11 |  |  |  | AI |  |  | All elements to have self-reset contacts and hand reset flags. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MVAA21 |  |  |  | AI |  |  | All elements to have self-reset contacts and hand reset flags. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MVAJ051 | MVAJ051RA0201 |  |  | TS, BBCKA | 30Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Instantaneous Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ051 | MVAJ051RA0801 |  |  | TS, BBCKA | 110Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Instantaneous Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ053 | MVAJ053RA0201 |  |  | TH | 30Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Hand Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ053 | MVAJ053RA0801 |  |  | TH | 110Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Hand Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ055 | MVAJ055RA0201 |  |  | TH, TE | 30Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Hand / Electrical Reset Relay, Hand Reset Flag | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ055 | MVAJ055RA0801 |  |  | TH, TE | 110Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Hand / Electrical Reset Relay, Hand Reset Flag | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ101 | MVAJ101RA0202 |  |  | TS, BBCKA | 30Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Instantaneous Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ101 | MVAJ101RA0802 |  |  | TS, BBCKA | 110Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Instantaneous Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ102 | MVAJ102RA0202 |  |  | TDS | 30Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Nominal 2.5s Time Delay Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ102 | MVAJ102RA0802 |  |  | TDS | 110Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Nominal 2.5s Time Delay Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ105 | MVAJ105RA0202 |  |  | TH, TE | 30Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Hand / Electrical Reset Relay, Hand reset Flag | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAJ105 | MVAJ105RA0802 |  |  | TH, TE | 110Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Hand / Electrical Reset Relay, Hand reset Flag | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Vernova | MVAP22 |  |  |  | VTS |  |  |  | Electromechanical |  |  | 10 or earlier
GE Vernova | MVAW02 |  |  |  | SIR |  |  | Used with protection signalling schemes Last Order Date August 15th 2025 | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MVAX11 |  |  |  | TRS |  |  |  | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MVAX12 |  |  |  | TSS |  |  |  | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MVAX31 |  |  |  | TCS |  |  |  | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Vernova | MVTP31 |  |  |  | CTS |  |  |  | Electronic | ENA | NoC 42 | 10 or earlier
GE Vernova | MVTT14 |  |  |  | TD |  |  |  | Electronic | ENA | Approval Notice 35 | 10 or earlier
GE Vernova | MVUA11 |  |  |  | TD |  |  | Last Order Date August 15th 2025 | Electronic |  | Approval Notice 42 | 10 or earlier
Schneider Electric | ADVC3 |  |  |  | 3OC, 3OCIT, E, EIT, SEF, AR |  | For use with Schneider Pole Mounted Reclosers |  | Numeric | ENA | NoC 193 | 10 or earlier
Schneider Electric | PowerLogic P5U20 | P5U20-AABB-BAAEA-AFEA |  |  | 3OC, 3HOC, 3OCIT, E, EIT, SBEF, SEF, TCS, BBCK | 24-250VDC |  |  | Numeric | ENA | NoC 237 Issue 1 | 13
Schneider Electric | PowerLogic P5V20 | P5V20-AABB-DAAEA-AFEA |  |  | 3OV, 3UV, 3OF, 3UF, NVD VTS | 24-250VDC |  |  | Numeric | ENA | NoC 238 Issue 1 | 13
Schneider Electric | PowerLogic P5F30 | P5F30-AACB-GAAEA-AFEA |  |  | 3DOCIT, 3OC, 3HOC, 3OCIT, DEIT, E, EIT, SEF, NVD, 3OV, 3UV, 3OF, 3UF, TCS, BBCK, VTS | 24-250VDC |  |  | Numeric | ENA | NoC 239 Issue 1 | 13
Schneider Electric | GCM05 |  |  |  | IT |  | For use with NGED owned pilots. A trip relay approved for function TS shall be installed to provide trip indication on the front of the cubicle. |  | Electronic | ENA | Approval Notice 54 | 10 or earlier
Schneider Electric | VIP 400 |  |  |  | 3OC, 3OCIT, E, EIT | Self-powered via CT inputs | Only for use on Schneider Ringmaster Switchgear |  | Numeric | ENA | NoC 180, issue 1 | 10 or earlier
Schweitzer Engineering Laboratories (SEL) | SEL-751 Feeder Protection | 751#4V3Y | See Notes | R302-V2 | 3DOCIT, 3OC, 3HOC, 3OCIT, DEIT, E, EIT, SEF, NVD, 3OV, 3UV, 3OF, 3UF, TCS, AR, BBCK, VTS | 110Vd.c. | Only for use with CTs with a 1 Amp Secondary | SEL relay references do not define hardware versions. The ENA assessed hardware is obtained by ordering “Special Spec NOC 227 Issue 01" | Numeric | ENA | NOC 227 Issue 01 | 13
Schweitzer Engineering Laboratories (SEL) | SEL-751 Feeder Protection | 751#DVHP | See Notes | R302-V2 | 3DOCIT, 3OC, 3HOC, 3OCIT, DEIT, E, EIT, SEF, NVD, 3OV, 3UV, 3OF, 3UF, TCS, AR, BBCK, VTS | 110Vd.c. | Only for use with CTs with a 5 Amp Secondary | SEL relay references do not define hardware versions. The ENA assessed hardware is obtained by ordering “Special Spec NOC 227 Issue 01" | Numeric | ENA | NOC 227 Issue 01 | 13
Schweitzer Engineering Laboratories (SEL) | SEL-2595 | 2595#CR2C |  |  | IT | 48 - 125Vd.c. | Retrofit option for legacy Teleprotection Relays | No software required 8 Inputs & 8 Outputs 1300nm (IEEE C37.94 Modulation) Single Mode Fibre | Numeric | NGED |  | 13
Siemens | 7PG1111 (AR111) | 7PG1111-1xxx0-0AC0 |  |  | AI | 30Vd.c. |  | Instantaneous self-reset relay, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1111 (AR111) | 7PG1111-1xxx0-0AF0 |  |  | AI | 110Vd.c. |  | Instantaneous self-reset relay, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1112 (AR121) | 7PG1112-1CC10-0AM0 |  |  | PWS | 240Va.c. |  | A.C. supply supervision for Solkor R/Rf pilot supervision scheme. Instantaneous self-reset relay, reverse-operating hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1513 (TR131) | 7PG1513-1xxx0-1AF0 |  |  | TS | 110Vd.c. |  | Instantaneous self-reset relay, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1521-2 (TR212) | 7PG1521-2xxx0-1xC0 |  |  | TS | 30Vd.c. |  | Instantaneous self-reset relay, operating coil with economy cut-off, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1521-2 (TR212) | 7PG1521-2xxx0-1xF0 |  |  | TS | 110Vd.c. |  | Instantaneous self-reset relay, operating coil with economy cut-off, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1521-4 (TR214) | 7PG1521-4xxx0-1CC0 |  |  | TDS | 30Vd.c. |  | Nominal 2s time delay self-reset relay and hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1521-4 (TR214) | 7PG1521-4xxx0-1CF0 |  |  | TDS | 110Vd.c. |  | Nominal 2s time delay self-reset relay and hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1522 (TR221) | 7PG1522-1xxx0-1AC0 |  |  | TS | 30Vd.c. |  | Instantaneous self-reset relay, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1522 (TR221) | 7PG1522-1xxx0-1AF0 |  |  | TS | 110Vd.c. |  | Instantaneous self-reset relay, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1741 (XR153) | 7PG1741-1CC10-2AA0 |  |  | TSS | 30Vd.c. |  | Instantaneous self reset relay. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1741 (XR153) | 7PG1741-1CC10-4AA0 |  |  | TSS | 110Vd.c. |  | Instantaneous self reset relay. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2111 (Solkor R/Rf) | 7PG2111-1DA30-0DB0 |  |  | PW |  | For use with NGED-owned pilots. Pilots shall be supervised. For 1A CTs. Isolation requirements shall be determined with reference to ACE 19. Other scheme components shall be selected in accordance with this schedule and the manufacturer's application note. | Main relay of Solkor Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2111 (Solkor R/Rf) | 7PG2111-1DA30-0DD0 |  |  | PW |  | For use with NGED-owned pilots. Pilots shall be supervised. For 5A CTs. Isolation requirements shall be determined with reference to ACE 19. Other scheme components shall be selected in accordance with this schedule and the manufacturer's application note. | Main relay of Solkor Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2112 (Solkor 15kV Pilot Isolation Transformer) | 7PG2112-0AA00-0AA0 |  |  | PWI |  | For 15kV pilot applications | Isolation transformer for Solkor R/Rf scheme. | N/A |  |  | 10 or earlier
Siemens | 7PG2120 (Solkor Pilot Supervision Send Unit) | 7PG2120-0AA00-1CA0 |  |  | PWS |  | For 5kV pilot applications. a.c. supply shall be supervised by 7PG2132 (B22) relay. | Supervision relay and send-end injection filter for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2120 (Solkor Pilot Supervision Send Unit) | 7PG2120-0AA00-2WA0 |  |  | PWS |  | For 15kV pilot applications. a.c. supply shall be supervised by 7PG2132 (B22) relay. | Supervision relay and send-end injection filter for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2132 (B22) | 7PG2132-1CC40-1AC0 |  |  | PWS | 240Va.c. |  | A.C. supply supervision for Solkor R/Rf pilot supervision scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2144 (B75/B74) | 7PG2144-1CC40-1CB0 |  |  | PWS | 30Vd.c. | For 5kV pilot applications. | Combined pilot supervision receive unit and repeat relay for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2144 (B75/B74) | 7PG2144-1CC40-1CE0 |  |  | PWS | 110Vd.c. | For 5kV pilot applications. | Combined pilot supervision receive unit and repeat relay for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2154 (B75) | 7PG2154-1BA10-2WA0 |  |  | PWS |  | For 15kV pilot applications. | Pilot supervision receive unit for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2164 (B74) | 7PG2164-1CC40-2AB0 |  |  | PWS | 30Vd.c. | For 15kV pilot applications. | Receive-end pilot supervision repeat relay for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2164 (B74) | 7PG2164-1CC40-2AE0 |  |  | PWS | 110Vd.c. | For 15kV pilot applications. | Receive-end pilot supervision repeat relay for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2311 (5B3) | 7PG2311-1DA30-1BA0 |  |  | REF, BEF |  | A suitable panel-mounted shunt setting resistor shall be provided. The necessary rating and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. | An external metrosil is not required with this relay, which has a built-in non-linear resistor. | Electromechanical |  |  | 10 or earlier
Siemens | 7SL86 (Siprotec 5) | Product Code: P1C917346 |  | V8.83 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS, SC | 60-250VDC | Maximum 2 circuits / end-to-end only | For use with end to end line differential or distance protection (maximum 2 circuits / end-to-end) For use with multi-mode fibre - maximum cable run 2km | Numeric | ENA (Ongoing) |  | 13
Siemens | 7SL86 (Siprotec 5) | Product Code: P1C917407 |  | V8.83 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS, SC | 60-250VDC | Maximum 2 circuits / end-to-end only | For use with end to end line differential or distance protection (maximum 2 circuits / end-to-end) For use with single-mode fibre - maximum cable run 60km | Numeric | ENA (Ongoing) |  | 13
Siemens | 7SL86 (Siprotec 5) | Product Code: P1C917438 |  | V8.83 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS, SC | 60-250VDC | Up to 4 circuits | For use with multi-ended line differential or distance protection (maximum 4 circuits) For use with multi-mode fibre - maximum cable run 2km | Numeric | ENA (Ongoing) |  | 13
Siemens | 7SL86 (Siprotec 5) | Product Code: P1C917414 |  | V8.83 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS, SC | 60-250VDC | Up to 4 circuits | For use with multi-ended line differential or distance protection (maximum 4 circuits) For use with single-mode fibre - maximum cable run 60km | Numeric | ENA (Ongoing) |  | 13
Siemens | 7SD86 (Siprotec 5) | Product Code: P1B395021 |  | V8.83 | CD, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS, SC | 60-250VDC | Does not include Distance Protection Maximum 2 circuits - end to end | For use with end to end line differential (maximum 2 circuits / end-to-end) For use with multi-mode fibre - maximum cable run 2km | Numeric | ENA (Ongoing) |  | 13
Siemens | 7SD86 (Siprotec 5) | Product Code: P1B395014 |  | V8.83 | CD, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS, SC | 60-250VDC | Does not include Distance Protection Maximum 2 circuits - end to end | For use with end to end line differential (maximum 2 circuits / end-to-end) For use with single-mode fibre - maximum cable run 60km | Numeric | ENA (Ongoing) |  | 13
Siemens | 7SD86 (Siprotec 5) | Product Code: P1B394970 |  | V8.83 | CD, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS, SC | 60-250VDC | Does not include Distance Protection Up to 4 circuits | For use with multi-ended line differential (maximum 4 circuits) For use with multi-mode fibre - maximum cable run 2km | Numeric | ENA (Ongoing) |  | 13
Siemens | 7SD86 (Siprotec 5) | Product Code: P1B394987 |  | V8.83 | CD, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS, SC | 60-250VDC | Does not include Distance Protection Up to 4 circuits | For use with multi-ended line differential (maximum 4 circuits) For use with single-mode fibre - maximum cable run 60km | Numeric | ENA (Ongoing) |  | 13
Siemens | GPS/DCF77 Time Synchronising Receiver | 7XV5664-1AB00 |  |  |  |  | For use with Siemens Siprotec 5 Protection Relays | To be used when GPS Time Synchronisation is required | N/A |  |  | 13
Siemens | SYNC-Transceiver | 7XV5654-0BA00 |  |  |  |  | For use with Siemens Siprotec 5 Protection Relays | To be used when GPS Time Synchronisation is required | N/A |  |  | 13
Siemens | 7SR1101-1 (Argus C) | 7SR1101-1MA12-1CA0 | /FF | 2436H80003R4k-3d | E, EIT, SBEF | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | Single element relay without SEF | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1101-1 (Argus C) | 7SR1101-1NA12-1CA0 | /FF | 2436H80003R4k-3d | E, EIT, SBEF | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | Single element relay without SEF | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1101-3 (Argus C) | 7SR1101-3MA12-1CA0 | /FF | 2436H80003R4k-3d | SEF | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | Single element SEF relay. | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1101-3 (Argus C) | 7SR1101-3NA12-1CA0 | /FF | 2436H80003R4k-3d | SEF | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | Single element SEF relay. | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1103-1 (Argus C) | 7SR1103-1MA12-2CA0 | /FF | 2436H80003R4k-3d | 3OC, 3HOC, 3OCIT, E, EIT, BBCK, TCS | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay without SEF, without A/R | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1103-1 (Argus C) | 7SR1103-1NA12-2CA0 | /FF | 2436H80003R4k-3d | 3OC, 3HOC, 3OCIT, E, EIT, BBCK, TCS | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay without SEF, without A/R | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1103-3 (Argus C) | 7SR1103-3MA12-2CA0 | /FF | 2436H80003R4k-3d | 3OC, 3HOC, 3OCIT, SEF, E, EIT, BBCK, TCS | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay with SEF, without A/R | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1103-3 (Argus C) | 7SR1103-3NA12-2CA0 | /FF | 2436H80003R4k-3d | 3OC, 3HOC, 3OCIT, SEF, E, EIT, BBCK, TCS | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay with SEF, without A/R | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1204-2 (Argus C) | 7SR1204-2MA12-1CA0 | /FF | 2436H80004R4k-3d | DEIT, NVD, 3OV | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Where NVD is derived from capacitive cones or bushings, a Siemens 7XG21 (Capacitor Cone Adaptor Unit) shall be fitted. | Single element directional earth fault / NVD relay. Relay may be used in conjunction with a conventional VT or with appropriate capacitor bushings to provide NVD protection. Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1204-2 (Argus C) | 7SR1204-2NA12-1CA0 | /FF | 2436H80004R4k-3d | DEIT, NVD, 3OV | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Where NVD is derived from capacitive cones or bushings, a Siemens 7XG21 (Capacitor Cone Adaptor Unit) shall be fitted. | Single element directional earth fault / NVD relay. Relay may be used in conjunction with a conventional VT or with appropriate capacitor bushings to provide NVD protection. Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1206-2 (Argus C) | 7SR1206-2M12-2CA0 | /FF | 2436H80004R4k-3d | 3DOCIT, DEIT, NVD, 3OV, BBCK, TCS | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Where NVD is derived from capacitive cones or bushings, a Siemens 7XG21 (Capacitor Cone Adaptor Unit) shall be fitted. | 4 element directional relay without SEF, without A/R Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1206-2 (Argus C) | 7SR1206-2NA12-2CA0 | /FF | 2436H80004R4k-3d | 3DOCIT, DEIT, NVD, 3OV, BBCK, TCS | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Where NVD is derived from capacitive cones or bushings, a Siemens 7XG21 (Capacitor Cone Adaptor Unit) shall be fitted | 4 element directional relay without SEF, without A/R Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1587 (Argus) | 7SR1587-5NA12-1CA0 | /CC | 2436H80011 R4e-2a | 3UV, 3OV, 3OF, 3UF, NVD, LFDD |  | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Where NVD is derived from capacitive cones or bushings, a Siemens 7XG21 (Capacitor Cone Adaptor Unit) shall be fitted. | Voltage & Frequency Protection Relay Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 196 Issue 02 | 10 or earlier
Siemens | 7SR2103-1 (Argus M) | 7SR2103-1MA12-0DA0 | /DD | 2435H85008 R8e-8a | 3OC, 3HOC, 3OCIT, E, EIT, SBEF, SEF, AR, BBCK, TCS | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay including SEF and A/R Last Order Date September 30th 2025 | Numeric | ENA | NoC 151 | 10 or earlier
Siemens | 7SR2103-1 (Argus M) | 7SR2103-1NA12-0DA0 | /DD | 2435H85008 R8e-8a | 3OC, 3HOC, 3OCIT, E, EIT, SBEF, SEF, AR, BBCK, TCS | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay including SEF and A/R Last Order Date September 30th 2025 | Numeric | ENA | NoC 151 | 10 or earlier
Siemens | 7SR2203-2 (Argus M) | 7SR2203-2NA12-0DA0 | /DD | 2435H85009 R8e-8a | 3OC, 3OCIT, 3DOCIT, 3DOCIT(LB), 3DOCIT(VC), E, EIT, DEIT, AR, TCS, BBCK, AI | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element directional relay including load-blinding and voltage-controlled directional overcurrent features. Last Order Date September 30th 2025 | Numeric | ENA | NoC 151 | 10 or earlier
Siemens | 7SR23 (DAD) | 7SR2302-1NA12-0CA0 | /CC | 2435H85014 R8e-1c | 3BBOC | 110Vd.c. | Suitable panel-mounted metrosils and series stabilising resistors shall be provided. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | The relay has 9 binary inputs, 8 binary outputs, and 8 LEDs. | Numeric | ENA | NoC 184 Issue 3 | 10 or earlier
Siemens | 7SR23 (DAD) | 7SR2303-1NA12-0CA0 | /CC | 2435H85014 R8e-1c | 3BBOC | 110Vd.c. | Suitable panel-mounted metrosils and stabilising resistors shall be provided. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | The relay has 19 binary inputs, 16 binary outputs, and 16 LEDs. | Numeric | ENA | NoC 184 Issue 3 | 10 or earlier
Siemens | 7SR242 (Duobias) | 7SR2423-2NA12-0BA0 | /DD | 2662H85001 RB8b-7c | BD, REF |  | For use with 2 winding transformers. A suitable panel-mounted metrosil and series stabilising resistor shall be provided for each REF zone. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | Last Order Date September 30th 2025 | Numeric | ENA | NoC 150 | 10 or earlier
Siemens | 7XG22 (RMLG02) |  |  |  | RTB |  |  | Intercompatible with GE Vernova MMLG02 | N/A |  |  | 10 or earlier
Siemens | 7XG21 Capacitor Cone Adaptor Units | 7XG2100-1AA00-0AA0 |  |  | NVD |  | Siemens 7XG21 Capacitor Cone Adaptor Units are now obsolete and no longer available to purchase from Siemens. | Last Order Date December 2023 NGED have secured a number of Capacitor Cone Adaptor Units that are located at central stores in Huthwaite - Item Number 63562 Units to be free-issued to sub-suppliers on request.
Arteche | RF-4SYDI | RF-4SYDI 110VDC OP00011 |  |  | AI | 110Vd.c. | To be ordered with socket for flush mounting - Order Code: F-EMP TR Short OPxxx1x | 4 x C/O Contacts Flush Mounted, Self-reset Relay, Hand Reset flags. | Electromechanical | ENA | NoC 210 Issue 02 | 13
Arteche | RJ-8SYDI | RJ-8SYDI 110VDC OP00011 |  |  | AI | 110Vd.c. | To be ordered with socket for flush mounting - Order Code: J-EMP TR Short OPxxx1x | 8 x C/O Contacts Flush Mounted, Self-reset Relay, Hand Reset flags. | Electromechanical | ENA | NoC 210 Issue 0 | 13
Arteche | RF-4R | RF-4R HB 110VDC OP01010 |  |  | TS, BBCKA | 110Vd.c. | To be ordered with socket for flush mounting - Order Code: F-EMP TR Short OPxxx1x | 4 x C/O Contacts Flush Mounted, Instantaneous Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 210 Issue 02 | 13
Arteche | RJ-8R | RJ-8R HB 110VDC OP01010 |  |  | TS, BBCKA | 110Vd.c. | To be ordered with socket for flush mounting - Order Code: J-EMP TR Short OPxxx1x | 8 x C/O Contacts Flush Mounted, Instantaneous Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 210 Issue 02 | 13
Arteche | BF-4RP | BF-4RP HB IR 110VDC |  |  | TH TEF | 110Vd.c. | To be ordered with socket for flush mounting - Order Code: F-EMP TR BF-4RP | 4 x C/O Contacts Flush Mounted, Hand or Electrical Reset Relay, Following Flag. | Electromechanical | ENA | NoC 211 Issue 02 | 13
Arteche | BJ-8RP | BJ-8RP HB IR 110VDC |  |  | TH TEF | 110Vd.c. | To be ordered with socket for flush mounting - Order Code: J-EMP TR BF-8RP | 8 x C/O Contacts Flush Mounted, Hand or Electrical Reset Relay, Following Flag. | Electromechanical | ENA | NoC 211 Issue 02 | 13
Arteche | TDJ-8 | TDJ-8 110VDC OP000 |  |  | TDS | 110Vd.c. | To be ordered with socket for flush mounting - Order Code: J-EMP TR OP | 8 x C/O Contacts Flush Mounted, Configurable Time Delay Self Reset Relay. | Electromechanical | ENA | NoC 209 Issue 01 | 13

## Schedule 2 (Function Key)
Function Code | Description | Notes
3BBOC | 3 phase busbar overcurrent | High impedance
3DOCIT | 3 phase directional IDMT overcurrent
3DOCIT(LB) | 3 phase directional IDMT overcurrent with load blinding
3DOCIT(VC) | 3 phase voltage controlled directional IDMT overcurrent
3HOC | 3 phase high set overcurrent
3OC | 3 phase instantaneous or definite time overcurrent
3OCIT | 3 phase IDMT overcurrent
3OV | 3 phase over voltage
3UV | 3 phase under voltage
3OF | 3 phase over Frequency
3UF | 3 phase under Frequency
AI | Alarm indication relay | Used for buchholz alarm, winding temperature alarm, SF6 pressure low alarm etc.
AR | Auto-reclose
AR(DBLLC) | Auto-reclose with dead bus, live line check
AR(LLC) | Auto-reclose with live line check
AR(SC) | Auto-reclose with synchronising check
ASC | ASC control relay
BA | Battery Alarm
BBCK | Busbar protection check relay
BBCKA | Busbar protection check auxiliary relay
BD | Biased differential
BEF | Balanced Earth Fault | High impedance
CD | Current Differential | Feeder differential protection using Category 1 communications links
CTS | CT supervision
DEIT | Directional IDMT earth fault
E | Instantaneous or definite time earth fault
EIT | IDMT earth fault
IT | Intertrip send/receive system
LFDD | Low frequency demand disconnection. | In addition to WPD requirements, ENA Technical Specifications and British Standards, LFDD relays must comply with CC.A.5 of the Grid Code.
NVD | Neutral voltage displacement
PW | Pilot wire protection | Feeder differential protection using WPD-owned pilot cables
PWI | Pilot wire isolation
PWS | Pilot wire supervision
REF | Restricted Earth Fault | High impedance
RTB | Relay test block
S | Signalling relay (for distance protection schemes)
SBEF | Standby earth fault
SC | Synchronising check
SEF | Sensitive earth fault
SIR | Signalling scheme interposing relay
TCC | Tap Change Control
TCM | Tap Change Monitor
TCS | Trip circuit supervision
TD | Time delay relay
TDS | Trip relay with time-delayed self-reset contacts, hand reset flag
TE | Trip relay with electrically reset contacts, hand reset flag
TEF | Trip relay with electrically reset contacts, following flag
TH | Trip relay with hand reset contacts and flag
TI | Trip indication relay | Used in series with trip coil or trip relay coil, e.g. buchholz trip, winding temperature trip etc.
TRS | Trip relay supervision
TS | Trip relay with instantaneous self-reset contacts, hand reset flag
TSS | Trip Supply Supervision
VR | Voltage regulation relay
VTS | VT supervision
Z | Distance protection