## Heat Pump Determination
Power Quality - Harmonics
| Power of Device | 22.08 | (kVA)
* | Manufacturer states Heat Pump System meets technical requirements of EN/IEC 61000-3-2? | Yes | Proceed to Flicker questions
* | Manufacturer states Heat Pump System complying with EN/IEC 61000-3-12? | Yes | Proceed to Flicker questions
* | Manufacturer states Heat Pump System complies with EN/IEC 61000-3-12 provided that the short-circuit power Ssc is greater than or equal to xx. | Yes | Enter fault level value provided by manufacturer into Cell D11
| 3-phase supply short circuit level, Ssc, required to allow connection under EN 61000-3-12 | 0 | (kVA)
| Rsce | 0 | Value should be >15 - Ask for revised figures
Power Quality - Flicker
* | Manufacturer states Heat Pump System meets technical requirements of EN/IEC 61000-3-3? | Yes | Proceed to Impedance Calculator
* | Manufacturer states Heat Pump System complying with EN/IEC 61000-3-11 provided that the source impedance is no more than Zmax? | Yes
| Z Max provided by manufacturer | 0.1 | Ω
Proceed to Impedance Calculator
* | Manufacturer states Heat Pump System complying with BS EN/IEC 61000-3-11 provided that service current capacity ≥100A per phase? | Yes | Enter phase configuration and then proceed to Impedance Calculator
| Configuration of Heat Pump | Single phase
Please note service cable does not require 100A capacity

## Impedance Calculator
Impedance calculator for EV's & HP's rated < 32A per phase
Rating of single phase EV charger (kVA) | Quantity(1) | Minimum Short circuit power (MVA)(2)
7.36 | 0 | 0.3312
Rating of single phase heat pump (kVA)(4) | Quantity(1) | Maximum Impedance at PCC (Ohms)(2)
22.08 | 0 | Single Phase
#DIV/0!
Rating of three phase EV charger (kVA) | Quantity
Three Phase
22.08 | 1 | 0.48309
Rating of three phase heat pump (kVA)(4) | Quantity | Combined(3)
0.48309
22.08 | 0
Maximum Impedance at the cut out (Ohms)(5)
0.47
Notes;
Minimum short circuit ratio factor | Sum
15 | 1
33
Summation exponent
2
EV Short circuit power ( single)
0
HP Short circuit power ( single)
0
EV & HP Short circuit power ( single)
0
EV Short circuit power (three ph)
331200
HP Short circuit power (three ph)
0
EV & HP Short circuit power (three ph)
331200
Combined (watts)
331200
(1) - Maximum single phase unbalanced load (e.g. device with 4 x outputs, 2 x car chargers on L1, 1 x car charger on L2 & L3 - insert value for L1 only (quantity of 2)
(2) - At the point of common coupling (PCC)
(3) - Value provided is Phase Impedance / Line Impedance (equivalent to three phase impedance)
(4) - Rating of compressor motor only (do not include back up or boost heating elements)
(5) - The Flicker standard is assessed at the cutout and already includes diversity for multiple connections
(6) - Calculation is based on ENA EREC G5/5 Stage 1B-1 assessment using Fsce of 15 for EV and 33 for HP and summation exponent of 2.

## Sheet1 (hidden)
| Harmonics | Fault level |  | Flicker | from other sheet
61000-3-2 | 1 |  | 61000-3-3 | 1
61000-3-12 | 728640 |  | Zmax | 1 | 0.1
Ssc | 0 |  | >100A | 1 | 0.3536
required F/L | 112553 |  |  | 0.47