## Battery Calculator
BATTERY CALCULATOR FOR EE SPEC 104/1
Battery Nominal Voltage | 48
Battery Voltage At End Of Duty Cycle | 44.4
Standby Period (Hours) | 72
Design Margin | 1.1
Ageing Factor | 1.25
Temperature Correction Factor | 1.09
Standing Load (Watts) | 48
|  |  |  | Accurate 15degC | Accurate 5degC
Battery Capacity Required (Ah) | 108.2361 |  |  | 101.7409 | 108.6424
Monobloc Type | Number of Parallel Strings | Actual Battery Capacity (Ah)
Enersys Powersafe EON SBS B14F | 2 | 123.4 | BATTERY CAPACITY IS ADEQUATE
Minimum Charger Rating (A) | 13.5292

## Kt_Data_Tables (hidden)
1
Kt: 1.85V/Cell @ 20degC |  | 1s | 5s | 30s | 60s | 3m | 5m | 10m | 15m | 20m | 30m | 40m | 50m | 1h | 1.5h | 3h | 5h | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
Time | 0 | 0.00032777 | 0.0014389 | 0.0083833 | 0.016717 | 0.05005 | 0.083383 | 0.16672 | 0.25005 | 0.33338 | 0.50005 | 0.66672 | 0.83338 | 1 | 1.5 | 3 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200
Enersys Powersafe EON SBS 100 | 0.3962 | 0.3962 | 0.3962 | 0.3962 | 0.3962 | 0.3962 | 0.3962 | 0.5102 | 0.61958 | 0.77232 | 0.92507 | 1.1127 | 1.3004 | 1.4881 | 2.5171 | 3.5461 | 5.4945 | 5.9524 | 6.4103 | 6.8548 | 7.2993 | 7.8163 | 8.3333 | 8.7963 | 9.2593 | 9.7006 | 10.142 | 10.5801 | 11.0181 | 11.4562 | 11.8943 | 12.3324 | 12.7705 | 13.2085 | 13.6466 | 14.0847 | 14.5228 | 14.9609 | 15.399 | 15.837 | 16.2751 | 16.7132 | 17.1513 | 17.5894 | 18.0274 | 18.4655 | 18.9036 | 19.3417 | 19.7798 | 20.2178 | 20.6559 | 21.094 | 21.5321 | 21.9702 | 22.4082 | 22.8463 | 23.2844 | 23.7225 | 24.1606 | 24.5986 | 25.0367 | 25.4748 | 25.9129 | 26.351 | 26.789 | 27.2271 | 27.6652 | 28.1033 | 28.5414 | 28.9794 | 29.4175 | 29.8556 | 30.2937 | 30.7318 | 31.1698 | 31.6079 | 32.046 | 32.4841 | 32.9222 | 33.3602 | 33.7983 | 34.2364 | 34.6745 | 35.1126 | 35.5506 | 35.9887 | 36.4268 | 36.8649 | 37.303 | 37.741 | 38.1791 | 38.6172 | 39.0553 | 39.4934 | 39.9314 | 40.3695 | 40.8076 | 41.2457 | 41.6838 | 42.1218 | 42.5599 | 42.998 | 43.4361 | 43.8742 | 44.3122 | 44.7503 | 45.1884 | 45.6265 | 46.0646 | 46.5026 | 46.9407 | 47.3788 | 47.8169 | 48.255 | 48.693 | 49.1311 | 49.5692 | 50.0073 | 50.4454 | 50.8834 | 51.3215 | 51.7596 | 52.1977 | 52.6358 | 53.0738 | 53.5119 | 53.95 | 54.3881 | 54.8262 | 55.2642 | 55.7023 | 56.1404 | 56.5785 | 57.0166 | 57.4546 | 57.8927 | 58.3308 | 58.7689 | 59.207 | 59.645 | 60.0831 | 60.5212 | 60.9593 | 61.3974 | 61.8355 | 62.2735 | 62.7116 | 63.1497 | 63.5878 | 64.0259 | 64.4639 | 64.902 | 65.3401 | 65.7782 | 66.2163 | 66.6543 | 67.0924 | 67.5305 | 67.9686 | 68.4067 | 68.8447 | 69.2828 | 69.7209 | 70.159 | 70.5971 | 71.0351 | 71.4732 | 71.9113 | 72.3494 | 72.7875 | 73.2255 | 73.6636 | 74.1017 | 74.5398 | 74.9779 | 75.4159 | 75.854 | 76.2921 | 76.7302 | 77.1683 | 77.6063 | 78.0444 | 78.4825 | 78.9206 | 79.3587 | 79.7967 | 80.2348 | 80.6729 | 81.111 | 81.5491 | 81.9871 | 82.4252 | 82.8633 | 83.3014 | 83.7395 | 84.1775 | 84.6156 | 85.0537 | 85.4918
Enersys Powersafe EON SBS 100F | 0.3962 | 0.3962 | 0.3962 | 0.3962 | 0.3962 | 0.3962 | 0.3962 | 0.5102 | 0.61958 | 0.77232 | 0.92507 | 1.1127 | 1.3004 | 1.4881 | 2.5171 | 3.5461 | 5.4945 | 5.9524 | 6.4103 | 6.8548 | 7.2993 | 7.8163 | 8.3333 | 8.7963 | 9.2593 | 9.7006 | 10.142 | 10.5801 | 11.0181 | 11.4562 | 11.8943 | 12.3324 | 12.7705 | 13.2085 | 13.6466 | 14.0847 | 14.5228 | 14.9609 | 15.399 | 15.837 | 16.2751 | 16.7132 | 17.1513 | 17.5894 | 18.0274 | 18.4655 | 18.9036 | 19.3417 | 19.7798 | 20.2178 | 20.6559 | 21.094 | 21.5321 | 21.9702 | 22.4082 | 22.8463 | 23.2844 | 23.7225 | 24.1606 | 24.5986 | 25.0367 | 25.4748 | 25.9129 | 26.351 | 26.789 | 27.2271 | 27.6652 | 28.1033 | 28.5414 | 28.9794 | 29.4175 | 29.8556 | 30.2937 | 30.7318 | 31.1698 | 31.6079 | 32.046 | 32.4841 | 32.9222 | 33.3602 | 33.7983 | 34.2364 | 34.6745 | 35.1126 | 35.5506 | 35.9887 | 36.4268 | 36.8649 | 37.303 | 37.741 | 38.1791 | 38.6172 | 39.0553 | 39.4934 | 39.9314 | 40.3695 | 40.8076 | 41.2457 | 41.6838 | 42.1218 | 42.5599 | 42.998 | 43.4361 | 43.8742 | 44.3122 | 44.7503 | 45.1884 | 45.6265 | 46.0646 | 46.5026 | 46.9407 | 47.3788 | 47.8169 | 48.255 | 48.693 | 49.1311 | 49.5692 | 50.0073 | 50.4454 | 50.8834 | 51.3215 | 51.7596 | 52.1977 | 52.6358 | 53.0738 | 53.5119 | 53.95 | 54.3881 | 54.8262 | 55.2642 | 55.7023 | 56.1404 | 56.5785 | 57.0166 | 57.4546 | 57.8927 | 58.3308 | 58.7689 | 59.207 | 59.645 | 60.0831 | 60.5212 | 60.9593 | 61.3974 | 61.8355 | 62.2735 | 62.7116 | 63.1497 | 63.5878 | 64.0259 | 64.4639 | 64.902 | 65.3401 | 65.7782 | 66.2163 | 66.6543 | 67.0924 | 67.5305 | 67.9686 | 68.4067 | 68.8447 | 69.2828 | 69.7209 | 70.159 | 70.5971 | 71.0351 | 71.4732 | 71.9113 | 72.3494 | 72.7875 | 73.2255 | 73.6636 | 74.1017 | 74.5398 | 74.9779 | 75.4159 | 75.854 | 76.2921 | 76.7302 | 77.1683 | 77.6063 | 78.0444 | 78.4825 | 78.9206 | 79.3587 | 79.7967 | 80.2348 | 80.6729 | 81.111 | 81.5491 | 81.9871 | 82.4252 | 82.8633 | 83.3014 | 83.7395 | 84.1775 | 84.6156 | 85.0537 | 85.4918
Enersys Powersafe EON SBS 170F | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.67114 | 0.82212 | 0.9731 | 1.1606 | 1.3482 | 1.5357 | 2.5764 | 3.617 | 5.6106 | 6.0999 | 6.5891 | 7.0556 | 7.5221 | 8.0111 | 8.5 | 8.9722 | 9.4444 | 9.9051 | 10.3659 | 10.7983 | 11.2308 | 11.6633 | 12.0958 | 12.5283 | 12.9608 | 13.3933 | 13.8258 | 14.2583 | 14.6908 | 15.1232 | 15.5557 | 15.9882 | 16.4207 | 16.8532 | 17.2857 | 17.7182 | 18.1507 | 18.5832 | 19.0157 | 19.4482 | 19.8806 | 20.3131 | 20.7456 | 21.1781 | 21.6106 | 22.0431 | 22.4756 | 22.9081 | 23.3406 | 23.7731 | 24.2055 | 24.638 | 25.0705 | 25.503 | 25.9355 | 26.368 | 26.8005 | 27.233 | 27.6655 | 28.098 | 28.5304 | 28.9629 | 29.3954 | 29.8279 | 30.2604 | 30.6929 | 31.1254 | 31.5579 | 31.9904 | 32.4229 | 32.8554 | 33.2878 | 33.7203 | 34.1528 | 34.5853 | 35.0178 | 35.4503 | 35.8828 | 36.3153 | 36.7478 | 37.1803 | 37.6127 | 38.0452 | 38.4777 | 38.9102 | 39.3427 | 39.7752 | 40.2077 | 40.6402 | 41.0727 | 41.5052 | 41.9376 | 42.3701 | 42.8026 | 43.2351 | 43.6676 | 44.1001 | 44.5326 | 44.9651 | 45.3976 | 45.8301 | 46.2625 | 46.695 | 47.1275 | 47.56 | 47.9925 | 48.425 | 48.8575 | 49.29 | 49.7225 | 50.155 | 50.5875 | 51.0199 | 51.4524 | 51.8849 | 52.3174 | 52.7499 | 53.1824 | 53.6149 | 54.0474 | 54.4799 | 54.9124 | 55.3448 | 55.7773 | 56.2098 | 56.6423 | 57.0748 | 57.5073 | 57.9398 | 58.3723 | 58.8048 | 59.2373 | 59.6697 | 60.1022 | 60.5347 | 60.9672 | 61.3997 | 61.8322 | 62.2647 | 62.6972 | 63.1297 | 63.5622 | 63.9947 | 64.4271 | 64.8596 | 65.2921 | 65.7246 | 66.1571 | 66.5896 | 67.0221 | 67.4546 | 67.8871 | 68.3196 | 68.752 | 69.1845 | 69.617 | 70.0495 | 70.482 | 70.9145 | 71.347 | 71.7795 | 72.212 | 72.6445 | 73.0769 | 73.5094 | 73.9419 | 74.3744 | 74.8069 | 75.2394 | 75.6719 | 76.1044 | 76.5369 | 76.9694 | 77.4019 | 77.8343 | 78.2668 | 78.6993 | 79.1318 | 79.5643 | 79.9968 | 80.4293 | 80.8618 | 81.2943 | 81.7268 | 82.1592 | 82.5917 | 83.0242 | 83.4567 | 83.8892 | 84.3217 | 84.7542
Enersys Powersafe EON SBS 190F | 0.55669 | 0.55669 | 0.55669 | 0.55669 | 0.55669 | 0.55669 | 0.55669 | 0.55669 | 0.66225 | 0.81508 | 0.96791 | 1.1598 | 1.3516 | 1.5435 | 2.5778 | 3.6122 | 5.6047 | 6.0896 | 6.5744 | 7.0421 | 7.5099 | 7.9772 | 8.4444 | 8.902 | 9.3596 | 9.8149 | 10.2703 | 10.6974 | 11.1244 | 11.5515 | 11.9786 | 12.4057 | 12.8328 | 13.2598 | 13.6869 | 14.114 | 14.5411 | 14.9682 | 15.3952 | 15.8223 | 16.2494 | 16.6765 | 17.1036 | 17.5306 | 17.9577 | 18.3848 | 18.8119 | 19.239 | 19.666 | 20.0931 | 20.5202 | 20.9473 | 21.3744 | 21.8014 | 22.2285 | 22.6556 | 23.0827 | 23.5098 | 23.9368 | 24.3639 | 24.791 | 25.2181 | 25.6452 | 26.0723 | 26.4993 | 26.9264 | 27.3535 | 27.7806 | 28.2077 | 28.6347 | 29.0618 | 29.4889 | 29.916 | 30.3431 | 30.7701 | 31.1972 | 31.6243 | 32.0514 | 32.4785 | 32.9055 | 33.3326 | 33.7597 | 34.1868 | 34.6139 | 35.0409 | 35.468 | 35.8951 | 36.3222 | 36.7493 | 37.1763 | 37.6034 | 38.0305 | 38.4576 | 38.8847 | 39.3117 | 39.7388 | 40.1659 | 40.593 | 41.0201 | 41.4472 | 41.8742 | 42.3013 | 42.7284 | 43.1555 | 43.5826 | 44.0096 | 44.4367 | 44.8638 | 45.2909 | 45.718 | 46.145 | 46.5721 | 46.9992 | 47.4263 | 47.8534 | 48.2804 | 48.7075 | 49.1346 | 49.5617 | 49.9888 | 50.4158 | 50.8429 | 51.27 | 51.6971 | 52.1242 | 52.5512 | 52.9783 | 53.4054 | 53.8325 | 54.2596 | 54.6866 | 55.1137 | 55.5408 | 55.9679 | 56.395 | 56.822 | 57.2491 | 57.6762 | 58.1033 | 58.5304 | 58.9575 | 59.3845 | 59.8116 | 60.2387 | 60.6658 | 61.0929 | 61.5199 | 61.947 | 62.3741 | 62.8012 | 63.2283 | 63.6553 | 64.0824 | 64.5095 | 64.9366 | 65.3637 | 65.7907 | 66.2178 | 66.6449 | 67.072 | 67.4991 | 67.9261 | 68.3532 | 68.7803 | 69.2074 | 69.6345 | 70.0615 | 70.4886 | 70.9157 | 71.3428 | 71.7699 | 72.1969 | 72.624 | 73.0511 | 73.4782 | 73.9053 | 74.3324 | 74.7594 | 75.1865 | 75.6136 | 76.0407 | 76.4678 | 76.8948 | 77.3219 | 77.749 | 78.1761 | 78.6032 | 79.0302 | 79.4573 | 79.8844 | 80.3115 | 80.7386 | 81.1656 | 81.5927 | 82.0198 | 82.4469 | 82.874 | 83.301 | 83.7281
Enersys Powersafe EON SBS 320 | 1.5173 | 1.5173 | 1.5173 | 1.5173 | 1.5173 | 1.5173 | 1.5173 | 1.5173 | 1.5173 | 1.6249 | 1.7325 | 1.8821 | 2.0317 | 2.1813 | 3.1134 | 4.0455 | 5.8716 | 6.3184 | 6.7653 | 7.2104 | 7.6555 | 8.0944 | 8.5333 | 8.9587 | 9.3842 | 9.8203 | 10.2564 | 10.7017 | 11.1469 | 11.5922 | 12.0375 | 12.4827 | 12.928 | 13.3733 | 13.8185 | 14.2638 | 14.709 | 15.1543 | 15.5996 | 16.0448 | 16.4901 | 16.9354 | 17.3806 | 17.8259 | 18.2712 | 18.7164 | 19.1617 | 19.6069 | 20.0522 | 20.4975 | 20.9427 | 21.388 | 21.8333 | 22.2785 | 22.7238 | 23.169 | 23.6143 | 24.0596 | 24.5048 | 24.9501 | 25.3954 | 25.8406 | 26.2859 | 26.7312 | 27.1764 | 27.6217 | 28.0669 | 28.5122 | 28.9575 | 29.4027 | 29.848 | 30.2933 | 30.7385 | 31.1838 | 31.629 | 32.0743 | 32.5196 | 32.9648 | 33.4101 | 33.8554 | 34.3006 | 34.7459 | 35.1912 | 35.6364 | 36.0817 | 36.5269 | 36.9722 | 37.4175 | 37.8627 | 38.308 | 38.7533 | 39.1985 | 39.6438 | 40.0891 | 40.5343 | 40.9796 | 41.4248 | 41.8701 | 42.3154 | 42.7606 | 43.2059 | 43.6512 | 44.0964 | 44.5417 | 44.9869 | 45.4322 | 45.8775 | 46.3227 | 46.768 | 47.2133 | 47.6585 | 48.1038 | 48.5491 | 48.9943 | 49.4396 | 49.8848 | 50.3301 | 50.7754 | 51.2206 | 51.6659 | 52.1112 | 52.5564 | 53.0017 | 53.447 | 53.8922 | 54.3375 | 54.7827 | 55.228 | 55.6733 | 56.1185 | 56.5638 | 57.0091 | 57.4543 | 57.8996 | 58.3448 | 58.7901 | 59.2354 | 59.6806 | 60.1259 | 60.5712 | 61.0164 | 61.4617 | 61.907 | 62.3522 | 62.7975 | 63.2427 | 63.688 | 64.1333 | 64.5785 | 65.0238 | 65.4691 | 65.9143 | 66.3596 | 66.8049 | 67.2501 | 67.6954 | 68.1406 | 68.5859 | 69.0312 | 69.4764 | 69.9217 | 70.367 | 70.8122 | 71.2575 | 71.7027 | 72.148 | 72.5933 | 73.0385 | 73.4838 | 73.9291 | 74.3743 | 74.8196 | 75.2649 | 75.7101 | 76.1554 | 76.6006 | 77.0459 | 77.4912 | 77.9364 | 78.3817 | 78.827 | 79.2722 | 79.7175 | 80.1628 | 80.608 | 81.0533 | 81.4985 | 81.9438 | 82.3891 | 82.8343 | 83.2796 | 83.7249 | 84.1701 | 84.6154 | 85.0606 | 85.5059 | 85.9512 | 86.3964 | 86.8417
Enersys Powersafe EON SBS 400 | 1.5175 | 1.5175 | 1.5175 | 1.5175 | 1.5175 | 1.5175 | 1.5175 | 1.5175 | 1.5175 | 1.6249 | 1.7324 | 1.8819 | 2.0315 | 2.181 | 3.1128 | 4.0445 | 5.8737 | 6.321 | 6.7682 | 7.2082 | 7.6482 | 8.0885 | 8.5288 | 8.9592 | 9.3897 | 9.8099 | 10.2302 | 10.6756 | 11.121 | 11.5665 | 12.0119 | 12.4573 | 12.9028 | 13.3482 | 13.7936 | 14.239 | 14.6845 | 15.1299 | 15.5753 | 16.0208 | 16.4662 | 16.9116 | 17.357 | 17.8025 | 18.2479 | 18.6933 | 19.1388 | 19.5842 | 20.0296 | 20.475 | 20.9205 | 21.3659 | 21.8113 | 22.2568 | 22.7022 | 23.1476 | 23.593 | 24.0385 | 24.4839 | 24.9293 | 25.3748 | 25.8202 | 26.2656 | 26.711 | 27.1565 | 27.6019 | 28.0473 | 28.4928 | 28.9382 | 29.3836 | 29.829 | 30.2745 | 30.7199 | 31.1653 | 31.6108 | 32.0562 | 32.5016 | 32.9471 | 33.3925 | 33.8379 | 34.2833 | 34.7288 | 35.1742 | 35.6196 | 36.0651 | 36.5105 | 36.9559 | 37.4013 | 37.8468 | 38.2922 | 38.7376 | 39.1831 | 39.6285 | 40.0739 | 40.5193 | 40.9648 | 41.4102 | 41.8556 | 42.3011 | 42.7465 | 43.1919 | 43.6373 | 44.0828 | 44.5282 | 44.9736 | 45.4191 | 45.8645 | 46.3099 | 46.7553 | 47.2008 | 47.6462 | 48.0916 | 48.5371 | 48.9825 | 49.4279 | 49.8733 | 50.3188 | 50.7642 | 51.2096 | 51.6551 | 52.1005 | 52.5459 | 52.9913 | 53.4368 | 53.8822 | 54.3276 | 54.7731 | 55.2185 | 55.6639 | 56.1094 | 56.5548 | 57.0002 | 57.4456 | 57.8911 | 58.3365 | 58.7819 | 59.2274 | 59.6728 | 60.1182 | 60.5636 | 61.0091 | 61.4545 | 61.8999 | 62.3454 | 62.7908 | 63.2362 | 63.6816 | 64.1271 | 64.5725 | 65.0179 | 65.4634 | 65.9088 | 66.3542 | 66.7996 | 67.2451 | 67.6905 | 68.1359 | 68.5814 | 69.0268 | 69.4722 | 69.9176 | 70.3631 | 70.8085 | 71.2539 | 71.6994 | 72.1448 | 72.5902 | 73.0356 | 73.4811 | 73.9265 | 74.3719 | 74.8174 | 75.2628 | 75.7082 | 76.1536 | 76.5991 | 77.0445 | 77.4899 | 77.9354 | 78.3808 | 78.8262 | 79.2717 | 79.7171 | 80.1625 | 80.6079 | 81.0534 | 81.4988 | 81.9442 | 82.3897 | 82.8351 | 83.2805 | 83.7259 | 84.1714 | 84.6168 | 85.0622 | 85.5077 | 85.9531 | 86.3985 | 86.8439
Enersys Powersafe EON SBS 410 | 0.49516 | 0.49516 | 0.49516 | 0.49516 | 0.49516 | 0.49516 | 0.49516 | 0.65756 | 0.818 | 1.0687 | 1.3194 | 1.4453 | 1.5712 | 1.6971 | 2.7316 | 3.7661 | 5.4461 | 6.2128 | 6.9795 | 7.4996 | 8.0196 | 8.0916 | 8.1637 | 9.0454 | 9.9272 | 10.038 | 10.1489 | 10.7178 | 11.2866 | 11.8555 | 12.4244 | 12.9932 | 13.5621 | 14.131 | 14.6999 | 15.2687 | 15.8376 | 16.4065 | 16.9753 | 17.5442 | 18.1131 | 18.682 | 19.2508 | 19.8197 | 20.3886 | 20.9574 | 21.5263 | 22.0952 | 22.6641 | 23.2329 | 23.8018 | 24.3707 | 24.9395 | 25.5084 | 26.0773 | 26.6462 | 27.215 | 27.7839 | 28.3528 | 28.9216 | 29.4905 | 30.0594 | 30.6283 | 31.1971 | 31.766 | 32.3349 | 32.9037 | 33.4726 | 34.0415 | 34.6104 | 35.1792 | 35.7481 | 36.317 | 36.8858 | 37.4547 | 38.0236 | 38.5925 | 39.1613 | 39.7302 | 40.2991 | 40.868 | 41.4368 | 42.0057 | 42.5746 | 43.1434 | 43.7123 | 44.2812 | 44.8501 | 45.4189 | 45.9878 | 46.5567 | 47.1255 | 47.6944 | 48.2633 | 48.8322 | 49.401 | 49.9699 | 50.5388 | 51.1076 | 51.6765 | 52.2454 | 52.8143 | 53.3831 | 53.952 | 54.5209 | 55.0897 | 55.6586 | 56.2275 | 56.7964 | 57.3652 | 57.9341 | 58.503 | 59.0718 | 59.6407 | 60.2096 | 60.7785 | 61.3473 | 61.9162 | 62.4851 | 63.0539 | 63.6228 | 64.1917 | 64.7606 | 65.3294 | 65.8983 | 66.4672 | 67.036 | 67.6049 | 68.1738 | 68.7427 | 69.3115 | 69.8804 | 70.4493 | 71.0181 | 71.587 | 72.1559 | 72.7248 | 73.2936 | 73.8625 | 74.4314 | 75.0002 | 75.5691 | 76.138 | 76.7069 | 77.2757 | 77.8446 | 78.4135 | 78.9823 | 79.5512 | 80.1201 | 80.689 | 81.2578 | 81.8267 | 82.3956 | 82.9645 | 83.5333 | 84.1022 | 84.6711 | 85.2399 | 85.8088 | 86.3777 | 86.9466 | 87.5154 | 88.0843 | 88.6532 | 89.222 | 89.7909 | 90.3598 | 90.9287 | 91.4975 | 92.0664 | 92.6353 | 93.2041 | 93.773 | 94.3419 | 94.9108 | 95.4796 | 96.0485 | 96.6174 | 97.1862 | 97.7551 | 98.324 | 98.8929 | 99.4617 | 100.0306 | 100.5995 | 101.1683 | 101.7372 | 102.3061 | 102.875 | 103.4438 | 104.0127 | 104.5816 | 105.1504 | 105.7193 | 106.2882 | 106.8571 | 107.4259 | 107.9948
Enersys Powersafe EON SBS 480 | 1.5171 | 1.5171 | 1.5171 | 1.5171 | 1.5171 | 1.5171 | 1.5171 | 1.5175 | 1.5175 | 1.6249 | 1.7322 | 1.8818 | 2.0313 | 2.1808 | 3.114 | 4.0472 | 5.868 | 6.319 | 6.7701 | 7.2067 | 7.6433 | 8.0845 | 8.5258 | 8.9504 | 9.375 | 9.8048 | 10.2345 | 10.679 | 11.1234 | 11.5679 | 12.0123 | 12.4568 | 12.9012 | 13.3457 | 13.7901 | 14.2346 | 14.679 | 15.1235 | 15.5679 | 16.0124 | 16.4568 | 16.9013 | 17.3457 | 17.7902 | 18.2346 | 18.6791 | 19.1235 | 19.568 | 20.0124 | 20.4569 | 20.9013 | 21.3457 | 21.7902 | 22.2346 | 22.6791 | 23.1235 | 23.568 | 24.0124 | 24.4569 | 24.9013 | 25.3458 | 25.7902 | 26.2347 | 26.6791 | 27.1236 | 27.568 | 28.0125 | 28.4569 | 28.9014 | 29.3458 | 29.7903 | 30.2347 | 30.6792 | 31.1236 | 31.5681 | 32.0125 | 32.457 | 32.9014 | 33.3458 | 33.7903 | 34.2347 | 34.6792 | 35.1236 | 35.5681 | 36.0125 | 36.457 | 36.9014 | 37.3459 | 37.7903 | 38.2348 | 38.6792 | 39.1237 | 39.5681 | 40.0126 | 40.457 | 40.9015 | 41.3459 | 41.7904 | 42.2348 | 42.6793 | 43.1237 | 43.5682 | 44.0126 | 44.4571 | 44.9015 | 45.346 | 45.7904 | 46.2348 | 46.6793 | 47.1237 | 47.5682 | 48.0126 | 48.4571 | 48.9015 | 49.346 | 49.7904 | 50.2349 | 50.6793 | 51.1238 | 51.5682 | 52.0127 | 52.4571 | 52.9016 | 53.346 | 53.7905 | 54.2349 | 54.6794 | 55.1238 | 55.5683 | 56.0127 | 56.4572 | 56.9016 | 57.3461 | 57.7905 | 58.2349 | 58.6794 | 59.1238 | 59.5683 | 60.0127 | 60.4572 | 60.9016 | 61.3461 | 61.7905 | 62.235 | 62.6794 | 63.1239 | 63.5683 | 64.0128 | 64.4572 | 64.9017 | 65.3461 | 65.7906 | 66.235 | 66.6795 | 67.1239 | 67.5684 | 68.0128 | 68.4573 | 68.9017 | 69.3462 | 69.7906 | 70.2351 | 70.6795 | 71.1239 | 71.5684 | 72.0128 | 72.4573 | 72.9017 | 73.3462 | 73.7906 | 74.2351 | 74.6795 | 75.124 | 75.5684 | 76.0129 | 76.4573 | 76.9018 | 77.3462 | 77.7907 | 78.2351 | 78.6796 | 79.124 | 79.5685 | 80.0129 | 80.4574 | 80.9018 | 81.3463 | 81.7907 | 82.2352 | 82.6796 | 83.124 | 83.5685 | 84.0129 | 84.4574 | 84.9018 | 85.3463 | 85.7907 | 86.2352 | 86.6796
Enersys Powersafe EON SBS 580 | 1.5171 | 1.5171 | 1.5171 | 1.5171 | 1.5171 | 1.5171 | 1.5171 | 1.5175 | 1.5175 | 1.6247 | 1.7319 | 1.8817 | 2.0315 | 2.1813 | 3.113 | 4.0446 | 5.8704 | 6.3191 | 6.7678 | 7.2098 | 7.6517 | 8.0843 | 8.5169 | 8.951 | 9.3851 | 9.8072 | 10.2293 | 10.6749 | 11.1205 | 11.5662 | 12.0118 | 12.4574 | 12.9031 | 13.3487 | 13.7943 | 14.24 | 14.6856 | 15.1312 | 15.5769 | 16.0225 | 16.4681 | 16.9138 | 17.3594 | 17.805 | 18.2507 | 18.6963 | 19.1419 | 19.5875 | 20.0332 | 20.4788 | 20.9244 | 21.3701 | 21.8157 | 22.2613 | 22.707 | 23.1526 | 23.5982 | 24.0439 | 24.4895 | 24.9351 | 25.3808 | 25.8264 | 26.272 | 26.7177 | 27.1633 | 27.6089 | 28.0546 | 28.5002 | 28.9458 | 29.3914 | 29.8371 | 30.2827 | 30.7283 | 31.174 | 31.6196 | 32.0652 | 32.5109 | 32.9565 | 33.4021 | 33.8478 | 34.2934 | 34.739 | 35.1847 | 35.6303 | 36.0759 | 36.5216 | 36.9672 | 37.4128 | 37.8585 | 38.3041 | 38.7497 | 39.1953 | 39.641 | 40.0866 | 40.5322 | 40.9779 | 41.4235 | 41.8691 | 42.3148 | 42.7604 | 43.206 | 43.6517 | 44.0973 | 44.5429 | 44.9886 | 45.4342 | 45.8798 | 46.3255 | 46.7711 | 47.2167 | 47.6624 | 48.108 | 48.5536 | 48.9992 | 49.4449 | 49.8905 | 50.3361 | 50.7818 | 51.2274 | 51.673 | 52.1187 | 52.5643 | 53.0099 | 53.4556 | 53.9012 | 54.3468 | 54.7925 | 55.2381 | 55.6837 | 56.1294 | 56.575 | 57.0206 | 57.4663 | 57.9119 | 58.3575 | 58.8032 | 59.2488 | 59.6944 | 60.14 | 60.5857 | 61.0313 | 61.4769 | 61.9226 | 62.3682 | 62.8138 | 63.2595 | 63.7051 | 64.1507 | 64.5964 | 65.042 | 65.4876 | 65.9333 | 66.3789 | 66.8245 | 67.2702 | 67.7158 | 68.1614 | 68.6071 | 69.0527 | 69.4983 | 69.9439 | 70.3896 | 70.8352 | 71.2808 | 71.7265 | 72.1721 | 72.6177 | 73.0634 | 73.509 | 73.9546 | 74.4003 | 74.8459 | 75.2915 | 75.7372 | 76.1828 | 76.6284 | 77.0741 | 77.5197 | 77.9653 | 78.411 | 78.8566 | 79.3022 | 79.7478 | 80.1935 | 80.6391 | 81.0847 | 81.5304 | 81.976 | 82.4216 | 82.8673 | 83.3129 | 83.7585 | 84.2042 | 84.6498 | 85.0954 | 85.5411 | 85.9867 | 86.4323 | 86.878
Enersys Powersafe EON SBS 680 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5175 | 1.6248 | 1.732 | 1.8817 | 2.0313 | 2.1809 | 3.113 | 4.0452 | 5.8671 | 6.3166 | 6.7662 | 7.2076 | 7.649 | 8.0852 | 8.5213 | 8.9503 | 9.3793 | 9.8024 | 10.2256 | 10.6693 | 11.1131 | 11.5569 | 12.0007 | 12.4445 | 12.8882 | 13.332 | 13.7758 | 14.2196 | 14.6633 | 15.1071 | 15.5509 | 15.9947 | 16.4385 | 16.8822 | 17.326 | 17.7698 | 18.2136 | 18.6573 | 19.1011 | 19.5449 | 19.9887 | 20.4325 | 20.8762 | 21.32 | 21.7638 | 22.2076 | 22.6513 | 23.0951 | 23.5389 | 23.9827 | 24.4265 | 24.8702 | 25.314 | 25.7578 | 26.2016 | 26.6453 | 27.0891 | 27.5329 | 27.9767 | 28.4205 | 28.8642 | 29.308 | 29.7518 | 30.1956 | 30.6394 | 31.0831 | 31.5269 | 31.9707 | 32.4145 | 32.8582 | 33.302 | 33.7458 | 34.1896 | 34.6334 | 35.0771 | 35.5209 | 35.9647 | 36.4085 | 36.8522 | 37.296 | 37.7398 | 38.1836 | 38.6274 | 39.0711 | 39.5149 | 39.9587 | 40.4025 | 40.8462 | 41.29 | 41.7338 | 42.1776 | 42.6214 | 43.0651 | 43.5089 | 43.9527 | 44.3965 | 44.8402 | 45.284 | 45.7278 | 46.1716 | 46.6154 | 47.0591 | 47.5029 | 47.9467 | 48.3905 | 48.8342 | 49.278 | 49.7218 | 50.1656 | 50.6094 | 51.0531 | 51.4969 | 51.9407 | 52.3845 | 52.8283 | 53.272 | 53.7158 | 54.1596 | 54.6034 | 55.0471 | 55.4909 | 55.9347 | 56.3785 | 56.8223 | 57.266 | 57.7098 | 58.1536 | 58.5974 | 59.0411 | 59.4849 | 59.9287 | 60.3725 | 60.8163 | 61.26 | 61.7038 | 62.1476 | 62.5914 | 63.0351 | 63.4789 | 63.9227 | 64.3665 | 64.8103 | 65.254 | 65.6978 | 66.1416 | 66.5854 | 67.0291 | 67.4729 | 67.9167 | 68.3605 | 68.8043 | 69.248 | 69.6918 | 70.1356 | 70.5794 | 71.0231 | 71.4669 | 71.9107 | 72.3545 | 72.7983 | 73.242 | 73.6858 | 74.1296 | 74.5734 | 75.0171 | 75.4609 | 75.9047 | 76.3485 | 76.7923 | 77.236 | 77.6798 | 78.1236 | 78.5674 | 79.0112 | 79.4549 | 79.8987 | 80.3425 | 80.7863 | 81.23 | 81.6738 | 82.1176 | 82.5614 | 83.0052 | 83.4489 | 83.8927 | 84.3365 | 84.7803 | 85.224 | 85.6678 | 86.1116 | 86.5554
Enersys Powersafe EON SBS 780 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5175 | 1.6247 | 1.7318 | 1.8816 | 2.0314 | 2.1812 | 3.1134 | 4.0456 | 5.8691 | 6.317 | 6.765 | 7.206 | 7.6471 | 8.0812 | 8.5153 | 8.9451 | 9.375 | 9.8056 | 10.2362 | 10.6803 | 11.1244 | 11.5684 | 12.0125 | 12.4566 | 12.9006 | 13.3447 | 13.7888 | 14.2329 | 14.6769 | 15.121 | 15.5651 | 16.0091 | 16.4532 | 16.8973 | 17.3414 | 17.7854 | 18.2295 | 18.6736 | 19.1176 | 19.5617 | 20.0058 | 20.4499 | 20.8939 | 21.338 | 21.7821 | 22.2261 | 22.6702 | 23.1143 | 23.5584 | 24.0024 | 24.4465 | 24.8906 | 25.3346 | 25.7787 | 26.2228 | 26.6669 | 27.1109 | 27.555 | 27.9991 | 28.4431 | 28.8872 | 29.3313 | 29.7754 | 30.2194 | 30.6635 | 31.1076 | 31.5516 | 31.9957 | 32.4398 | 32.8839 | 33.3279 | 33.772 | 34.2161 | 34.6601 | 35.1042 | 35.5483 | 35.9924 | 36.4364 | 36.8805 | 37.3246 | 37.7686 | 38.2127 | 38.6568 | 39.1009 | 39.5449 | 39.989 | 40.4331 | 40.8771 | 41.3212 | 41.7653 | 42.2094 | 42.6534 | 43.0975 | 43.5416 | 43.9856 | 44.4297 | 44.8738 | 45.3179 | 45.7619 | 46.206 | 46.6501 | 47.0941 | 47.5382 | 47.9823 | 48.4264 | 48.8704 | 49.3145 | 49.7586 | 50.2026 | 50.6467 | 51.0908 | 51.5349 | 51.9789 | 52.423 | 52.8671 | 53.3111 | 53.7552 | 54.1993 | 54.6434 | 55.0874 | 55.5315 | 55.9756 | 56.4196 | 56.8637 | 57.3078 | 57.7519 | 58.1959 | 58.64 | 59.0841 | 59.5281 | 59.9722 | 60.4163 | 60.8604 | 61.3044 | 61.7485 | 62.1926 | 62.6366 | 63.0807 | 63.5248 | 63.9689 | 64.4129 | 64.857 | 65.3011 | 65.7451 | 66.1892 | 66.6333 | 67.0774 | 67.5214 | 67.9655 | 68.4096 | 68.8536 | 69.2977 | 69.7418 | 70.1858 | 70.6299 | 71.074 | 71.5181 | 71.9621 | 72.4062 | 72.8503 | 73.2943 | 73.7384 | 74.1825 | 74.6266 | 75.0706 | 75.5147 | 75.9588 | 76.4028 | 76.8469 | 77.291 | 77.7351 | 78.1791 | 78.6232 | 79.0673 | 79.5113 | 79.9554 | 80.3995 | 80.8436 | 81.2876 | 81.7317 | 82.1758 | 82.6198 | 83.0639 | 83.508 | 83.9521 | 84.3961 | 84.8402 | 85.2843 | 85.7283 | 86.1724 | 86.6165
Enersys Powersafe EON SBS 900 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5172 | 1.5175 | 1.5175 | 1.6253 | 1.7331 | 1.8829 | 2.0326 | 2.1823 | 3.1146 | 4.0468 | 5.8708 | 6.3189 | 6.7669 | 7.2067 | 7.6466 | 8.0806 | 8.5147 | 8.9497 | 9.3848 | 9.8118 | 10.2389 | 10.6824 | 11.1258 | 11.5693 | 12.0128 | 12.4563 | 12.8997 | 13.3432 | 13.7867 | 14.2301 | 14.6736 | 15.1171 | 15.5605 | 16.004 | 16.4475 | 16.8909 | 17.3344 | 17.7779 | 18.2213 | 18.6648 | 19.1083 | 19.5517 | 19.9952 | 20.4387 | 20.8822 | 21.3256 | 21.7691 | 22.2126 | 22.656 | 23.0995 | 23.543 | 23.9864 | 24.4299 | 24.8734 | 25.3168 | 25.7603 | 26.2038 | 26.6472 | 27.0907 | 27.5342 | 27.9777 | 28.4211 | 28.8646 | 29.3081 | 29.7515 | 30.195 | 30.6385 | 31.0819 | 31.5254 | 31.9689 | 32.4123 | 32.8558 | 33.2993 | 33.7427 | 34.1862 | 34.6297 | 35.0732 | 35.5166 | 35.9601 | 36.4036 | 36.847 | 37.2905 | 37.734 | 38.1774 | 38.6209 | 39.0644 | 39.5078 | 39.9513 | 40.3948 | 40.8382 | 41.2817 | 41.7252 | 42.1686 | 42.6121 | 43.0556 | 43.4991 | 43.9425 | 44.386 | 44.8295 | 45.2729 | 45.7164 | 46.1599 | 46.6033 | 47.0468 | 47.4903 | 47.9337 | 48.3772 | 48.8207 | 49.2641 | 49.7076 | 50.1511 | 50.5946 | 51.038 | 51.4815 | 51.925 | 52.3684 | 52.8119 | 53.2554 | 53.6988 | 54.1423 | 54.5858 | 55.0292 | 55.4727 | 55.9162 | 56.3596 | 56.8031 | 57.2466 | 57.6901 | 58.1335 | 58.577 | 59.0205 | 59.4639 | 59.9074 | 60.3509 | 60.7943 | 61.2378 | 61.6813 | 62.1247 | 62.5682 | 63.0117 | 63.4551 | 63.8986 | 64.3421 | 64.7855 | 65.229 | 65.6725 | 66.116 | 66.5594 | 67.0029 | 67.4464 | 67.8898 | 68.3333 | 68.7768 | 69.2202 | 69.6637 | 70.1072 | 70.5506 | 70.9941 | 71.4376 | 71.881 | 72.3245 | 72.768 | 73.2115 | 73.6549 | 74.0984 | 74.5419 | 74.9853 | 75.4288 | 75.8723 | 76.3157 | 76.7592 | 77.2027 | 77.6461 | 78.0896 | 78.5331 | 78.9765 | 79.42 | 79.8635 | 80.3069 | 80.7504 | 81.1939 | 81.6374 | 82.0808 | 82.5243 | 82.9678 | 83.4112 | 83.8547 | 84.2982 | 84.7416 | 85.1851 | 85.6286 | 86.072 | 86.5155
Enersys Powersafe EON SBS B14 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.43147 | 0.53652 | 0.6818 | 0.82708 | 1.0353 | 1.2435 | 1.4518 | 2.4117 | 3.3716 | 5.2735 | 5.7592 | 6.2449 | 6.718 | 7.1911 | 7.6601 | 8.1291 | 8.6013 | 9.0735 | 9.5368 | 10 | 10.4581 | 10.9161 | 11.3742 | 11.8323 | 12.2904 | 12.7484 | 13.2065 | 13.6646 | 14.1227 | 14.5807 | 15.0388 | 15.4969 | 15.955 | 16.413 | 16.8711 | 17.3292 | 17.7873 | 18.2453 | 18.7034 | 19.1615 | 19.6196 | 20.0776 | 20.5357 | 20.9938 | 21.4519 | 21.9099 | 22.368 | 22.8261 | 23.2842 | 23.7422 | 24.2003 | 24.6584 | 25.1165 | 25.5745 | 26.0326 | 26.4907 | 26.9488 | 27.4068 | 27.8649 | 28.323 | 28.7811 | 29.2391 | 29.6972 | 30.1553 | 30.6134 | 31.0714 | 31.5295 | 31.9876 | 32.4457 | 32.9037 | 33.3618 | 33.8199 | 34.278 | 34.736 | 35.1941 | 35.6522 | 36.1102 | 36.5683 | 37.0264 | 37.4845 | 37.9425 | 38.4006 | 38.8587 | 39.3168 | 39.7748 | 40.2329 | 40.691 | 41.1491 | 41.6071 | 42.0652 | 42.5233 | 42.9814 | 43.4394 | 43.8975 | 44.3556 | 44.8137 | 45.2717 | 45.7298 | 46.1879 | 46.646 | 47.104 | 47.5621 | 48.0202 | 48.4783 | 48.9363 | 49.3944 | 49.8525 | 50.3106 | 50.7686 | 51.2267 | 51.6848 | 52.1429 | 52.6009 | 53.059 | 53.5171 | 53.9752 | 54.4332 | 54.8913 | 55.3494 | 55.8075 | 56.2655 | 56.7236 | 57.1817 | 57.6398 | 58.0978 | 58.5559 | 59.014 | 59.472 | 59.9301 | 60.3882 | 60.8463 | 61.3043 | 61.7624 | 62.2205 | 62.6786 | 63.1366 | 63.5947 | 64.0528 | 64.5109 | 64.9689 | 65.427 | 65.8851 | 66.3432 | 66.8012 | 67.2593 | 67.7174 | 68.1755 | 68.6335 | 69.0916 | 69.5497 | 70.0078 | 70.4658 | 70.9239 | 71.382 | 71.8401 | 72.2981 | 72.7562 | 73.2143 | 73.6724 | 74.1304 | 74.5885 | 75.0466 | 75.5047 | 75.9627 | 76.4208 | 76.8789 | 77.337 | 77.795 | 78.2531 | 78.7112 | 79.1693 | 79.6273 | 80.0854 | 80.5435 | 81.0016 | 81.4596 | 81.9177 | 82.3758 | 82.8339 | 83.2919 | 83.75 | 84.2081 | 84.6661 | 85.1242 | 85.5823 | 86.0404 | 86.4984 | 86.9565 | 87.4146 | 87.8727 | 88.3307 | 88.7888
Enersys Powersafe EON SBS B14F | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.43147 | 0.53652 | 0.6818 | 0.82708 | 1.0353 | 1.2435 | 1.4518 | 2.4117 | 3.3716 | 5.2735 | 5.7592 | 6.2449 | 6.718 | 7.1911 | 7.6601 | 8.1291 | 8.6013 | 9.0735 | 9.5368 | 10 | 10.4581 | 10.9161 | 11.3742 | 11.8323 | 12.2904 | 12.7484 | 13.2065 | 13.6646 | 14.1227 | 14.5807 | 15.0388 | 15.4969 | 15.955 | 16.413 | 16.8711 | 17.3292 | 17.7873 | 18.2453 | 18.7034 | 19.1615 | 19.6196 | 20.0776 | 20.5357 | 20.9938 | 21.4519 | 21.9099 | 22.368 | 22.8261 | 23.2842 | 23.7422 | 24.2003 | 24.6584 | 25.1165 | 25.5745 | 26.0326 | 26.4907 | 26.9488 | 27.4068 | 27.8649 | 28.323 | 28.7811 | 29.2391 | 29.6972 | 30.1553 | 30.6134 | 31.0714 | 31.5295 | 31.9876 | 32.4457 | 32.9037 | 33.3618 | 33.8199 | 34.278 | 34.736 | 35.1941 | 35.6522 | 36.1102 | 36.5683 | 37.0264 | 37.4845 | 37.9425 | 38.4006 | 38.8587 | 39.3168 | 39.7748 | 40.2329 | 40.691 | 41.1491 | 41.6071 | 42.0652 | 42.5233 | 42.9814 | 43.4394 | 43.8975 | 44.3556 | 44.8137 | 45.2717 | 45.7298 | 46.1879 | 46.646 | 47.104 | 47.5621 | 48.0202 | 48.4783 | 48.9363 | 49.3944 | 49.8525 | 50.3106 | 50.7686 | 51.2267 | 51.6848 | 52.1429 | 52.6009 | 53.059 | 53.5171 | 53.9752 | 54.4332 | 54.8913 | 55.3494 | 55.8075 | 56.2655 | 56.7236 | 57.1817 | 57.6398 | 58.0978 | 58.5559 | 59.014 | 59.472 | 59.9301 | 60.3882 | 60.8463 | 61.3043 | 61.7624 | 62.2205 | 62.6786 | 63.1366 | 63.5947 | 64.0528 | 64.5109 | 64.9689 | 65.427 | 65.8851 | 66.3432 | 66.8012 | 67.2593 | 67.7174 | 68.1755 | 68.6335 | 69.0916 | 69.5497 | 70.0078 | 70.4658 | 70.9239 | 71.382 | 71.8401 | 72.2981 | 72.7562 | 73.2143 | 73.6724 | 74.1304 | 74.5885 | 75.0466 | 75.5047 | 75.9627 | 76.4208 | 76.8789 | 77.337 | 77.795 | 78.2531 | 78.7112 | 79.1693 | 79.6273 | 80.0854 | 80.5435 | 81.0016 | 81.4596 | 81.9177 | 82.3758 | 82.8339 | 83.2919 | 83.75 | 84.2081 | 84.6661 | 85.1242 | 85.5823 | 86.0404 | 86.4984 | 86.9565 | 87.4146 | 87.8727 | 88.3307 | 88.7888
Enersys Powersafe EON SBS C11 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.49728 | 0.61409 | 0.77676 | 0.93943 | 1.1372 | 1.3349 | 1.5327 | 2.6037 | 3.6747 | 5.6832 | 6.1568 | 6.6304 | 7.0962 | 7.562 | 7.9026 | 8.2432 | 8.6966 | 9.15 | 9.6135 | 10.0771 | 10.5031 | 10.9291 | 11.3552 | 11.7812 | 12.2072 | 12.6332 | 13.0593 | 13.4853 | 13.9113 | 14.3373 | 14.7634 | 15.1894 | 15.6154 | 16.0414 | 16.4674 | 16.8935 | 17.3195 | 17.7455 | 18.1715 | 18.5976 | 19.0236 | 19.4496 | 19.8756 | 20.3017 | 20.7277 | 21.1537 | 21.5797 | 22.0057 | 22.4318 | 22.8578 | 23.2838 | 23.7098 | 24.1359 | 24.5619 | 24.9879 | 25.4139 | 25.84 | 26.266 | 26.692 | 27.118 | 27.5441 | 27.9701 | 28.3961 | 28.8221 | 29.2481 | 29.6742 | 30.1002 | 30.5262 | 30.9522 | 31.3783 | 31.8043 | 32.2303 | 32.6563 | 33.0824 | 33.5084 | 33.9344 | 34.3604 | 34.7865 | 35.2125 | 35.6385 | 36.0645 | 36.4905 | 36.9166 | 37.3426 | 37.7686 | 38.1946 | 38.6207 | 39.0467 | 39.4727 | 39.8987 | 40.3248 | 40.7508 | 41.1768 | 41.6028 | 42.0288 | 42.4549 | 42.8809 | 43.3069 | 43.7329 | 44.159 | 44.585 | 45.011 | 45.437 | 45.8631 | 46.2891 | 46.7151 | 47.1411 | 47.5672 | 47.9932 | 48.4192 | 48.8452 | 49.2712 | 49.6973 | 50.1233 | 50.5493 | 50.9753 | 51.4014 | 51.8274 | 52.2534 | 52.6794 | 53.1055 | 53.5315 | 53.9575 | 54.3835 | 54.8096 | 55.2356 | 55.6616 | 56.0876 | 56.5136 | 56.9397 | 57.3657 | 57.7917 | 58.2177 | 58.6438 | 59.0698 | 59.4958 | 59.9218 | 60.3479 | 60.7739 | 61.1999 | 61.6259 | 62.052 | 62.478 | 62.904 | 63.33 | 63.756 | 64.1821 | 64.6081 | 65.0341 | 65.4601 | 65.8862 | 66.3122 | 66.7382 | 67.1642 | 67.5903 | 68.0163 | 68.4423 | 68.8683 | 69.2943 | 69.7204 | 70.1464 | 70.5724 | 70.9984 | 71.4245 | 71.8505 | 72.2765 | 72.7025 | 73.1286 | 73.5546 | 73.9806 | 74.4066 | 74.8327 | 75.2587 | 75.6847 | 76.1107 | 76.5367 | 76.9628 | 77.3888 | 77.8148 | 78.2408 | 78.6669 | 79.0929 | 79.5189 | 79.9449 | 80.371 | 80.797 | 81.223 | 81.649 | 82.0751 | 82.5011 | 82.9271 | 83.3531
Enersys Powersafe EON SBS C11F | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.49728 | 0.61409 | 0.77676 | 0.93943 | 1.1372 | 1.3349 | 1.5327 | 2.6037 | 3.6747 | 5.6832 | 6.1568 | 6.6304 | 7.0962 | 7.562 | 7.9026 | 8.2432 | 8.6966 | 9.15 | 9.6135 | 10.0771 | 10.5031 | 10.9291 | 11.3552 | 11.7812 | 12.2072 | 12.6332 | 13.0593 | 13.4853 | 13.9113 | 14.3373 | 14.7634 | 15.1894 | 15.6154 | 16.0414 | 16.4674 | 16.8935 | 17.3195 | 17.7455 | 18.1715 | 18.5976 | 19.0236 | 19.4496 | 19.8756 | 20.3017 | 20.7277 | 21.1537 | 21.5797 | 22.0057 | 22.4318 | 22.8578 | 23.2838 | 23.7098 | 24.1359 | 24.5619 | 24.9879 | 25.4139 | 25.84 | 26.266 | 26.692 | 27.118 | 27.5441 | 27.9701 | 28.3961 | 28.8221 | 29.2481 | 29.6742 | 30.1002 | 30.5262 | 30.9522 | 31.3783 | 31.8043 | 32.2303 | 32.6563 | 33.0824 | 33.5084 | 33.9344 | 34.3604 | 34.7865 | 35.2125 | 35.6385 | 36.0645 | 36.4905 | 36.9166 | 37.3426 | 37.7686 | 38.1946 | 38.6207 | 39.0467 | 39.4727 | 39.8987 | 40.3248 | 40.7508 | 41.1768 | 41.6028 | 42.0288 | 42.4549 | 42.8809 | 43.3069 | 43.7329 | 44.159 | 44.585 | 45.011 | 45.437 | 45.8631 | 46.2891 | 46.7151 | 47.1411 | 47.5672 | 47.9932 | 48.4192 | 48.8452 | 49.2712 | 49.6973 | 50.1233 | 50.5493 | 50.9753 | 51.4014 | 51.8274 | 52.2534 | 52.6794 | 53.1055 | 53.5315 | 53.9575 | 54.3835 | 54.8096 | 55.2356 | 55.6616 | 56.0876 | 56.5136 | 56.9397 | 57.3657 | 57.7917 | 58.2177 | 58.6438 | 59.0698 | 59.4958 | 59.9218 | 60.3479 | 60.7739 | 61.1999 | 61.6259 | 62.052 | 62.478 | 62.904 | 63.33 | 63.756 | 64.1821 | 64.6081 | 65.0341 | 65.4601 | 65.8862 | 66.3122 | 66.7382 | 67.1642 | 67.5903 | 68.0163 | 68.4423 | 68.8683 | 69.2943 | 69.7204 | 70.1464 | 70.5724 | 70.9984 | 71.4245 | 71.8505 | 72.2765 | 72.7025 | 73.1286 | 73.5546 | 73.9806 | 74.4066 | 74.8327 | 75.2587 | 75.6847 | 76.1107 | 76.5367 | 76.9628 | 77.3888 | 77.8148 | 78.2408 | 78.6669 | 79.0929 | 79.5189 | 79.9449 | 80.371 | 80.797 | 81.223 | 81.649 | 82.0751 | 82.5011 | 82.9271 | 83.3531
1
Kt: 1.85V/Cell @ 15degC |  | 1s | 5s | 30s | 60s | 3m | 5m | 10m | 15m | 20m | 30m | 40m | 50m | 1h | 1.5h | 3h | 5h | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
Time | 0 | 0.00032777 | 0.0014389 | 0.0083833 | 0.016717 | 0.05005 | 0.083383 | 0.16672 | 0.25005 | 0.33338 | 0.50005 | 0.66672 | 0.83338 | 1 | 1.5 | 3 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200
Enersys Powersafe EON SBS 100 | 0.43112 | 0.43112 | 0.43112 | 0.43112 | 0.43112 | 0.43112 | 0.43112 | 0.54684 | 0.65913 | 0.81644 | 0.97376 | 1.1664 | 1.3591 | 1.5517 | 2.6037 | 3.6558 | 5.647 | 6.1176 | 6.5881 | 7.045 | 7.5018 | 8.0244 | 8.547 | 9.0218 | 9.4967 | 9.944 | 10.3914 | 10.8402 | 11.2891 | 11.7379 | 12.1868 | 12.6356 | 13.0845 | 13.5333 | 13.9822 | 14.4311 | 14.8799 | 15.3288 | 15.7776 | 16.2265 | 16.6753 | 17.1242 | 17.573 | 18.0219 | 18.4707 | 18.9196 | 19.3684 | 19.8173 | 20.2661 | 20.715 | 21.1638 | 21.6127 | 22.0616 | 22.5104 | 22.9593 | 23.4081 | 23.857 | 24.3058 | 24.7547 | 25.2035 | 25.6524 | 26.1012 | 26.5501 | 26.9989 | 27.4478 | 27.8966 | 28.3455 | 28.7943 | 29.2432 | 29.692 | 30.1409 | 30.5898 | 31.0386 | 31.4875 | 31.9363 | 32.3852 | 32.834 | 33.2829 | 33.7317 | 34.1806 | 34.6294 | 35.0783 | 35.5271 | 35.976 | 36.4248 | 36.8737 | 37.3225 | 37.7714 | 38.2202 | 38.6691 | 39.118 | 39.5668 | 40.0157 | 40.4645 | 40.9134 | 41.3622 | 41.8111 | 42.2599 | 42.7088 | 43.1576 | 43.6065 | 44.0553 | 44.5042 | 44.953 | 45.4019 | 45.8507 | 46.2996 | 46.7484 | 47.1973 | 47.6462 | 48.095 | 48.5439 | 48.9927 | 49.4416 | 49.8904 | 50.3393 | 50.7881 | 51.237 | 51.6858 | 52.1347 | 52.5835 | 53.0324 | 53.4812 | 53.9301 | 54.3789 | 54.8278 | 55.2766 | 55.7255 | 56.1744 | 56.6232 | 57.0721 | 57.5209 | 57.9698 | 58.4186 | 58.8675 | 59.3163 | 59.7652 | 60.214 | 60.6629 | 61.1117 | 61.5606 | 62.0094 | 62.4583 | 62.9071 | 63.356 | 63.8048 | 64.2537 | 64.7026 | 65.1514 | 65.6003 | 66.0491 | 66.498 | 66.9468 | 67.3957 | 67.8445 | 68.2934 | 68.7422 | 69.1911 | 69.6399 | 70.0888 | 70.5376 | 70.9865 | 71.4353 | 71.8842 | 72.333 | 72.7819 | 73.2308 | 73.6796 | 74.1285 | 74.5773 | 75.0262 | 75.475 | 75.9239 | 76.3727 | 76.8216 | 77.2704 | 77.7193 | 78.1681 | 78.617 | 79.0658 | 79.5147 | 79.9635 | 80.4124 | 80.8612 | 81.3101 | 81.759 | 82.2078 | 82.6567 | 83.1055 | 83.5544 | 84.0032 | 84.4521 | 84.9009 | 85.3498 | 85.7986 | 86.2475 | 86.6963 | 87.1452 | 87.594
Enersys Powersafe EON SBS 100F | 0.43112 | 0.43112 | 0.43112 | 0.43112 | 0.43112 | 0.43112 | 0.43112 | 0.54684 | 0.65913 | 0.81644 | 0.97376 | 1.1664 | 1.3591 | 1.5517 | 2.6037 | 3.6558 | 5.647 | 6.1176 | 6.5881 | 7.045 | 7.5018 | 8.0244 | 8.547 | 9.0218 | 9.4967 | 9.944 | 10.3914 | 10.8402 | 11.2891 | 11.7379 | 12.1868 | 12.6356 | 13.0845 | 13.5333 | 13.9822 | 14.4311 | 14.8799 | 15.3288 | 15.7776 | 16.2265 | 16.6753 | 17.1242 | 17.573 | 18.0219 | 18.4707 | 18.9196 | 19.3684 | 19.8173 | 20.2661 | 20.715 | 21.1638 | 21.6127 | 22.0616 | 22.5104 | 22.9593 | 23.4081 | 23.857 | 24.3058 | 24.7547 | 25.2035 | 25.6524 | 26.1012 | 26.5501 | 26.9989 | 27.4478 | 27.8966 | 28.3455 | 28.7943 | 29.2432 | 29.692 | 30.1409 | 30.5898 | 31.0386 | 31.4875 | 31.9363 | 32.3852 | 32.834 | 33.2829 | 33.7317 | 34.1806 | 34.6294 | 35.0783 | 35.5271 | 35.976 | 36.4248 | 36.8737 | 37.3225 | 37.7714 | 38.2202 | 38.6691 | 39.118 | 39.5668 | 40.0157 | 40.4645 | 40.9134 | 41.3622 | 41.8111 | 42.2599 | 42.7088 | 43.1576 | 43.6065 | 44.0553 | 44.5042 | 44.953 | 45.4019 | 45.8507 | 46.2996 | 46.7484 | 47.1973 | 47.6462 | 48.095 | 48.5439 | 48.9927 | 49.4416 | 49.8904 | 50.3393 | 50.7881 | 51.237 | 51.6858 | 52.1347 | 52.5835 | 53.0324 | 53.4812 | 53.9301 | 54.3789 | 54.8278 | 55.2766 | 55.7255 | 56.1744 | 56.6232 | 57.0721 | 57.5209 | 57.9698 | 58.4186 | 58.8675 | 59.3163 | 59.7652 | 60.214 | 60.6629 | 61.1117 | 61.5606 | 62.0094 | 62.4583 | 62.9071 | 63.356 | 63.8048 | 64.2537 | 64.7026 | 65.1514 | 65.6003 | 66.0491 | 66.498 | 66.9468 | 67.3957 | 67.8445 | 68.2934 | 68.7422 | 69.1911 | 69.6399 | 70.0888 | 70.5376 | 70.9865 | 71.4353 | 71.8842 | 72.333 | 72.7819 | 73.2308 | 73.6796 | 74.1285 | 74.5773 | 75.0262 | 75.475 | 75.9239 | 76.3727 | 76.8216 | 77.2704 | 77.7193 | 78.1681 | 78.617 | 79.0658 | 79.5147 | 79.9635 | 80.4124 | 80.8612 | 81.3101 | 81.759 | 82.2078 | 82.6567 | 83.1055 | 83.5544 | 84.0032 | 84.4521 | 84.9009 | 85.3498 | 85.7986 | 86.2475 | 86.6963 | 87.1452 | 87.594
Enersys Powersafe EON SBS 170F | 0.61641 | 0.61641 | 0.61641 | 0.61641 | 0.61641 | 0.61641 | 0.61641 | 0.60716 | 0.71398 | 0.86915 | 1.0243 | 1.2167 | 1.409 | 1.6013 | 2.6651 | 3.7289 | 5.7662 | 6.2691 | 6.772 | 7.2514 | 7.7309 | 8.2244 | 8.7179 | 9.2023 | 9.6866 | 10.1537 | 10.6208 | 11.0639 | 11.507 | 11.9501 | 12.3933 | 12.8364 | 13.2795 | 13.7226 | 14.1658 | 14.6089 | 15.052 | 15.4951 | 15.9383 | 16.3814 | 16.8245 | 17.2676 | 17.7108 | 18.1539 | 18.597 | 19.0401 | 19.4833 | 19.9264 | 20.3695 | 20.8126 | 21.2558 | 21.6989 | 22.142 | 22.5851 | 23.0283 | 23.4714 | 23.9145 | 24.3576 | 24.8008 | 25.2439 | 25.687 | 26.1301 | 26.5733 | 27.0164 | 27.4595 | 27.9026 | 28.3458 | 28.7889 | 29.232 | 29.6751 | 30.1183 | 30.5614 | 31.0045 | 31.4476 | 31.8908 | 32.3339 | 32.777 | 33.2201 | 33.6633 | 34.1064 | 34.5495 | 34.9926 | 35.4358 | 35.8789 | 36.322 | 36.7651 | 37.2083 | 37.6514 | 38.0945 | 38.5376 | 38.9808 | 39.4239 | 39.867 | 40.3101 | 40.7533 | 41.1964 | 41.6395 | 42.0826 | 42.5258 | 42.9689 | 43.412 | 43.8552 | 44.2983 | 44.7414 | 45.1845 | 45.6277 | 46.0708 | 46.5139 | 46.957 | 47.4002 | 47.8433 | 48.2864 | 48.7295 | 49.1727 | 49.6158 | 50.0589 | 50.502 | 50.9452 | 51.3883 | 51.8314 | 52.2745 | 52.7177 | 53.1608 | 53.6039 | 54.047 | 54.4902 | 54.9333 | 55.3764 | 55.8195 | 56.2627 | 56.7058 | 57.1489 | 57.592 | 58.0352 | 58.4783 | 58.9214 | 59.3645 | 59.8077 | 60.2508 | 60.6939 | 61.137 | 61.5802 | 62.0233 | 62.4664 | 62.9095 | 63.3527 | 63.7958 | 64.2389 | 64.682 | 65.1252 | 65.5683 | 66.0114 | 66.4545 | 66.8977 | 67.3408 | 67.7839 | 68.227 | 68.6702 | 69.1133 | 69.5564 | 69.9995 | 70.4427 | 70.8858 | 71.3289 | 71.772 | 72.2152 | 72.6583 | 73.1014 | 73.5445 | 73.9877 | 74.4308 | 74.8739 | 75.317 | 75.7602 | 76.2033 | 76.6464 | 77.0896 | 77.5327 | 77.9758 | 78.4189 | 78.8621 | 79.3052 | 79.7483 | 80.1914 | 80.6346 | 81.0777 | 81.5208 | 81.9639 | 82.4071 | 82.8502 | 83.2933 | 83.7364 | 84.1796 | 84.6227 | 85.0658 | 85.5089 | 85.9521 | 86.3952 | 86.8383
Enersys Powersafe EON SBS 190F | 0.60576 | 0.60576 | 0.60576 | 0.60576 | 0.60576 | 0.60576 | 0.60576 | 0.59667 | 0.70452 | 0.86169 | 1.0188 | 1.2157 | 1.4126 | 1.6094 | 2.6667 | 3.7239 | 5.7602 | 6.2585 | 6.7568 | 7.2376 | 7.7183 | 8.1896 | 8.661 | 9.1303 | 9.5996 | 10.0612 | 10.5228 | 10.9604 | 11.398 | 11.8356 | 12.2731 | 12.7107 | 13.1483 | 13.5859 | 14.0235 | 14.4611 | 14.8986 | 15.3362 | 15.7738 | 16.2114 | 16.649 | 17.0866 | 17.5241 | 17.9617 | 18.3993 | 18.8369 | 19.2745 | 19.7121 | 20.1496 | 20.5872 | 21.0248 | 21.4624 | 21.9 | 22.3375 | 22.7751 | 23.2127 | 23.6503 | 24.0879 | 24.5255 | 24.963 | 25.4006 | 25.8382 | 26.2758 | 26.7134 | 27.151 | 27.5885 | 28.0261 | 28.4637 | 28.9013 | 29.3389 | 29.7764 | 30.214 | 30.6516 | 31.0892 | 31.5268 | 31.9644 | 32.4019 | 32.8395 | 33.2771 | 33.7147 | 34.1523 | 34.5899 | 35.0274 | 35.465 | 35.9026 | 36.3402 | 36.7778 | 37.2154 | 37.6529 | 38.0905 | 38.5281 | 38.9657 | 39.4033 | 39.8408 | 40.2784 | 40.716 | 41.1536 | 41.5912 | 42.0288 | 42.4663 | 42.9039 | 43.3415 | 43.7791 | 44.2167 | 44.6543 | 45.0918 | 45.5294 | 45.967 | 46.4046 | 46.8422 | 47.2798 | 47.7173 | 48.1549 | 48.5925 | 49.0301 | 49.4677 | 49.9052 | 50.3428 | 50.7804 | 51.218 | 51.6556 | 52.0932 | 52.5307 | 52.9683 | 53.4059 | 53.8435 | 54.2811 | 54.7187 | 55.1562 | 55.5938 | 56.0314 | 56.469 | 56.9066 | 57.3441 | 57.7817 | 58.2193 | 58.6569 | 59.0945 | 59.5321 | 59.9696 | 60.4072 | 60.8448 | 61.2824 | 61.72 | 62.1576 | 62.5951 | 63.0327 | 63.4703 | 63.9079 | 64.3455 | 64.7831 | 65.2206 | 65.6582 | 66.0958 | 66.5334 | 66.971 | 67.4085 | 67.8461 | 68.2837 | 68.7213 | 69.1589 | 69.5965 | 70.034 | 70.4716 | 70.9092 | 71.3468 | 71.7844 | 72.222 | 72.6595 | 73.0971 | 73.5347 | 73.9723 | 74.4099 | 74.8474 | 75.285 | 75.7226 | 76.1602 | 76.5978 | 77.0354 | 77.4729 | 77.9105 | 78.3481 | 78.7857 | 79.2233 | 79.6609 | 80.0984 | 80.536 | 80.9736 | 81.4112 | 81.8488 | 82.2864 | 82.7239 | 83.1615 | 83.5991 | 84.0367 | 84.4743 | 84.9118 | 85.3494 | 85.787
Enersys Powersafe EON SBS 320 | 1.651 | 1.651 | 1.651 | 1.651 | 1.651 | 1.651 | 1.651 | 1.6263 | 1.6142 | 1.7189 | 1.8237 | 1.974 | 2.1243 | 2.2746 | 3.2226 | 4.1706 | 6.0345 | 6.4938 | 6.9531 | 7.4105 | 7.8679 | 8.31 | 8.7521 | 9.1885 | 9.6248 | 10.0667 | 10.5086 | 10.9648 | 11.421 | 11.8773 | 12.3335 | 12.7897 | 13.2459 | 13.7021 | 14.1583 | 14.6145 | 15.0707 | 15.527 | 15.9832 | 16.4394 | 16.8956 | 17.3518 | 17.808 | 18.2642 | 18.7204 | 19.1767 | 19.6329 | 20.0891 | 20.5453 | 21.0015 | 21.4577 | 21.9139 | 22.3701 | 22.8264 | 23.2826 | 23.7388 | 24.195 | 24.6512 | 25.1074 | 25.5636 | 26.0198 | 26.4761 | 26.9323 | 27.3885 | 27.8447 | 28.3009 | 28.7571 | 29.2133 | 29.6695 | 30.1258 | 30.582 | 31.0382 | 31.4944 | 31.9506 | 32.4068 | 32.863 | 33.3192 | 33.7755 | 34.2317 | 34.6879 | 35.1441 | 35.6003 | 36.0565 | 36.5127 | 36.9689 | 37.4251 | 37.8814 | 38.3376 | 38.7938 | 39.25 | 39.7062 | 40.1624 | 40.6186 | 41.0748 | 41.5311 | 41.9873 | 42.4435 | 42.8997 | 43.3559 | 43.8121 | 44.2683 | 44.7245 | 45.1808 | 45.637 | 46.0932 | 46.5494 | 47.0056 | 47.4618 | 47.918 | 48.3742 | 48.8305 | 49.2867 | 49.7429 | 50.1991 | 50.6553 | 51.1115 | 51.5677 | 52.0239 | 52.4802 | 52.9364 | 53.3926 | 53.8488 | 54.305 | 54.7612 | 55.2174 | 55.6736 | 56.1299 | 56.5861 | 57.0423 | 57.4985 | 57.9547 | 58.4109 | 58.8671 | 59.3233 | 59.7796 | 60.2358 | 60.692 | 61.1482 | 61.6044 | 62.0606 | 62.5168 | 62.973 | 63.4293 | 63.8855 | 64.3417 | 64.7979 | 65.2541 | 65.7103 | 66.1665 | 66.6227 | 67.079 | 67.5352 | 67.9914 | 68.4476 | 68.9038 | 69.36 | 69.8162 | 70.2724 | 70.7287 | 71.1849 | 71.6411 | 72.0973 | 72.5535 | 73.0097 | 73.4659 | 73.9221 | 74.3784 | 74.8346 | 75.2908 | 75.747 | 76.2032 | 76.6594 | 77.1156 | 77.5718 | 78.0281 | 78.4843 | 78.9405 | 79.3967 | 79.8529 | 80.3091 | 80.7653 | 81.2215 | 81.6778 | 82.134 | 82.5902 | 83.0464 | 83.5026 | 83.9588 | 84.415 | 84.8712 | 85.3275 | 85.7837 | 86.2399 | 86.6961 | 87.1523 | 87.6085 | 88.0647 | 88.5209 | 88.9772
Enersys Powersafe EON SBS 400 | 1.6512 | 1.6512 | 1.6512 | 1.6512 | 1.6512 | 1.6512 | 1.6512 | 1.6264 | 1.6143 | 1.7189 | 1.8235 | 1.9738 | 2.124 | 2.2743 | 3.2219 | 4.1696 | 6.0367 | 6.4964 | 6.956 | 7.4082 | 7.8604 | 8.3039 | 8.7475 | 9.189 | 9.6304 | 10.0561 | 10.4817 | 10.9381 | 11.3945 | 11.8509 | 12.3073 | 12.7637 | 13.22 | 13.6764 | 14.1328 | 14.5892 | 15.0456 | 15.5019 | 15.9583 | 16.4147 | 16.8711 | 17.3275 | 17.7839 | 18.2402 | 18.6966 | 19.153 | 19.6094 | 20.0658 | 20.5221 | 20.9785 | 21.4349 | 21.8913 | 22.3477 | 22.8041 | 23.2604 | 23.7168 | 24.1732 | 24.6296 | 25.086 | 25.5423 | 25.9987 | 26.4551 | 26.9115 | 27.3679 | 27.8243 | 28.2806 | 28.737 | 29.1934 | 29.6498 | 30.1062 | 30.5625 | 31.0189 | 31.4753 | 31.9317 | 32.3881 | 32.8445 | 33.3008 | 33.7572 | 34.2136 | 34.67 | 35.1264 | 35.5828 | 36.0391 | 36.4955 | 36.9519 | 37.4083 | 37.8647 | 38.321 | 38.7774 | 39.2338 | 39.6902 | 40.1466 | 40.603 | 41.0593 | 41.5157 | 41.9721 | 42.4285 | 42.8849 | 43.3412 | 43.7976 | 44.254 | 44.7104 | 45.1668 | 45.6232 | 46.0795 | 46.5359 | 46.9923 | 47.4487 | 47.9051 | 48.3614 | 48.8178 | 49.2742 | 49.7306 | 50.187 | 50.6434 | 51.0997 | 51.5561 | 52.0125 | 52.4689 | 52.9253 | 53.3817 | 53.838 | 54.2944 | 54.7508 | 55.2072 | 55.6636 | 56.1199 | 56.5763 | 57.0327 | 57.4891 | 57.9455 | 58.4019 | 58.8582 | 59.3146 | 59.771 | 60.2274 | 60.6838 | 61.1401 | 61.5965 | 62.0529 | 62.5093 | 62.9657 | 63.4221 | 63.8784 | 64.3348 | 64.7912 | 65.2476 | 65.704 | 66.1603 | 66.6167 | 67.0731 | 67.5295 | 67.9859 | 68.4423 | 68.8986 | 69.355 | 69.8114 | 70.2678 | 70.7242 | 71.1805 | 71.6369 | 72.0933 | 72.5497 | 73.0061 | 73.4625 | 73.9188 | 74.3752 | 74.8316 | 75.288 | 75.7444 | 76.2008 | 76.6571 | 77.1135 | 77.5699 | 78.0263 | 78.4827 | 78.939 | 79.3954 | 79.8518 | 80.3082 | 80.7646 | 81.221 | 81.6773 | 82.1337 | 82.5901 | 83.0465 | 83.5029 | 83.9592 | 84.4156 | 84.872 | 85.3284 | 85.7848 | 86.2412 | 86.6975 | 87.1539 | 87.6103 | 88.0667 | 88.5231 | 88.9794
Enersys Powersafe EON SBS 410 | 0.5388 | 0.5388 | 0.5388 | 0.5388 | 0.5388 | 0.5388 | 0.5388 | 0.70478 | 0.87021 | 1.1295 | 1.3888 | 1.5157 | 1.6427 | 1.7697 | 2.8261 | 3.8826 | 5.5972 | 6.3852 | 7.1732 | 7.7077 | 8.2421 | 8.3076 | 8.373 | 9.2774 | 10.1817 | 10.2901 | 10.3984 | 10.9813 | 11.5642 | 12.147 | 12.7299 | 13.3127 | 13.8956 | 14.4785 | 15.0613 | 15.6442 | 16.227 | 16.8099 | 17.3928 | 17.9756 | 18.5585 | 19.1414 | 19.7242 | 20.3071 | 20.8899 | 21.4728 | 22.0557 | 22.6385 | 23.2214 | 23.8042 | 24.3871 | 24.97 | 25.5528 | 26.1357 | 26.7185 | 27.3014 | 27.8843 | 28.4671 | 29.05 | 29.6328 | 30.2157 | 30.7986 | 31.3814 | 31.9643 | 32.5471 | 33.13 | 33.7129 | 34.2957 | 34.8786 | 35.4614 | 36.0443 | 36.6272 | 37.21 | 37.7929 | 38.3757 | 38.9586 | 39.5415 | 40.1243 | 40.7072 | 41.29 | 41.8729 | 42.4558 | 43.0386 | 43.6215 | 44.2043 | 44.7872 | 45.3701 | 45.9529 | 46.5358 | 47.1186 | 47.7015 | 48.2844 | 48.8672 | 49.4501 | 50.0329 | 50.6158 | 51.1987 | 51.7815 | 52.3644 | 52.9472 | 53.5301 | 54.113 | 54.6958 | 55.2787 | 55.8615 | 56.4444 | 57.0273 | 57.6101 | 58.193 | 58.7758 | 59.3587 | 59.9416 | 60.5244 | 61.1073 | 61.6901 | 62.273 | 62.8559 | 63.4387 | 64.0216 | 64.6045 | 65.1873 | 65.7702 | 66.353 | 66.9359 | 67.5188 | 68.1016 | 68.6845 | 69.2673 | 69.8502 | 70.4331 | 71.0159 | 71.5988 | 72.1816 | 72.7645 | 73.3474 | 73.9302 | 74.5131 | 75.0959 | 75.6788 | 76.2617 | 76.8445 | 77.4274 | 78.0102 | 78.5931 | 79.176 | 79.7588 | 80.3417 | 80.9245 | 81.5074 | 82.0903 | 82.6731 | 83.256 | 83.8388 | 84.4217 | 85.0046 | 85.5874 | 86.1703 | 86.7531 | 87.336 | 87.9189 | 88.5017 | 89.0846 | 89.6674 | 90.2503 | 90.8332 | 91.416 | 91.9989 | 92.5817 | 93.1646 | 93.7475 | 94.3303 | 94.9132 | 95.496 | 96.0789 | 96.6618 | 97.2446 | 97.8275 | 98.4103 | 98.9932 | 99.5761 | 100.1589 | 100.7418 | 101.3246 | 101.9075 | 102.4904 | 103.0732 | 103.6561 | 104.2389 | 104.8218 | 105.4047 | 105.9875 | 106.5704 | 107.1533 | 107.7361 | 108.319 | 108.9018 | 109.4847 | 110.0676 | 110.6504
Enersys Powersafe EON SBS 480 | 1.6508 | 1.6508 | 1.6508 | 1.6508 | 1.6508 | 1.6508 | 1.6508 | 1.6265 | 1.6144 | 1.7189 | 1.8234 | 1.9736 | 2.1238 | 2.2741 | 3.2232 | 4.1724 | 6.0308 | 6.4944 | 6.958 | 7.4067 | 7.8554 | 8.2999 | 8.7444 | 9.1799 | 9.6154 | 10.0508 | 10.4862 | 10.9416 | 11.397 | 11.8523 | 12.3077 | 12.7631 | 13.2185 | 13.6739 | 14.1292 | 14.5846 | 15.04 | 15.4954 | 15.9507 | 16.4061 | 16.8615 | 17.3169 | 17.7722 | 18.2276 | 18.683 | 19.1384 | 19.5938 | 20.0491 | 20.5045 | 20.9599 | 21.4153 | 21.8706 | 22.326 | 22.7814 | 23.2368 | 23.6922 | 24.1475 | 24.6029 | 25.0583 | 25.5137 | 25.969 | 26.4244 | 26.8798 | 27.3352 | 27.7905 | 28.2459 | 28.7013 | 29.1567 | 29.6121 | 30.0674 | 30.5228 | 30.9782 | 31.4336 | 31.8889 | 32.3443 | 32.7997 | 33.2551 | 33.7105 | 34.1658 | 34.6212 | 35.0766 | 35.532 | 35.9873 | 36.4427 | 36.8981 | 37.3535 | 37.8088 | 38.2642 | 38.7196 | 39.175 | 39.6304 | 40.0857 | 40.5411 | 40.9965 | 41.4519 | 41.9072 | 42.3626 | 42.818 | 43.2734 | 43.7288 | 44.1841 | 44.6395 | 45.0949 | 45.5503 | 46.0056 | 46.461 | 46.9164 | 47.3718 | 47.8271 | 48.2825 | 48.7379 | 49.1933 | 49.6487 | 50.104 | 50.5594 | 51.0148 | 51.4702 | 51.9255 | 52.3809 | 52.8363 | 53.2917 | 53.7471 | 54.2024 | 54.6578 | 55.1132 | 55.5686 | 56.0239 | 56.4793 | 56.9347 | 57.3901 | 57.8454 | 58.3008 | 58.7562 | 59.2116 | 59.667 | 60.1223 | 60.5777 | 61.0331 | 61.4885 | 61.9438 | 62.3992 | 62.8546 | 63.31 | 63.7654 | 64.2207 | 64.6761 | 65.1315 | 65.5869 | 66.0422 | 66.4976 | 66.953 | 67.4084 | 67.8637 | 68.3191 | 68.7745 | 69.2299 | 69.6853 | 70.1406 | 70.596 | 71.0514 | 71.5068 | 71.9621 | 72.4175 | 72.8729 | 73.3283 | 73.7837 | 74.239 | 74.6944 | 75.1498 | 75.6052 | 76.0605 | 76.5159 | 76.9713 | 77.4267 | 77.882 | 78.3374 | 78.7928 | 79.2482 | 79.7036 | 80.1589 | 80.6143 | 81.0697 | 81.5251 | 81.9804 | 82.4358 | 82.8912 | 83.3466 | 83.802 | 84.2573 | 84.7127 | 85.1681 | 85.6235 | 86.0788 | 86.5342 | 86.9896 | 87.445 | 87.9003 | 88.3557 | 88.8111
Enersys Powersafe EON SBS 580 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6265 | 1.6144 | 1.7187 | 1.823 | 1.9735 | 2.124 | 2.2745 | 3.2221 | 4.1697 | 6.0333 | 6.4945 | 6.9556 | 7.4098 | 7.864 | 8.2997 | 8.7353 | 9.1805 | 9.6258 | 10.0533 | 10.4808 | 10.9374 | 11.394 | 11.8506 | 12.3072 | 12.7638 | 13.2204 | 13.6769 | 14.1335 | 14.5901 | 15.0467 | 15.5033 | 15.9599 | 16.4165 | 16.8731 | 17.3297 | 17.7863 | 18.2428 | 18.6994 | 19.156 | 19.6126 | 20.0692 | 20.5258 | 20.9824 | 21.439 | 21.8956 | 22.3522 | 22.8087 | 23.2653 | 23.7219 | 24.1785 | 24.6351 | 25.0917 | 25.5483 | 26.0049 | 26.4615 | 26.9181 | 27.3746 | 27.8312 | 28.2878 | 28.7444 | 29.201 | 29.6576 | 30.1142 | 30.5708 | 31.0274 | 31.484 | 31.9405 | 32.3971 | 32.8537 | 33.3103 | 33.7669 | 34.2235 | 34.6801 | 35.1367 | 35.5933 | 36.0499 | 36.5064 | 36.963 | 37.4196 | 37.8762 | 38.3328 | 38.7894 | 39.246 | 39.7026 | 40.1592 | 40.6158 | 41.0723 | 41.5289 | 41.9855 | 42.4421 | 42.8987 | 43.3553 | 43.8119 | 44.2685 | 44.7251 | 45.1817 | 45.6382 | 46.0948 | 46.5514 | 47.008 | 47.4646 | 47.9212 | 48.3778 | 48.8344 | 49.291 | 49.7476 | 50.2041 | 50.6607 | 51.1173 | 51.5739 | 52.0305 | 52.4871 | 52.9437 | 53.4003 | 53.8569 | 54.3135 | 54.77 | 55.2266 | 55.6832 | 56.1398 | 56.5964 | 57.053 | 57.5096 | 57.9662 | 58.4228 | 58.8794 | 59.3359 | 59.7925 | 60.2491 | 60.7057 | 61.1623 | 61.6189 | 62.0755 | 62.5321 | 62.9887 | 63.4453 | 63.9018 | 64.3584 | 64.815 | 65.2716 | 65.7282 | 66.1848 | 66.6414 | 67.098 | 67.5546 | 68.0112 | 68.4677 | 68.9243 | 69.3809 | 69.8375 | 70.2941 | 70.7507 | 71.2073 | 71.6639 | 72.1205 | 72.5771 | 73.0336 | 73.4902 | 73.9468 | 74.4034 | 74.86 | 75.3166 | 75.7732 | 76.2298 | 76.6864 | 77.143 | 77.5996 | 78.0561 | 78.5127 | 78.9693 | 79.4259 | 79.8825 | 80.3391 | 80.7957 | 81.2523 | 81.7089 | 82.1655 | 82.622 | 83.0786 | 83.5352 | 83.9918 | 84.4484 | 84.905 | 85.3616 | 85.8182 | 86.2748 | 86.7314 | 87.1879 | 87.6445 | 88.1011 | 88.5577 | 89.0143
Enersys Powersafe EON SBS 680 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6261 | 1.6144 | 1.7188 | 1.8232 | 1.9735 | 2.1238 | 2.2741 | 3.2222 | 4.1703 | 6.0299 | 6.4919 | 6.9539 | 7.4076 | 7.8613 | 8.3005 | 8.7398 | 9.1798 | 9.6198 | 10.0484 | 10.477 | 10.9317 | 11.3864 | 11.8411 | 12.2958 | 12.7505 | 13.2052 | 13.6598 | 14.1145 | 14.5692 | 15.0239 | 15.4786 | 15.9333 | 16.388 | 16.8427 | 17.2974 | 17.7521 | 18.2068 | 18.6614 | 19.1161 | 19.5708 | 20.0255 | 20.4802 | 20.9349 | 21.3896 | 21.8443 | 22.299 | 22.7537 | 23.2083 | 23.663 | 24.1177 | 24.5724 | 25.0271 | 25.4818 | 25.9365 | 26.3912 | 26.8459 | 27.3006 | 27.7553 | 28.2099 | 28.6646 | 29.1193 | 29.574 | 30.0287 | 30.4834 | 30.9381 | 31.3928 | 31.8475 | 32.3022 | 32.7568 | 33.2115 | 33.6662 | 34.1209 | 34.5756 | 35.0303 | 35.485 | 35.9397 | 36.3944 | 36.8491 | 37.3038 | 37.7584 | 38.2131 | 38.6678 | 39.1225 | 39.5772 | 40.0319 | 40.4866 | 40.9413 | 41.396 | 41.8507 | 42.3054 | 42.76 | 43.2147 | 43.6694 | 44.1241 | 44.5788 | 45.0335 | 45.4882 | 45.9429 | 46.3976 | 46.8523 | 47.3069 | 47.7616 | 48.2163 | 48.671 | 49.1257 | 49.5804 | 50.0351 | 50.4898 | 50.9445 | 51.3992 | 51.8539 | 52.3085 | 52.7632 | 53.2179 | 53.6726 | 54.1273 | 54.582 | 55.0367 | 55.4914 | 55.9461 | 56.4008 | 56.8554 | 57.3101 | 57.7648 | 58.2195 | 58.6742 | 59.1289 | 59.5836 | 60.0383 | 60.493 | 60.9477 | 61.4024 | 61.857 | 62.3117 | 62.7664 | 63.2211 | 63.6758 | 64.1305 | 64.5852 | 65.0399 | 65.4946 | 65.9493 | 66.404 | 66.8586 | 67.3133 | 67.768 | 68.2227 | 68.6774 | 69.1321 | 69.5868 | 70.0415 | 70.4962 | 70.9509 | 71.4055 | 71.8602 | 72.3149 | 72.7696 | 73.2243 | 73.679 | 74.1337 | 74.5884 | 75.0431 | 75.4978 | 75.9525 | 76.4071 | 76.8618 | 77.3165 | 77.7712 | 78.2259 | 78.6806 | 79.1353 | 79.59 | 80.0447 | 80.4994 | 80.954 | 81.4087 | 81.8634 | 82.3181 | 82.7728 | 83.2275 | 83.6822 | 84.1369 | 84.5916 | 85.0463 | 85.501 | 85.9556 | 86.4103 | 86.865 | 87.3197 | 87.7744 | 88.2291 | 88.6838
Enersys Powersafe EON SBS 780 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6262 | 1.6144 | 1.7187 | 1.8229 | 1.9734 | 2.124 | 2.2745 | 3.2226 | 4.1708 | 6.0319 | 6.4923 | 6.9527 | 7.406 | 7.8593 | 8.2964 | 8.7336 | 9.1745 | 9.6154 | 10.0517 | 10.4879 | 10.9429 | 11.3979 | 11.8529 | 12.3079 | 12.7629 | 13.2179 | 13.6729 | 14.1279 | 14.5829 | 15.0378 | 15.4928 | 15.9478 | 16.4028 | 16.8578 | 17.3128 | 17.7678 | 18.2228 | 18.6778 | 19.1328 | 19.5878 | 20.0427 | 20.4977 | 20.9527 | 21.4077 | 21.8627 | 22.3177 | 22.7727 | 23.2277 | 23.6827 | 24.1377 | 24.5927 | 25.0476 | 25.5026 | 25.9576 | 26.4126 | 26.8676 | 27.3226 | 27.7776 | 28.2326 | 28.6876 | 29.1426 | 29.5976 | 30.0525 | 30.5075 | 30.9625 | 31.4175 | 31.8725 | 32.3275 | 32.7825 | 33.2375 | 33.6925 | 34.1475 | 34.6025 | 35.0575 | 35.5124 | 35.9674 | 36.4224 | 36.8774 | 37.3324 | 37.7874 | 38.2424 | 38.6974 | 39.1524 | 39.6074 | 40.0624 | 40.5173 | 40.9723 | 41.4273 | 41.8823 | 42.3373 | 42.7923 | 43.2473 | 43.7023 | 44.1573 | 44.6123 | 45.0673 | 45.5222 | 45.9772 | 46.4322 | 46.8872 | 47.3422 | 47.7972 | 48.2522 | 48.7072 | 49.1622 | 49.6172 | 50.0722 | 50.5271 | 50.9821 | 51.4371 | 51.8921 | 52.3471 | 52.8021 | 53.2571 | 53.7121 | 54.1671 | 54.6221 | 55.0771 | 55.5321 | 55.987 | 56.442 | 56.897 | 57.352 | 57.807 | 58.262 | 58.717 | 59.172 | 59.627 | 60.082 | 60.537 | 60.9919 | 61.4469 | 61.9019 | 62.3569 | 62.8119 | 63.2669 | 63.7219 | 64.1769 | 64.6319 | 65.0869 | 65.5419 | 65.9968 | 66.4518 | 66.9068 | 67.3618 | 67.8168 | 68.2718 | 68.7268 | 69.1818 | 69.6368 | 70.0918 | 70.5468 | 71.0017 | 71.4567 | 71.9117 | 72.3667 | 72.8217 | 73.2767 | 73.7317 | 74.1867 | 74.6417 | 75.0967 | 75.5517 | 76.0067 | 76.4616 | 76.9166 | 77.3716 | 77.8266 | 78.2816 | 78.7366 | 79.1916 | 79.6466 | 80.1016 | 80.5566 | 81.0116 | 81.4665 | 81.9215 | 82.3765 | 82.8315 | 83.2865 | 83.7415 | 84.1965 | 84.6515 | 85.1065 | 85.5615 | 86.0165 | 86.4714 | 86.9264 | 87.3814 | 87.8364 | 88.2914 | 88.7464
Enersys Powersafe EON SBS 900 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6264 | 1.6143 | 1.7193 | 1.8243 | 1.9748 | 2.1252 | 2.2756 | 3.2238 | 4.1719 | 6.0338 | 6.4942 | 6.9547 | 7.4067 | 7.8587 | 8.2959 | 8.733 | 9.1792 | 9.6254 | 10.058 | 10.4907 | 10.9451 | 11.3994 | 11.8538 | 12.3082 | 12.7626 | 13.2169 | 13.6713 | 14.1257 | 14.58 | 15.0344 | 15.4888 | 15.9432 | 16.3975 | 16.8519 | 17.3063 | 17.7607 | 18.215 | 18.6694 | 19.1238 | 19.5782 | 20.0325 | 20.4869 | 20.9413 | 21.3957 | 21.85 | 22.3044 | 22.7588 | 23.2131 | 23.6675 | 24.1219 | 24.5763 | 25.0306 | 25.485 | 25.9394 | 26.3938 | 26.8481 | 27.3025 | 27.7569 | 28.2113 | 28.6656 | 29.12 | 29.5744 | 30.0287 | 30.4831 | 30.9375 | 31.3919 | 31.8462 | 32.3006 | 32.755 | 33.2094 | 33.6637 | 34.1181 | 34.5725 | 35.0269 | 35.4812 | 35.9356 | 36.39 | 36.8444 | 37.2987 | 37.7531 | 38.2075 | 38.6618 | 39.1162 | 39.5706 | 40.025 | 40.4793 | 40.9337 | 41.3881 | 41.8425 | 42.2968 | 42.7512 | 43.2056 | 43.66 | 44.1143 | 44.5687 | 45.0231 | 45.4775 | 45.9318 | 46.3862 | 46.8406 | 47.2949 | 47.7493 | 48.2037 | 48.6581 | 49.1124 | 49.5668 | 50.0212 | 50.4756 | 50.9299 | 51.3843 | 51.8387 | 52.2931 | 52.7474 | 53.2018 | 53.6562 | 54.1105 | 54.5649 | 55.0193 | 55.4737 | 55.928 | 56.3824 | 56.8368 | 57.2912 | 57.7455 | 58.1999 | 58.6543 | 59.1087 | 59.563 | 60.0174 | 60.4718 | 60.9262 | 61.3805 | 61.8349 | 62.2893 | 62.7436 | 63.198 | 63.6524 | 64.1068 | 64.5611 | 65.0155 | 65.4699 | 65.9243 | 66.3786 | 66.833 | 67.2874 | 67.7418 | 68.1961 | 68.6505 | 69.1049 | 69.5593 | 70.0136 | 70.468 | 70.9224 | 71.3767 | 71.8311 | 72.2855 | 72.7399 | 73.1942 | 73.6486 | 74.103 | 74.5574 | 75.0117 | 75.4661 | 75.9205 | 76.3749 | 76.8292 | 77.2836 | 77.738 | 78.1923 | 78.6467 | 79.1011 | 79.5555 | 80.0098 | 80.4642 | 80.9186 | 81.373 | 81.8273 | 82.2817 | 82.7361 | 83.1905 | 83.6448 | 84.0992 | 84.5536 | 85.008 | 85.4623 | 85.9167 | 86.3711 | 86.8254 | 87.2798 | 87.7342 | 88.1886 | 88.6429
Enersys Powersafe EON SBS B14 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.46245 | 0.57077 | 0.72069 | 0.87061 | 1.085 | 1.2994 | 1.5138 | 2.4948 | 3.4759 | 5.4198 | 5.919 | 6.4182 | 6.9045 | 7.3907 | 7.8641 | 8.3376 | 8.8219 | 9.3062 | 9.776 | 10.2459 | 10.7152 | 11.1846 | 11.6539 | 12.1233 | 12.5926 | 13.0619 | 13.5313 | 14.0006 | 14.4699 | 14.9393 | 15.4086 | 15.878 | 16.3473 | 16.8166 | 17.286 | 17.7553 | 18.2247 | 18.694 | 19.1633 | 19.6327 | 20.102 | 20.5714 | 21.0407 | 21.51 | 21.9794 | 22.4487 | 22.918 | 23.3874 | 23.8567 | 24.3261 | 24.7954 | 25.2647 | 25.7341 | 26.2034 | 26.6728 | 27.1421 | 27.6114 | 28.0808 | 28.5501 | 29.0194 | 29.4888 | 29.9581 | 30.4275 | 30.8968 | 31.3661 | 31.8355 | 32.3048 | 32.7742 | 33.2435 | 33.7128 | 34.1822 | 34.6515 | 35.1209 | 35.5902 | 36.0595 | 36.5289 | 36.9982 | 37.4675 | 37.9369 | 38.4062 | 38.8756 | 39.3449 | 39.8142 | 40.2836 | 40.7529 | 41.2223 | 41.6916 | 42.1609 | 42.6303 | 43.0996 | 43.5689 | 44.0383 | 44.5076 | 44.977 | 45.4463 | 45.9156 | 46.385 | 46.8543 | 47.3237 | 47.793 | 48.2623 | 48.7317 | 49.201 | 49.6703 | 50.1397 | 50.609 | 51.0784 | 51.5477 | 52.017 | 52.4864 | 52.9557 | 53.4251 | 53.8944 | 54.3637 | 54.8331 | 55.3024 | 55.7718 | 56.2411 | 56.7104 | 57.1798 | 57.6491 | 58.1184 | 58.5878 | 59.0571 | 59.5265 | 59.9958 | 60.4651 | 60.9345 | 61.4038 | 61.8732 | 62.3425 | 62.8118 | 63.2812 | 63.7505 | 64.2198 | 64.6892 | 65.1585 | 65.6279 | 66.0972 | 66.5665 | 67.0359 | 67.5052 | 67.9746 | 68.4439 | 68.9132 | 69.3826 | 69.8519 | 70.3213 | 70.7906 | 71.2599 | 71.7293 | 72.1986 | 72.6679 | 73.1373 | 73.6066 | 74.076 | 74.5453 | 75.0146 | 75.484 | 75.9533 | 76.4227 | 76.892 | 77.3613 | 77.8307 | 78.3 | 78.7693 | 79.2387 | 79.708 | 80.1774 | 80.6467 | 81.116 | 81.5854 | 82.0547 | 82.5241 | 82.9934 | 83.4627 | 83.9321 | 84.4014 | 84.8707 | 85.3401 | 85.8094 | 86.2788 | 86.7481 | 87.2174 | 87.6868 | 88.1561 | 88.6255 | 89.0948 | 89.5641 | 90.0335 | 90.5028 | 90.9722
Enersys Powersafe EON SBS B14F | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.34787 | 0.46245 | 0.57077 | 0.72069 | 0.87061 | 1.085 | 1.2994 | 1.5138 | 2.4948 | 3.4759 | 5.4198 | 5.919 | 6.4182 | 6.9045 | 7.3907 | 7.8641 | 8.3376 | 8.8219 | 9.3062 | 9.776 | 10.2459 | 10.7152 | 11.1846 | 11.6539 | 12.1233 | 12.5926 | 13.0619 | 13.5313 | 14.0006 | 14.4699 | 14.9393 | 15.4086 | 15.878 | 16.3473 | 16.8166 | 17.286 | 17.7553 | 18.2247 | 18.694 | 19.1633 | 19.6327 | 20.102 | 20.5714 | 21.0407 | 21.51 | 21.9794 | 22.4487 | 22.918 | 23.3874 | 23.8567 | 24.3261 | 24.7954 | 25.2647 | 25.7341 | 26.2034 | 26.6728 | 27.1421 | 27.6114 | 28.0808 | 28.5501 | 29.0194 | 29.4888 | 29.9581 | 30.4275 | 30.8968 | 31.3661 | 31.8355 | 32.3048 | 32.7742 | 33.2435 | 33.7128 | 34.1822 | 34.6515 | 35.1209 | 35.5902 | 36.0595 | 36.5289 | 36.9982 | 37.4675 | 37.9369 | 38.4062 | 38.8756 | 39.3449 | 39.8142 | 40.2836 | 40.7529 | 41.2223 | 41.6916 | 42.1609 | 42.6303 | 43.0996 | 43.5689 | 44.0383 | 44.5076 | 44.977 | 45.4463 | 45.9156 | 46.385 | 46.8543 | 47.3237 | 47.793 | 48.2623 | 48.7317 | 49.201 | 49.6703 | 50.1397 | 50.609 | 51.0784 | 51.5477 | 52.017 | 52.4864 | 52.9557 | 53.4251 | 53.8944 | 54.3637 | 54.8331 | 55.3024 | 55.7718 | 56.2411 | 56.7104 | 57.1798 | 57.6491 | 58.1184 | 58.5878 | 59.0571 | 59.5265 | 59.9958 | 60.4651 | 60.9345 | 61.4038 | 61.8732 | 62.3425 | 62.8118 | 63.2812 | 63.7505 | 64.2198 | 64.6892 | 65.1585 | 65.6279 | 66.0972 | 66.5665 | 67.0359 | 67.5052 | 67.9746 | 68.4439 | 68.9132 | 69.3826 | 69.8519 | 70.3213 | 70.7906 | 71.2599 | 71.7293 | 72.1986 | 72.6679 | 73.1373 | 73.6066 | 74.076 | 74.5453 | 75.0146 | 75.484 | 75.9533 | 76.4227 | 76.892 | 77.3613 | 77.8307 | 78.3 | 78.7693 | 79.2387 | 79.708 | 80.1774 | 80.6467 | 81.116 | 81.5854 | 82.0547 | 82.5241 | 82.9934 | 83.4627 | 83.9321 | 84.4014 | 84.8707 | 85.3401 | 85.8094 | 86.2788 | 86.7481 | 87.2174 | 87.6868 | 88.1561 | 88.6255 | 89.0948 | 89.5641 | 90.0335 | 90.5028 | 90.9722
Enersys Powersafe EON SBS C11 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.53299 | 0.65329 | 0.82108 | 0.98887 | 1.192 | 1.3951 | 1.5982 | 2.6933 | 3.7883 | 5.8409 | 6.3277 | 6.8144 | 7.2931 | 7.7718 | 8.1132 | 8.4546 | 8.9196 | 9.3846 | 9.8548 | 10.3249 | 10.7614 | 11.1979 | 11.6344 | 12.0709 | 12.5074 | 12.9439 | 13.3804 | 13.8169 | 14.2534 | 14.6899 | 15.1264 | 15.5629 | 15.9994 | 16.4359 | 16.8724 | 17.3089 | 17.7454 | 18.1819 | 18.6184 | 19.0549 | 19.4914 | 19.9279 | 20.3644 | 20.8009 | 21.2374 | 21.6739 | 22.1104 | 22.5469 | 22.9834 | 23.4199 | 23.8564 | 24.2929 | 24.7294 | 25.1659 | 25.6024 | 26.0389 | 26.4754 | 26.9119 | 27.3484 | 27.7849 | 28.2214 | 28.6579 | 29.0944 | 29.5309 | 29.9674 | 30.4039 | 30.8404 | 31.2769 | 31.7134 | 32.1499 | 32.5864 | 33.0229 | 33.4594 | 33.8959 | 34.3324 | 34.7689 | 35.2054 | 35.6419 | 36.0784 | 36.5149 | 36.9514 | 37.3879 | 37.8244 | 38.2609 | 38.6974 | 39.1339 | 39.5704 | 40.0068 | 40.4433 | 40.8798 | 41.3163 | 41.7528 | 42.1893 | 42.6258 | 43.0623 | 43.4988 | 43.9353 | 44.3718 | 44.8083 | 45.2448 | 45.6813 | 46.1178 | 46.5543 | 46.9908 | 47.4273 | 47.8638 | 48.3003 | 48.7368 | 49.1733 | 49.6098 | 50.0463 | 50.4828 | 50.9193 | 51.3558 | 51.7923 | 52.2288 | 52.6653 | 53.1018 | 53.5383 | 53.9748 | 54.4113 | 54.8478 | 55.2843 | 55.7208 | 56.1573 | 56.5938 | 57.0303 | 57.4668 | 57.9033 | 58.3398 | 58.7763 | 59.2128 | 59.6493 | 60.0858 | 60.5223 | 60.9588 | 61.3953 | 61.8318 | 62.2683 | 62.7048 | 63.1413 | 63.5778 | 64.0143 | 64.4508 | 64.8873 | 65.3238 | 65.7603 | 66.1968 | 66.6333 | 67.0698 | 67.5063 | 67.9428 | 68.3793 | 68.8158 | 69.2523 | 69.6888 | 70.1253 | 70.5618 | 70.9983 | 71.4348 | 71.8713 | 72.3078 | 72.7443 | 73.1808 | 73.6173 | 74.0538 | 74.4903 | 74.9268 | 75.3633 | 75.7998 | 76.2363 | 76.6728 | 77.1093 | 77.5458 | 77.9823 | 78.4188 | 78.8553 | 79.2918 | 79.7283 | 80.1648 | 80.6013 | 81.0378 | 81.4743 | 81.9108 | 82.3473 | 82.7838 | 83.2203 | 83.6568 | 84.0933 | 84.5298 | 84.9663 | 85.4028
Enersys Powersafe EON SBS C11F | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.40147 | 0.53299 | 0.65329 | 0.82108 | 0.98887 | 1.192 | 1.3951 | 1.5982 | 2.6933 | 3.7883 | 5.8409 | 6.3277 | 6.8144 | 7.2931 | 7.7718 | 8.1132 | 8.4546 | 8.9196 | 9.3846 | 9.8548 | 10.3249 | 10.7614 | 11.1979 | 11.6344 | 12.0709 | 12.5074 | 12.9439 | 13.3804 | 13.8169 | 14.2534 | 14.6899 | 15.1264 | 15.5629 | 15.9994 | 16.4359 | 16.8724 | 17.3089 | 17.7454 | 18.1819 | 18.6184 | 19.0549 | 19.4914 | 19.9279 | 20.3644 | 20.8009 | 21.2374 | 21.6739 | 22.1104 | 22.5469 | 22.9834 | 23.4199 | 23.8564 | 24.2929 | 24.7294 | 25.1659 | 25.6024 | 26.0389 | 26.4754 | 26.9119 | 27.3484 | 27.7849 | 28.2214 | 28.6579 | 29.0944 | 29.5309 | 29.9674 | 30.4039 | 30.8404 | 31.2769 | 31.7134 | 32.1499 | 32.5864 | 33.0229 | 33.4594 | 33.8959 | 34.3324 | 34.7689 | 35.2054 | 35.6419 | 36.0784 | 36.5149 | 36.9514 | 37.3879 | 37.8244 | 38.2609 | 38.6974 | 39.1339 | 39.5704 | 40.0068 | 40.4433 | 40.8798 | 41.3163 | 41.7528 | 42.1893 | 42.6258 | 43.0623 | 43.4988 | 43.9353 | 44.3718 | 44.8083 | 45.2448 | 45.6813 | 46.1178 | 46.5543 | 46.9908 | 47.4273 | 47.8638 | 48.3003 | 48.7368 | 49.1733 | 49.6098 | 50.0463 | 50.4828 | 50.9193 | 51.3558 | 51.7923 | 52.2288 | 52.6653 | 53.1018 | 53.5383 | 53.9748 | 54.4113 | 54.8478 | 55.2843 | 55.7208 | 56.1573 | 56.5938 | 57.0303 | 57.4668 | 57.9033 | 58.3398 | 58.7763 | 59.2128 | 59.6493 | 60.0858 | 60.5223 | 60.9588 | 61.3953 | 61.8318 | 62.2683 | 62.7048 | 63.1413 | 63.5778 | 64.0143 | 64.4508 | 64.8873 | 65.3238 | 65.7603 | 66.1968 | 66.6333 | 67.0698 | 67.5063 | 67.9428 | 68.3793 | 68.8158 | 69.2523 | 69.6888 | 70.1253 | 70.5618 | 70.9983 | 71.4348 | 71.8713 | 72.3078 | 72.7443 | 73.1808 | 73.6173 | 74.0538 | 74.4903 | 74.9268 | 75.3633 | 75.7998 | 76.2363 | 76.6728 | 77.1093 | 77.5458 | 77.9823 | 78.4188 | 78.8553 | 79.2918 | 79.7283 | 80.1648 | 80.6013 | 81.0378 | 81.4743 | 81.9108 | 82.3473 | 82.7838 | 83.2203 | 83.6568 | 84.0933 | 84.5298 | 84.9663 | 85.4028
1
Kt: 1.85V/Cell @ 5degC |  | 1s | 5s | 30s | 60s | 3m | 5m | 10m | 15m | 20m | 30m | 40m | 50m | 1h | 1.5h | 3h | 5h | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
Time | 0 | 0.00032777 | 0.0014389 | 0.0083833 | 0.016717 | 0.05005 | 0.083383 | 0.16672 | 0.25005 | 0.33338 | 0.50005 | 0.66672 | 0.83338 | 1 | 1.5 | 3 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200
Enersys Powersafe EON SBS 100 | 0.51926 | 0.51926 | 0.51926 | 0.51926 | 0.51926 | 0.51926 | 0.51926 | 0.64177 | 0.76303 | 0.93215 | 1.1013 | 1.309 | 1.5166 | 1.7243 | 2.8477 | 3.971 | 6.105 | 6.6138 | 7.1225 | 7.6164 | 8.1103 | 8.6289 | 9.1475 | 9.6556 | 10.1638 | 10.6301 | 11.0963 | 11.5756 | 12.0549 | 12.5342 | 13.0135 | 13.4928 | 13.9721 | 14.4514 | 14.9307 | 15.41 | 15.8893 | 16.3686 | 16.8479 | 17.3272 | 17.8065 | 18.2858 | 18.7651 | 19.2444 | 19.7237 | 20.203 | 20.6823 | 21.1616 | 21.6409 | 22.1202 | 22.5995 | 23.0788 | 23.5581 | 24.0374 | 24.5167 | 24.996 | 25.4753 | 25.9546 | 26.4339 | 26.9132 | 27.3925 | 27.8718 | 28.3511 | 28.8304 | 29.3097 | 29.789 | 30.2683 | 30.7476 | 31.2269 | 31.7062 | 32.1855 | 32.6648 | 33.1441 | 33.6234 | 34.1027 | 34.582 | 35.0613 | 35.5406 | 36.0199 | 36.4992 | 36.9785 | 37.4578 | 37.9371 | 38.4164 | 38.8957 | 39.375 | 39.8543 | 40.3336 | 40.8129 | 41.2922 | 41.7715 | 42.2508 | 42.7301 | 43.2094 | 43.6887 | 44.168 | 44.6473 | 45.1266 | 45.6059 | 46.0852 | 46.5645 | 47.0438 | 47.5231 | 48.0024 | 48.4817 | 48.961 | 49.4403 | 49.9196 | 50.3989 | 50.8782 | 51.3575 | 51.8368 | 52.3161 | 52.7954 | 53.2747 | 53.754 | 54.2333 | 54.7126 | 55.1919 | 55.6712 | 56.1505 | 56.6298 | 57.1091 | 57.5884 | 58.0677 | 58.547 | 59.0263 | 59.5056 | 59.9849 | 60.4642 | 60.9435 | 61.4228 | 61.9021 | 62.3814 | 62.8607 | 63.34 | 63.8193 | 64.2986 | 64.7779 | 65.2572 | 65.7365 | 66.2158 | 66.6951 | 67.1744 | 67.6537 | 68.133 | 68.6123 | 69.0916 | 69.5709 | 70.0502 | 70.5295 | 71.0088 | 71.4881 | 71.9674 | 72.4467 | 72.926 | 73.4053 | 73.8846 | 74.3639 | 74.8432 | 75.3225 | 75.8018 | 76.2811 | 76.7604 | 77.2397 | 77.719 | 78.1983 | 78.6776 | 79.1569 | 79.6362 | 80.1155 | 80.5948 | 81.0741 | 81.5534 | 82.0327 | 82.512 | 82.9913 | 83.4706 | 83.9499 | 84.4292 | 84.9085 | 85.3878 | 85.8671 | 86.3464 | 86.8257 | 87.305 | 87.7843 | 88.2636 | 88.7429 | 89.2222 | 89.7015 | 90.1808 | 90.6601 | 91.1394 | 91.6187 | 92.098 | 92.5773 | 93.0566 | 93.5359
Enersys Powersafe EON SBS 100F | 0.51926 | 0.51926 | 0.51926 | 0.51926 | 0.51926 | 0.51926 | 0.51926 | 0.64177 | 0.76303 | 0.93215 | 1.1013 | 1.309 | 1.5166 | 1.7243 | 2.8477 | 3.971 | 6.105 | 6.6138 | 7.1225 | 7.6164 | 8.1103 | 8.6289 | 9.1475 | 9.6556 | 10.1638 | 10.6301 | 11.0963 | 11.5756 | 12.0549 | 12.5342 | 13.0135 | 13.4928 | 13.9721 | 14.4514 | 14.9307 | 15.41 | 15.8893 | 16.3686 | 16.8479 | 17.3272 | 17.8065 | 18.2858 | 18.7651 | 19.2444 | 19.7237 | 20.203 | 20.6823 | 21.1616 | 21.6409 | 22.1202 | 22.5995 | 23.0788 | 23.5581 | 24.0374 | 24.5167 | 24.996 | 25.4753 | 25.9546 | 26.4339 | 26.9132 | 27.3925 | 27.8718 | 28.3511 | 28.8304 | 29.3097 | 29.789 | 30.2683 | 30.7476 | 31.2269 | 31.7062 | 32.1855 | 32.6648 | 33.1441 | 33.6234 | 34.1027 | 34.582 | 35.0613 | 35.5406 | 36.0199 | 36.4992 | 36.9785 | 37.4578 | 37.9371 | 38.4164 | 38.8957 | 39.375 | 39.8543 | 40.3336 | 40.8129 | 41.2922 | 41.7715 | 42.2508 | 42.7301 | 43.2094 | 43.6887 | 44.168 | 44.6473 | 45.1266 | 45.6059 | 46.0852 | 46.5645 | 47.0438 | 47.5231 | 48.0024 | 48.4817 | 48.961 | 49.4403 | 49.9196 | 50.3989 | 50.8782 | 51.3575 | 51.8368 | 52.3161 | 52.7954 | 53.2747 | 53.754 | 54.2333 | 54.7126 | 55.1919 | 55.6712 | 56.1505 | 56.6298 | 57.1091 | 57.5884 | 58.0677 | 58.547 | 59.0263 | 59.5056 | 59.9849 | 60.4642 | 60.9435 | 61.4228 | 61.9021 | 62.3814 | 62.8607 | 63.34 | 63.8193 | 64.2986 | 64.7779 | 65.2572 | 65.7365 | 66.2158 | 66.6951 | 67.1744 | 67.6537 | 68.133 | 68.6123 | 69.0916 | 69.5709 | 70.0502 | 70.5295 | 71.0088 | 71.4881 | 71.9674 | 72.4467 | 72.926 | 73.4053 | 73.8846 | 74.3639 | 74.8432 | 75.3225 | 75.8018 | 76.2811 | 76.7604 | 77.2397 | 77.719 | 78.1983 | 78.6776 | 79.1569 | 79.6362 | 80.1155 | 80.5948 | 81.0741 | 81.5534 | 82.0327 | 82.512 | 82.9913 | 83.4706 | 83.9499 | 84.4292 | 84.9085 | 85.3878 | 85.8671 | 86.3464 | 86.8257 | 87.305 | 87.7843 | 88.2636 | 88.7429 | 89.2222 | 89.7015 | 90.1808 | 90.6601 | 91.1394 | 91.6187 | 92.098 | 92.5773 | 93.0566 | 93.5359
Enersys Powersafe EON SBS 170F | 0.74243 | 0.74243 | 0.74243 | 0.74243 | 0.74243 | 0.74243 | 0.74243 | 0.71255 | 0.82653 | 0.99249 | 1.1584 | 1.3655 | 1.5725 | 1.7795 | 2.9149 | 4.0504 | 6.234 | 6.7776 | 7.3213 | 7.8396 | 8.3579 | 8.8442 | 9.3304 | 9.8488 | 10.3671 | 10.8542 | 11.3412 | 11.8144 | 12.2876 | 12.7607 | 13.2339 | 13.7071 | 14.1803 | 14.6535 | 15.1267 | 15.5999 | 16.073 | 16.5462 | 17.0194 | 17.4926 | 17.9658 | 18.439 | 18.9121 | 19.3853 | 19.8585 | 20.3317 | 20.8049 | 21.2781 | 21.7512 | 22.2244 | 22.6976 | 23.1708 | 23.644 | 24.1172 | 24.5904 | 25.0635 | 25.5367 | 26.0099 | 26.4831 | 26.9563 | 27.4295 | 27.9026 | 28.3758 | 28.849 | 29.3222 | 29.7954 | 30.2686 | 30.7417 | 31.2149 | 31.6881 | 32.1613 | 32.6345 | 33.1077 | 33.5809 | 34.054 | 34.5272 | 35.0004 | 35.4736 | 35.9468 | 36.42 | 36.8931 | 37.3663 | 37.8395 | 38.3127 | 38.7859 | 39.2591 | 39.7322 | 40.2054 | 40.6786 | 41.1518 | 41.625 | 42.0982 | 42.5714 | 43.0445 | 43.5177 | 43.9909 | 44.4641 | 44.9373 | 45.4105 | 45.8836 | 46.3568 | 46.83 | 47.3032 | 47.7764 | 48.2496 | 48.7227 | 49.1959 | 49.6691 | 50.1423 | 50.6155 | 51.0887 | 51.5618 | 52.035 | 52.5082 | 52.9814 | 53.4546 | 53.9278 | 54.401 | 54.8741 | 55.3473 | 55.8205 | 56.2937 | 56.7669 | 57.2401 | 57.7132 | 58.1864 | 58.6596 | 59.1328 | 59.606 | 60.0792 | 60.5523 | 61.0255 | 61.4987 | 61.9719 | 62.4451 | 62.9183 | 63.3915 | 63.8646 | 64.3378 | 64.811 | 65.2842 | 65.7574 | 66.2306 | 66.7037 | 67.1769 | 67.6501 | 68.1233 | 68.5965 | 69.0697 | 69.5428 | 70.016 | 70.4892 | 70.9624 | 71.4356 | 71.9088 | 72.382 | 72.8551 | 73.3283 | 73.8015 | 74.2747 | 74.7479 | 75.2211 | 75.6942 | 76.1674 | 76.6406 | 77.1138 | 77.587 | 78.0602 | 78.5333 | 79.0065 | 79.4797 | 79.9529 | 80.4261 | 80.8993 | 81.3725 | 81.8456 | 82.3188 | 82.792 | 83.2652 | 83.7384 | 84.2116 | 84.6847 | 85.1579 | 85.6311 | 86.1043 | 86.5775 | 87.0507 | 87.5238 | 87.997 | 88.4702 | 88.9434 | 89.4166 | 89.8898 | 90.3629 | 90.8361 | 91.3093 | 91.7825 | 92.2557 | 92.7289
Enersys Powersafe EON SBS 190F | 0.72961 | 0.72961 | 0.72961 | 0.72961 | 0.72961 | 0.72961 | 0.72961 | 0.70025 | 0.81558 | 0.98393 | 1.1523 | 1.3643 | 1.5764 | 1.7885 | 2.9167 | 4.045 | 6.2275 | 6.7662 | 7.3049 | 7.8246 | 8.3443 | 8.8069 | 9.2694 | 9.7717 | 10.274 | 10.7553 | 11.2366 | 11.7039 | 12.1712 | 12.6384 | 13.1057 | 13.5729 | 14.0402 | 14.5075 | 14.9747 | 15.442 | 15.9093 | 16.3765 | 16.8438 | 17.3111 | 17.7783 | 18.2456 | 18.7129 | 19.1801 | 19.6474 | 20.1147 | 20.5819 | 21.0492 | 21.5165 | 21.9837 | 22.451 | 22.9183 | 23.3855 | 23.8528 | 24.32 | 24.7873 | 25.2546 | 25.7218 | 26.1891 | 26.6564 | 27.1236 | 27.5909 | 28.0582 | 28.5254 | 28.9927 | 29.46 | 29.9272 | 30.3945 | 30.8618 | 31.329 | 31.7963 | 32.2636 | 32.7308 | 33.1981 | 33.6654 | 34.1326 | 34.5999 | 35.0672 | 35.5344 | 36.0017 | 36.4689 | 36.9362 | 37.4035 | 37.8707 | 38.338 | 38.8053 | 39.2725 | 39.7398 | 40.2071 | 40.6743 | 41.1416 | 41.6089 | 42.0761 | 42.5434 | 43.0107 | 43.4779 | 43.9452 | 44.4125 | 44.8797 | 45.347 | 45.8143 | 46.2815 | 46.7488 | 47.2161 | 47.6833 | 48.1506 | 48.6178 | 49.0851 | 49.5524 | 50.0196 | 50.4869 | 50.9542 | 51.4214 | 51.8887 | 52.356 | 52.8232 | 53.2905 | 53.7578 | 54.225 | 54.6923 | 55.1596 | 55.6268 | 56.0941 | 56.5614 | 57.0286 | 57.4959 | 57.9632 | 58.4304 | 58.8977 | 59.365 | 59.8322 | 60.2995 | 60.7667 | 61.234 | 61.7013 | 62.1685 | 62.6358 | 63.1031 | 63.5703 | 64.0376 | 64.5049 | 64.9721 | 65.4394 | 65.9067 | 66.3739 | 66.8412 | 67.3085 | 67.7757 | 68.243 | 68.7103 | 69.1775 | 69.6448 | 70.1121 | 70.5793 | 71.0466 | 71.5139 | 71.9811 | 72.4484 | 72.9156 | 73.3829 | 73.8502 | 74.3174 | 74.7847 | 75.252 | 75.7192 | 76.1865 | 76.6538 | 77.121 | 77.5883 | 78.0556 | 78.5228 | 78.9901 | 79.4574 | 79.9246 | 80.3919 | 80.8592 | 81.3264 | 81.7937 | 82.261 | 82.7282 | 83.1955 | 83.6628 | 84.13 | 84.5973 | 85.0645 | 85.5318 | 85.9991 | 86.4663 | 86.9336 | 87.4009 | 87.8681 | 88.3354 | 88.8027 | 89.2699 | 89.7372 | 90.2045 | 90.6717 | 91.139 | 91.6063
Enersys Powersafe EON SBS 320 | 1.9886 | 1.9886 | 1.9886 | 1.9886 | 1.9886 | 1.9886 | 1.9886 | 1.9086 | 1.8686 | 1.9656 | 2.0625 | 2.2176 | 2.3726 | 2.5276 | 3.5289 | 4.5302 | 6.524 | 7.0205 | 7.517 | 8.0116 | 8.5061 | 8.9366 | 9.367 | 9.834 | 10.3009 | 10.7612 | 11.2215 | 11.7086 | 12.1958 | 12.6829 | 13.1701 | 13.6573 | 14.1444 | 14.6316 | 15.1187 | 15.6059 | 16.093 | 16.5802 | 17.0674 | 17.5545 | 18.0417 | 18.5288 | 19.016 | 19.5032 | 19.9903 | 20.4775 | 20.9646 | 21.4518 | 21.939 | 22.4261 | 22.9133 | 23.4004 | 23.8876 | 24.3747 | 24.8619 | 25.3491 | 25.8362 | 26.3234 | 26.8105 | 27.2977 | 27.7849 | 28.272 | 28.7592 | 29.2463 | 29.7335 | 30.2207 | 30.7078 | 31.195 | 31.6821 | 32.1693 | 32.6565 | 33.1436 | 33.6308 | 34.1179 | 34.6051 | 35.0922 | 35.5794 | 36.0666 | 36.5537 | 37.0409 | 37.528 | 38.0152 | 38.5024 | 38.9895 | 39.4767 | 39.9638 | 40.451 | 40.9382 | 41.4253 | 41.9125 | 42.3996 | 42.8868 | 43.3739 | 43.8611 | 44.3483 | 44.8354 | 45.3226 | 45.8097 | 46.2969 | 46.7841 | 47.2712 | 47.7584 | 48.2455 | 48.7327 | 49.2199 | 49.707 | 50.1942 | 50.6813 | 51.1685 | 51.6557 | 52.1428 | 52.63 | 53.1171 | 53.6043 | 54.0914 | 54.5786 | 55.0658 | 55.5529 | 56.0401 | 56.5272 | 57.0144 | 57.5016 | 57.9887 | 58.4759 | 58.963 | 59.4502 | 59.9374 | 60.4245 | 60.9117 | 61.3988 | 61.886 | 62.3731 | 62.8603 | 63.3475 | 63.8346 | 64.3218 | 64.8089 | 65.2961 | 65.7833 | 66.2704 | 66.7576 | 67.2447 | 67.7319 | 68.2191 | 68.7062 | 69.1934 | 69.6805 | 70.1677 | 70.6549 | 71.142 | 71.6292 | 72.1163 | 72.6035 | 73.0906 | 73.5778 | 74.065 | 74.5521 | 75.0393 | 75.5264 | 76.0136 | 76.5008 | 76.9879 | 77.4751 | 77.9622 | 78.4494 | 78.9366 | 79.4237 | 79.9109 | 80.398 | 80.8852 | 81.3724 | 81.8595 | 82.3467 | 82.8338 | 83.321 | 83.8081 | 84.2953 | 84.7825 | 85.2696 | 85.7568 | 86.2439 | 86.7311 | 87.2183 | 87.7054 | 88.1926 | 88.6797 | 89.1669 | 89.6541 | 90.1412 | 90.6284 | 91.1155 | 91.6027 | 92.0898 | 92.577 | 93.0642 | 93.5513 | 94.0385 | 94.5256 | 95.0128
Enersys Powersafe EON SBS 400 | 1.9888 | 1.9888 | 1.9888 | 1.9888 | 1.9888 | 1.9888 | 1.9888 | 1.9087 | 1.8688 | 1.9656 | 2.0623 | 2.2173 | 2.3723 | 2.5273 | 3.5282 | 4.5291 | 6.5264 | 7.0233 | 7.5202 | 8.0091 | 8.498 | 8.93 | 9.362 | 9.8345 | 10.307 | 10.7499 | 11.1928 | 11.6801 | 12.1674 | 12.6548 | 13.1421 | 13.6295 | 14.1168 | 14.6041 | 15.0915 | 15.5788 | 16.0662 | 16.5535 | 17.0408 | 17.5282 | 18.0155 | 18.5029 | 18.9902 | 19.4775 | 19.9649 | 20.4522 | 20.9396 | 21.4269 | 21.9142 | 22.4016 | 22.8889 | 23.3763 | 23.8636 | 24.3509 | 24.8383 | 25.3256 | 25.813 | 26.3003 | 26.7876 | 27.275 | 27.7623 | 28.2497 | 28.737 | 29.2243 | 29.7117 | 30.199 | 30.6864 | 31.1737 | 31.661 | 32.1484 | 32.6357 | 33.1231 | 33.6104 | 34.0977 | 34.5851 | 35.0724 | 35.5598 | 36.0471 | 36.5344 | 37.0218 | 37.5091 | 37.9965 | 38.4838 | 38.9711 | 39.4585 | 39.9458 | 40.4332 | 40.9205 | 41.4078 | 41.8952 | 42.3825 | 42.8699 | 43.3572 | 43.8445 | 44.3319 | 44.8192 | 45.3066 | 45.7939 | 46.2812 | 46.7686 | 47.2559 | 47.7433 | 48.2306 | 48.7179 | 49.2053 | 49.6926 | 50.18 | 50.6673 | 51.1546 | 51.642 | 52.1293 | 52.6167 | 53.104 | 53.5913 | 54.0787 | 54.566 | 55.0534 | 55.5407 | 56.028 | 56.5154 | 57.0027 | 57.4901 | 57.9774 | 58.4647 | 58.9521 | 59.4394 | 59.9268 | 60.4141 | 60.9014 | 61.3888 | 61.8761 | 62.3635 | 62.8508 | 63.3381 | 63.8255 | 64.3128 | 64.8002 | 65.2875 | 65.7748 | 66.2622 | 66.7495 | 67.2369 | 67.7242 | 68.2115 | 68.6989 | 69.1862 | 69.6736 | 70.1609 | 70.6482 | 71.1356 | 71.6229 | 72.1103 | 72.5976 | 73.0849 | 73.5723 | 74.0596 | 74.547 | 75.0343 | 75.5216 | 76.009 | 76.4963 | 76.9837 | 77.471 | 77.9583 | 78.4457 | 78.933 | 79.4204 | 79.9077 | 80.395 | 80.8824 | 81.3697 | 81.8571 | 82.3444 | 82.8318 | 83.3191 | 83.8064 | 84.2938 | 84.7811 | 85.2685 | 85.7558 | 86.2431 | 86.7305 | 87.2178 | 87.7052 | 88.1925 | 88.6798 | 89.1672 | 89.6545 | 90.1419 | 90.6292 | 91.1165 | 91.6039 | 92.0912 | 92.5786 | 93.0659 | 93.5532 | 94.0406 | 94.5279 | 95.0153
Enersys Powersafe EON SBS 410 | 0.64896 | 0.64896 | 0.64896 | 0.64896 | 0.64896 | 0.64896 | 0.64896 | 0.82711 | 1.0074 | 1.289 | 1.5707 | 1.7026 | 1.8346 | 1.9665 | 3.0919 | 4.2174 | 6.0512 | 6.9031 | 7.755 | 8.3329 | 8.9107 | 8.9359 | 8.9612 | 9.9291 | 10.897 | 11.0004 | 11.1038 | 11.7262 | 12.3486 | 12.971 | 13.5934 | 14.2158 | 14.8382 | 15.4606 | 16.083 | 16.7054 | 17.3278 | 17.9502 | 18.5726 | 19.195 | 19.8174 | 20.4398 | 21.0622 | 21.6846 | 22.307 | 22.9294 | 23.5518 | 24.1742 | 24.7966 | 25.419 | 26.0414 | 26.6638 | 27.2862 | 27.9086 | 28.531 | 29.1533 | 29.7757 | 30.3981 | 31.0205 | 31.6429 | 32.2653 | 32.8877 | 33.5101 | 34.1325 | 34.7549 | 35.3773 | 35.9997 | 36.6221 | 37.2445 | 37.8669 | 38.4893 | 39.1117 | 39.7341 | 40.3565 | 40.9789 | 41.6013 | 42.2237 | 42.8461 | 43.4685 | 44.0909 | 44.7133 | 45.3357 | 45.9581 | 46.5805 | 47.2029 | 47.8253 | 48.4477 | 49.0701 | 49.6925 | 50.3149 | 50.9373 | 51.5597 | 52.1821 | 52.8045 | 53.4269 | 54.0493 | 54.6717 | 55.2941 | 55.9165 | 56.5389 | 57.1613 | 57.7836 | 58.406 | 59.0284 | 59.6508 | 60.2732 | 60.8956 | 61.518 | 62.1404 | 62.7628 | 63.3852 | 64.0076 | 64.63 | 65.2524 | 65.8748 | 66.4972 | 67.1196 | 67.742 | 68.3644 | 68.9868 | 69.6092 | 70.2316 | 70.854 | 71.4764 | 72.0988 | 72.7212 | 73.3436 | 73.966 | 74.5884 | 75.2108 | 75.8332 | 76.4556 | 77.078 | 77.7004 | 78.3228 | 78.9452 | 79.5676 | 80.19 | 80.8124 | 81.4348 | 82.0572 | 82.6796 | 83.302 | 83.9244 | 84.5468 | 85.1692 | 85.7916 | 86.4139 | 87.0363 | 87.6587 | 88.2811 | 88.9035 | 89.5259 | 90.1483 | 90.7707 | 91.3931 | 92.0155 | 92.6379 | 93.2603 | 93.8827 | 94.5051 | 95.1275 | 95.7499 | 96.3723 | 96.9947 | 97.6171 | 98.2395 | 98.8619 | 99.4843 | 100.1067 | 100.7291 | 101.3515 | 101.9739 | 102.5963 | 103.2187 | 103.8411 | 104.4635 | 105.0859 | 105.7083 | 106.3307 | 106.9531 | 107.5755 | 108.1979 | 108.8203 | 109.4427 | 110.0651 | 110.6875 | 111.3099 | 111.9323 | 112.5547 | 113.1771 | 113.7995 | 114.4219 | 115.0442 | 115.6666 | 116.289 | 116.9114 | 117.5338 | 118.1562
Enersys Powersafe EON SBS 480 | 1.9883 | 1.9883 | 1.9883 | 1.9883 | 1.9883 | 1.9883 | 1.9883 | 1.9089 | 1.8689 | 1.9655 | 2.0622 | 2.2171 | 2.3721 | 2.527 | 3.5296 | 4.5322 | 6.52 | 7.0211 | 7.5223 | 8.0075 | 8.4926 | 8.9256 | 9.3587 | 9.8248 | 10.2909 | 10.7442 | 11.1975 | 11.6838 | 12.1701 | 12.6563 | 13.1426 | 13.6289 | 14.1151 | 14.6014 | 15.0877 | 15.5739 | 16.0602 | 16.5465 | 17.0327 | 17.519 | 18.0053 | 18.4915 | 18.9778 | 19.4641 | 19.9503 | 20.4366 | 20.9229 | 21.4091 | 21.8954 | 22.3817 | 22.8679 | 23.3542 | 23.8405 | 24.3267 | 24.813 | 25.2993 | 25.7855 | 26.2718 | 26.7581 | 27.2443 | 27.7306 | 28.2169 | 28.7031 | 29.1894 | 29.6757 | 30.1619 | 30.6482 | 31.1345 | 31.6208 | 32.107 | 32.5933 | 33.0796 | 33.5658 | 34.0521 | 34.5384 | 35.0246 | 35.5109 | 35.9972 | 36.4834 | 36.9697 | 37.456 | 37.9422 | 38.4285 | 38.9148 | 39.401 | 39.8873 | 40.3736 | 40.8598 | 41.3461 | 41.8324 | 42.3186 | 42.8049 | 43.2912 | 43.7774 | 44.2637 | 44.75 | 45.2362 | 45.7225 | 46.2088 | 46.695 | 47.1813 | 47.6676 | 48.1538 | 48.6401 | 49.1264 | 49.6126 | 50.0989 | 50.5852 | 51.0714 | 51.5577 | 52.044 | 52.5302 | 53.0165 | 53.5028 | 53.989 | 54.4753 | 54.9616 | 55.4478 | 55.9341 | 56.4204 | 56.9066 | 57.3929 | 57.8792 | 58.3654 | 58.8517 | 59.338 | 59.8242 | 60.3105 | 60.7968 | 61.2831 | 61.7693 | 62.2556 | 62.7419 | 63.2281 | 63.7144 | 64.2007 | 64.6869 | 65.1732 | 65.6595 | 66.1457 | 66.632 | 67.1183 | 67.6045 | 68.0908 | 68.5771 | 69.0633 | 69.5496 | 70.0359 | 70.5221 | 71.0084 | 71.4947 | 71.9809 | 72.4672 | 72.9535 | 73.4397 | 73.926 | 74.4123 | 74.8985 | 75.3848 | 75.8711 | 76.3573 | 76.8436 | 77.3299 | 77.8161 | 78.3024 | 78.7887 | 79.2749 | 79.7612 | 80.2475 | 80.7337 | 81.22 | 81.7063 | 82.1925 | 82.6788 | 83.1651 | 83.6513 | 84.1376 | 84.6239 | 85.1101 | 85.5964 | 86.0827 | 86.5689 | 87.0552 | 87.5415 | 88.0277 | 88.514 | 89.0003 | 89.4865 | 89.9728 | 90.4591 | 90.9453 | 91.4316 | 91.9179 | 92.4042 | 92.8904 | 93.3767 | 93.863 | 94.3492 | 94.8355
Enersys Powersafe EON SBS 580 | 1.9884 | 1.9884 | 1.9884 | 1.9884 | 1.9884 | 1.9884 | 1.9884 | 1.9088 | 1.8689 | 1.9653 | 2.0617 | 2.217 | 2.3723 | 2.5275 | 3.5284 | 4.5293 | 6.5227 | 7.0212 | 7.5198 | 8.0108 | 8.5019 | 8.9254 | 9.3489 | 9.8255 | 10.302 | 10.7469 | 11.1918 | 11.6793 | 12.1669 | 12.6545 | 13.142 | 13.6296 | 14.1171 | 14.6047 | 15.0923 | 15.5798 | 16.0674 | 16.555 | 17.0425 | 17.5301 | 18.0176 | 18.5052 | 18.9928 | 19.4803 | 19.9679 | 20.4555 | 20.943 | 21.4306 | 21.9181 | 22.4057 | 22.8933 | 23.3808 | 23.8684 | 24.3559 | 24.8435 | 25.3311 | 25.8186 | 26.3062 | 26.7938 | 27.2813 | 27.7689 | 28.2564 | 28.744 | 29.2316 | 29.7191 | 30.2067 | 30.6943 | 31.1818 | 31.6694 | 32.1569 | 32.6445 | 33.1321 | 33.6196 | 34.1072 | 34.5948 | 35.0823 | 35.5699 | 36.0574 | 36.545 | 37.0326 | 37.5201 | 38.0077 | 38.4953 | 38.9828 | 39.4704 | 39.9579 | 40.4455 | 40.9331 | 41.4206 | 41.9082 | 42.3958 | 42.8833 | 43.3709 | 43.8584 | 44.346 | 44.8336 | 45.3211 | 45.8087 | 46.2962 | 46.7838 | 47.2714 | 47.7589 | 48.2465 | 48.7341 | 49.2216 | 49.7092 | 50.1967 | 50.6843 | 51.1719 | 51.6594 | 52.147 | 52.6346 | 53.1221 | 53.6097 | 54.0972 | 54.5848 | 55.0724 | 55.5599 | 56.0475 | 56.5351 | 57.0226 | 57.5102 | 57.9977 | 58.4853 | 58.9729 | 59.4604 | 59.948 | 60.4356 | 60.9231 | 61.4107 | 61.8982 | 62.3858 | 62.8734 | 63.3609 | 63.8485 | 64.3361 | 64.8236 | 65.3112 | 65.7987 | 66.2863 | 66.7739 | 67.2614 | 67.749 | 68.2365 | 68.7241 | 69.2117 | 69.6992 | 70.1868 | 70.6744 | 71.1619 | 71.6495 | 72.137 | 72.6246 | 73.1122 | 73.5997 | 74.0873 | 74.5749 | 75.0624 | 75.55 | 76.0375 | 76.5251 | 77.0127 | 77.5002 | 77.9878 | 78.4754 | 78.9629 | 79.4505 | 79.938 | 80.4256 | 80.9132 | 81.4007 | 81.8883 | 82.3759 | 82.8634 | 83.351 | 83.8385 | 84.3261 | 84.8137 | 85.3012 | 85.7888 | 86.2764 | 86.7639 | 87.2515 | 87.739 | 88.2266 | 88.7142 | 89.2017 | 89.6893 | 90.1768 | 90.6644 | 91.152 | 91.6395 | 92.1271 | 92.6147 | 93.1022 | 93.5898 | 94.0773 | 94.5649 | 95.0525
Enersys Powersafe EON SBS 680 | 1.9884 | 1.9884 | 1.9884 | 1.9884 | 1.9884 | 1.9884 | 1.9884 | 1.9084 | 1.8689 | 1.9654 | 2.062 | 2.217 | 2.3721 | 2.5271 | 3.5285 | 4.5299 | 6.519 | 7.0185 | 7.518 | 8.0085 | 8.4989 | 8.9264 | 9.3538 | 9.8247 | 10.2956 | 10.7417 | 11.1877 | 11.6732 | 12.1588 | 12.6443 | 13.1298 | 13.6154 | 14.1009 | 14.5864 | 15.072 | 15.5575 | 16.043 | 16.5286 | 17.0141 | 17.4996 | 17.9852 | 18.4707 | 18.9562 | 19.4418 | 19.9273 | 20.4129 | 20.8984 | 21.3839 | 21.8695 | 22.355 | 22.8405 | 23.3261 | 23.8116 | 24.2971 | 24.7827 | 25.2682 | 25.7537 | 26.2393 | 26.7248 | 27.2103 | 27.6959 | 28.1814 | 28.6669 | 29.1525 | 29.638 | 30.1235 | 30.6091 | 31.0946 | 31.5801 | 32.0657 | 32.5512 | 33.0367 | 33.5223 | 34.0078 | 34.4933 | 34.9789 | 35.4644 | 35.9499 | 36.4355 | 36.921 | 37.4065 | 37.8921 | 38.3776 | 38.8631 | 39.3487 | 39.8342 | 40.3197 | 40.8053 | 41.2908 | 41.7763 | 42.2619 | 42.7474 | 43.2329 | 43.7185 | 44.204 | 44.6895 | 45.1751 | 45.6606 | 46.1461 | 46.6317 | 47.1172 | 47.6027 | 48.0883 | 48.5738 | 49.0594 | 49.5449 | 50.0304 | 50.516 | 51.0015 | 51.487 | 51.9726 | 52.4581 | 52.9436 | 53.4292 | 53.9147 | 54.4002 | 54.8858 | 55.3713 | 55.8568 | 56.3424 | 56.8279 | 57.3134 | 57.799 | 58.2845 | 58.77 | 59.2556 | 59.7411 | 60.2266 | 60.7122 | 61.1977 | 61.6832 | 62.1688 | 62.6543 | 63.1398 | 63.6254 | 64.1109 | 64.5964 | 65.082 | 65.5675 | 66.053 | 66.5386 | 67.0241 | 67.5096 | 67.9952 | 68.4807 | 68.9662 | 69.4518 | 69.9373 | 70.4228 | 70.9084 | 71.3939 | 71.8794 | 72.365 | 72.8505 | 73.336 | 73.8216 | 74.3071 | 74.7926 | 75.2782 | 75.7637 | 76.2492 | 76.7348 | 77.2203 | 77.7059 | 78.1914 | 78.6769 | 79.1625 | 79.648 | 80.1335 | 80.6191 | 81.1046 | 81.5901 | 82.0757 | 82.5612 | 83.0467 | 83.5323 | 84.0178 | 84.5033 | 84.9889 | 85.4744 | 85.9599 | 86.4455 | 86.931 | 87.4165 | 87.9021 | 88.3876 | 88.8731 | 89.3587 | 89.8442 | 90.3297 | 90.8153 | 91.3008 | 91.7863 | 92.2719 | 92.7574 | 93.2429 | 93.7285 | 94.214 | 94.6995
Enersys Powersafe EON SBS 780 | 1.9885 | 1.9885 | 1.9885 | 1.9885 | 1.9885 | 1.9885 | 1.9885 | 1.9084 | 1.8689 | 1.9653 | 2.0617 | 2.2169 | 2.3722 | 2.5275 | 3.5289 | 4.5304 | 6.5212 | 7.0189 | 7.5166 | 8.0067 | 8.4967 | 8.922 | 9.3472 | 9.819 | 10.2909 | 10.7451 | 11.1994 | 11.6852 | 12.1711 | 12.6569 | 13.1428 | 13.6286 | 14.1145 | 14.6003 | 15.0862 | 15.5721 | 16.0579 | 16.5438 | 17.0296 | 17.5155 | 18.0013 | 18.4872 | 18.973 | 19.4589 | 19.9448 | 20.4306 | 20.9165 | 21.4023 | 21.8882 | 22.374 | 22.8599 | 23.3457 | 23.8316 | 24.3174 | 24.8033 | 25.2892 | 25.775 | 26.2609 | 26.7467 | 27.2326 | 27.7184 | 28.2043 | 28.6901 | 29.176 | 29.6619 | 30.1477 | 30.6336 | 31.1194 | 31.6053 | 32.0911 | 32.577 | 33.0628 | 33.5487 | 34.0345 | 34.5204 | 35.0063 | 35.4921 | 35.978 | 36.4638 | 36.9497 | 37.4355 | 37.9214 | 38.4072 | 38.8931 | 39.3789 | 39.8648 | 40.3507 | 40.8365 | 41.3224 | 41.8082 | 42.2941 | 42.7799 | 43.2658 | 43.7516 | 44.2375 | 44.7234 | 45.2092 | 45.6951 | 46.1809 | 46.6668 | 47.1526 | 47.6385 | 48.1243 | 48.6102 | 49.096 | 49.5819 | 50.0678 | 50.5536 | 51.0395 | 51.5253 | 52.0112 | 52.497 | 52.9829 | 53.4687 | 53.9546 | 54.4404 | 54.9263 | 55.4122 | 55.898 | 56.3839 | 56.8697 | 57.3556 | 57.8414 | 58.3273 | 58.8131 | 59.299 | 59.7849 | 60.2707 | 60.7566 | 61.2424 | 61.7283 | 62.2141 | 62.7 | 63.1858 | 63.6717 | 64.1575 | 64.6434 | 65.1293 | 65.6151 | 66.101 | 66.5868 | 67.0727 | 67.5585 | 68.0444 | 68.5302 | 69.0161 | 69.5019 | 69.9878 | 70.4737 | 70.9595 | 71.4454 | 71.9312 | 72.4171 | 72.9029 | 73.3888 | 73.8746 | 74.3605 | 74.8464 | 75.3322 | 75.8181 | 76.3039 | 76.7898 | 77.2756 | 77.7615 | 78.2473 | 78.7332 | 79.219 | 79.7049 | 80.1908 | 80.6766 | 81.1625 | 81.6483 | 82.1342 | 82.62 | 83.1059 | 83.5917 | 84.0776 | 84.5634 | 85.0493 | 85.5352 | 86.021 | 86.5069 | 86.9927 | 87.4786 | 87.9644 | 88.4503 | 88.9361 | 89.422 | 89.9079 | 90.3937 | 90.8796 | 91.3654 | 91.8513 | 92.3371 | 92.823 | 93.3088 | 93.7947 | 94.2805 | 94.7664
Enersys Powersafe EON SBS 900 | 1.9885 | 1.9885 | 1.9885 | 1.9885 | 1.9885 | 1.9885 | 1.9885 | 1.9087 | 1.8688 | 1.966 | 2.0632 | 2.2184 | 2.3736 | 2.5288 | 3.5302 | 4.5316 | 6.5232 | 7.021 | 7.5188 | 8.0075 | 8.4962 | 8.9213 | 9.3465 | 9.8241 | 10.3016 | 10.752 | 11.2023 | 11.6875 | 12.1727 | 12.6579 | 13.1431 | 13.6283 | 14.1135 | 14.5987 | 15.0839 | 15.5691 | 16.0543 | 16.5395 | 17.0247 | 17.5098 | 17.995 | 18.4802 | 18.9654 | 19.4506 | 19.9358 | 20.421 | 20.9062 | 21.3914 | 21.8766 | 22.3618 | 22.847 | 23.3322 | 23.8174 | 24.3026 | 24.7878 | 25.273 | 25.7582 | 26.2434 | 26.7286 | 27.2138 | 27.699 | 28.1841 | 28.6693 | 29.1545 | 29.6397 | 30.1249 | 30.6101 | 31.0953 | 31.5805 | 32.0657 | 32.5509 | 33.0361 | 33.5213 | 34.0065 | 34.4917 | 34.9769 | 35.4621 | 35.9473 | 36.4325 | 36.9177 | 37.4029 | 37.8881 | 38.3733 | 38.8584 | 39.3436 | 39.8288 | 40.314 | 40.7992 | 41.2844 | 41.7696 | 42.2548 | 42.74 | 43.2252 | 43.7104 | 44.1956 | 44.6808 | 45.166 | 45.6512 | 46.1364 | 46.6216 | 47.1068 | 47.592 | 48.0772 | 48.5624 | 49.0475 | 49.5327 | 50.0179 | 50.5031 | 50.9883 | 51.4735 | 51.9587 | 52.4439 | 52.9291 | 53.4143 | 53.8995 | 54.3847 | 54.8699 | 55.3551 | 55.8403 | 56.3255 | 56.8107 | 57.2959 | 57.7811 | 58.2663 | 58.7515 | 59.2367 | 59.7218 | 60.207 | 60.6922 | 61.1774 | 61.6626 | 62.1478 | 62.633 | 63.1182 | 63.6034 | 64.0886 | 64.5738 | 65.059 | 65.5442 | 66.0294 | 66.5146 | 66.9998 | 67.485 | 67.9702 | 68.4554 | 68.9406 | 69.4258 | 69.911 | 70.3961 | 70.8813 | 71.3665 | 71.8517 | 72.3369 | 72.8221 | 73.3073 | 73.7925 | 74.2777 | 74.7629 | 75.2481 | 75.7333 | 76.2185 | 76.7037 | 77.1889 | 77.6741 | 78.1593 | 78.6445 | 79.1297 | 79.6149 | 80.1001 | 80.5853 | 81.0704 | 81.5556 | 82.0408 | 82.526 | 83.0112 | 83.4964 | 83.9816 | 84.4668 | 84.952 | 85.4372 | 85.9224 | 86.4076 | 86.8928 | 87.378 | 87.8632 | 88.3484 | 88.8336 | 89.3188 | 89.804 | 90.2892 | 90.7744 | 91.2596 | 91.7447 | 92.2299 | 92.7151 | 93.2003 | 93.6855 | 94.1707 | 94.6559
Enersys Powersafe EON SBS B14 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.54273 | 0.66074 | 0.82268 | 0.98462 | 1.2172 | 1.4497 | 1.6822 | 2.7289 | 3.7756 | 5.8594 | 6.3991 | 6.9388 | 7.4645 | 7.9902 | 8.4567 | 8.9233 | 9.4416 | 9.96 | 10.4504 | 10.9409 | 11.4421 | 11.9433 | 12.4444 | 12.9456 | 13.4468 | 13.948 | 14.4491 | 14.9503 | 15.4515 | 15.9527 | 16.4539 | 16.955 | 17.4562 | 17.9574 | 18.4586 | 18.9597 | 19.4609 | 19.9621 | 20.4633 | 20.9644 | 21.4656 | 21.9668 | 22.468 | 22.9691 | 23.4703 | 23.9715 | 24.4727 | 24.9738 | 25.475 | 25.9762 | 26.4774 | 26.9785 | 27.4797 | 27.9809 | 28.4821 | 28.9832 | 29.4844 | 29.9856 | 30.4868 | 30.9879 | 31.4891 | 31.9903 | 32.4915 | 32.9926 | 33.4938 | 33.995 | 34.4962 | 34.9973 | 35.4985 | 35.9997 | 36.5009 | 37.0021 | 37.5032 | 38.0044 | 38.5056 | 39.0068 | 39.5079 | 40.0091 | 40.5103 | 41.0115 | 41.5126 | 42.0138 | 42.515 | 43.0162 | 43.5173 | 44.0185 | 44.5197 | 45.0209 | 45.522 | 46.0232 | 46.5244 | 47.0256 | 47.5267 | 48.0279 | 48.5291 | 49.0303 | 49.5314 | 50.0326 | 50.5338 | 51.035 | 51.5361 | 52.0373 | 52.5385 | 53.0397 | 53.5408 | 54.042 | 54.5432 | 55.0444 | 55.5456 | 56.0467 | 56.5479 | 57.0491 | 57.5503 | 58.0514 | 58.5526 | 59.0538 | 59.555 | 60.0561 | 60.5573 | 61.0585 | 61.5597 | 62.0608 | 62.562 | 63.0632 | 63.5644 | 64.0655 | 64.5667 | 65.0679 | 65.5691 | 66.0702 | 66.5714 | 67.0726 | 67.5738 | 68.0749 | 68.5761 | 69.0773 | 69.5785 | 70.0796 | 70.5808 | 71.082 | 71.5832 | 72.0843 | 72.5855 | 73.0867 | 73.5879 | 74.089 | 74.5902 | 75.0914 | 75.5926 | 76.0938 | 76.5949 | 77.0961 | 77.5973 | 78.0985 | 78.5996 | 79.1008 | 79.602 | 80.1032 | 80.6043 | 81.1055 | 81.6067 | 82.1079 | 82.609 | 83.1102 | 83.6114 | 84.1126 | 84.6137 | 85.1149 | 85.6161 | 86.1173 | 86.6184 | 87.1196 | 87.6208 | 88.122 | 88.6231 | 89.1243 | 89.6255 | 90.1267 | 90.6278 | 91.129 | 91.6302 | 92.1314 | 92.6325 | 93.1337 | 93.6349 | 94.1361 | 94.6373 | 95.1384 | 95.6396 | 96.1408 | 96.642 | 97.1431
Enersys Powersafe EON SBS B14F | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.41899 | 0.54273 | 0.66074 | 0.82268 | 0.98462 | 1.2172 | 1.4497 | 1.6822 | 2.7289 | 3.7756 | 5.8594 | 6.3991 | 6.9388 | 7.4645 | 7.9902 | 8.4567 | 8.9233 | 9.4416 | 9.96 | 10.4504 | 10.9409 | 11.4421 | 11.9433 | 12.4444 | 12.9456 | 13.4468 | 13.948 | 14.4491 | 14.9503 | 15.4515 | 15.9527 | 16.4539 | 16.955 | 17.4562 | 17.9574 | 18.4586 | 18.9597 | 19.4609 | 19.9621 | 20.4633 | 20.9644 | 21.4656 | 21.9668 | 22.468 | 22.9691 | 23.4703 | 23.9715 | 24.4727 | 24.9738 | 25.475 | 25.9762 | 26.4774 | 26.9785 | 27.4797 | 27.9809 | 28.4821 | 28.9832 | 29.4844 | 29.9856 | 30.4868 | 30.9879 | 31.4891 | 31.9903 | 32.4915 | 32.9926 | 33.4938 | 33.995 | 34.4962 | 34.9973 | 35.4985 | 35.9997 | 36.5009 | 37.0021 | 37.5032 | 38.0044 | 38.5056 | 39.0068 | 39.5079 | 40.0091 | 40.5103 | 41.0115 | 41.5126 | 42.0138 | 42.515 | 43.0162 | 43.5173 | 44.0185 | 44.5197 | 45.0209 | 45.522 | 46.0232 | 46.5244 | 47.0256 | 47.5267 | 48.0279 | 48.5291 | 49.0303 | 49.5314 | 50.0326 | 50.5338 | 51.035 | 51.5361 | 52.0373 | 52.5385 | 53.0397 | 53.5408 | 54.042 | 54.5432 | 55.0444 | 55.5456 | 56.0467 | 56.5479 | 57.0491 | 57.5503 | 58.0514 | 58.5526 | 59.0538 | 59.555 | 60.0561 | 60.5573 | 61.0585 | 61.5597 | 62.0608 | 62.562 | 63.0632 | 63.5644 | 64.0655 | 64.5667 | 65.0679 | 65.5691 | 66.0702 | 66.5714 | 67.0726 | 67.5738 | 68.0749 | 68.5761 | 69.0773 | 69.5785 | 70.0796 | 70.5808 | 71.082 | 71.5832 | 72.0843 | 72.5855 | 73.0867 | 73.5879 | 74.089 | 74.5902 | 75.0914 | 75.5926 | 76.0938 | 76.5949 | 77.0961 | 77.5973 | 78.0985 | 78.5996 | 79.1008 | 79.602 | 80.1032 | 80.6043 | 81.1055 | 81.6067 | 82.1079 | 82.609 | 83.1102 | 83.6114 | 84.1126 | 84.6137 | 85.1149 | 85.6161 | 86.1173 | 86.6184 | 87.1196 | 87.6208 | 88.122 | 88.6231 | 89.1243 | 89.6255 | 90.1267 | 90.6278 | 91.129 | 91.6302 | 92.1314 | 92.6325 | 93.1337 | 93.6349 | 94.1361 | 94.6373 | 95.1384 | 95.6396 | 96.1408 | 96.642 | 97.1431
Enersys Powersafe EON SBS C11 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.62551 | 0.75627 | 0.93732 | 1.1184 | 1.3376 | 1.5568 | 1.776 | 2.9455 | 4.115 | 6.3147 | 6.8409 | 7.3671 | 7.8847 | 8.4022 | 8.7254 | 9.0486 | 9.5462 | 10.0439 | 10.5346 | 11.0253 | 11.4914 | 11.9575 | 12.4236 | 12.8897 | 13.3558 | 13.8219 | 14.288 | 14.7541 | 15.2202 | 15.6864 | 16.1525 | 16.6186 | 17.0847 | 17.5508 | 18.0169 | 18.483 | 18.9491 | 19.4152 | 19.8813 | 20.3474 | 20.8135 | 21.2797 | 21.7458 | 22.2119 | 22.678 | 23.1441 | 23.6102 | 24.0763 | 24.5424 | 25.0085 | 25.4746 | 25.9407 | 26.4069 | 26.873 | 27.3391 | 27.8052 | 28.2713 | 28.7374 | 29.2035 | 29.6696 | 30.1357 | 30.6018 | 31.0679 | 31.5341 | 32.0002 | 32.4663 | 32.9324 | 33.3985 | 33.8646 | 34.3307 | 34.7968 | 35.2629 | 35.729 | 36.1951 | 36.6612 | 37.1274 | 37.5935 | 38.0596 | 38.5257 | 38.9918 | 39.4579 | 39.924 | 40.3901 | 40.8562 | 41.3223 | 41.7884 | 42.2546 | 42.7207 | 43.1868 | 43.6529 | 44.119 | 44.5851 | 45.0512 | 45.5173 | 45.9834 | 46.4495 | 46.9156 | 47.3818 | 47.8479 | 48.314 | 48.7801 | 49.2462 | 49.7123 | 50.1784 | 50.6445 | 51.1106 | 51.5767 | 52.0428 | 52.5089 | 52.9751 | 53.4412 | 53.9073 | 54.3734 | 54.8395 | 55.3056 | 55.7717 | 56.2378 | 56.7039 | 57.17 | 57.6361 | 58.1023 | 58.5684 | 59.0345 | 59.5006 | 59.9667 | 60.4328 | 60.8989 | 61.365 | 61.8311 | 62.2972 | 62.7633 | 63.2294 | 63.6956 | 64.1617 | 64.6278 | 65.0939 | 65.56 | 66.0261 | 66.4922 | 66.9583 | 67.4244 | 67.8905 | 68.3566 | 68.8228 | 69.2889 | 69.755 | 70.2211 | 70.6872 | 71.1533 | 71.6194 | 72.0855 | 72.5516 | 73.0177 | 73.4838 | 73.95 | 74.4161 | 74.8822 | 75.3483 | 75.8144 | 76.2805 | 76.7466 | 77.2127 | 77.6788 | 78.1449 | 78.611 | 79.0771 | 79.5433 | 80.0094 | 80.4755 | 80.9416 | 81.4077 | 81.8738 | 82.3399 | 82.806 | 83.2721 | 83.7382 | 84.2043 | 84.6705 | 85.1366 | 85.6027 | 86.0688 | 86.5349 | 87.001 | 87.4671 | 87.9332 | 88.3993 | 88.8654 | 89.3315 | 89.7976 | 90.2638 | 90.7299 | 91.196
Enersys Powersafe EON SBS C11F | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.48355 | 0.62551 | 0.75627 | 0.93732 | 1.1184 | 1.3376 | 1.5568 | 1.776 | 2.9455 | 4.115 | 6.3147 | 6.8409 | 7.3671 | 7.8847 | 8.4022 | 8.7254 | 9.0486 | 9.5462 | 10.0439 | 10.5346 | 11.0253 | 11.4914 | 11.9575 | 12.4236 | 12.8897 | 13.3558 | 13.8219 | 14.288 | 14.7541 | 15.2202 | 15.6864 | 16.1525 | 16.6186 | 17.0847 | 17.5508 | 18.0169 | 18.483 | 18.9491 | 19.4152 | 19.8813 | 20.3474 | 20.8135 | 21.2797 | 21.7458 | 22.2119 | 22.678 | 23.1441 | 23.6102 | 24.0763 | 24.5424 | 25.0085 | 25.4746 | 25.9407 | 26.4069 | 26.873 | 27.3391 | 27.8052 | 28.2713 | 28.7374 | 29.2035 | 29.6696 | 30.1357 | 30.6018 | 31.0679 | 31.5341 | 32.0002 | 32.4663 | 32.9324 | 33.3985 | 33.8646 | 34.3307 | 34.7968 | 35.2629 | 35.729 | 36.1951 | 36.6612 | 37.1274 | 37.5935 | 38.0596 | 38.5257 | 38.9918 | 39.4579 | 39.924 | 40.3901 | 40.8562 | 41.3223 | 41.7884 | 42.2546 | 42.7207 | 43.1868 | 43.6529 | 44.119 | 44.5851 | 45.0512 | 45.5173 | 45.9834 | 46.4495 | 46.9156 | 47.3818 | 47.8479 | 48.314 | 48.7801 | 49.2462 | 49.7123 | 50.1784 | 50.6445 | 51.1106 | 51.5767 | 52.0428 | 52.5089 | 52.9751 | 53.4412 | 53.9073 | 54.3734 | 54.8395 | 55.3056 | 55.7717 | 56.2378 | 56.7039 | 57.17 | 57.6361 | 58.1023 | 58.5684 | 59.0345 | 59.5006 | 59.9667 | 60.4328 | 60.8989 | 61.365 | 61.8311 | 62.2972 | 62.7633 | 63.2294 | 63.6956 | 64.1617 | 64.6278 | 65.0939 | 65.56 | 66.0261 | 66.4922 | 66.9583 | 67.4244 | 67.8905 | 68.3566 | 68.8228 | 69.2889 | 69.755 | 70.2211 | 70.6872 | 71.1533 | 71.6194 | 72.0855 | 72.5516 | 73.0177 | 73.4838 | 73.95 | 74.4161 | 74.8822 | 75.3483 | 75.8144 | 76.2805 | 76.7466 | 77.2127 | 77.6788 | 78.1449 | 78.611 | 79.0771 | 79.5433 | 80.0094 | 80.4755 | 80.9416 | 81.4077 | 81.8738 | 82.3399 | 82.806 | 83.2721 | 83.7382 | 84.2043 | 84.6705 | 85.1366 | 85.6027 | 86.0688 | 86.5349 | 87.001 | 87.4671 | 87.9332 | 88.3993 | 88.8654 | 89.3315 | 89.7976 | 90.2638 | 90.7299 | 91.196

## Data_Enersys_VRLA (hidden)
Enersys Powersafe EON SBS 100 (12V)
Ref (Ah): | 100 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC) |  | 20oC Factor | 15oC Factor | 5oC Factor
0
0.083333 | 252.4 | 0.3962 | 0.43112 | 0.51926 |  | 1 | 0.919 | 0.763
0.16667 | 196 | 0.5102 | 0.54684 | 0.64177 |  | 1 | 0.933 | 0.795
0.25 | 161.4 | 0.61958 | 0.65913 | 0.76303 |  | 1 | 0.94 | 0.812
0.33333 | 138 | 0.72464 | 0.76762 | 0.87941 |  | 1 | 0.944 | 0.824
0.41667 | 120.5 | 0.82988 | 0.8754 | 0.99625 |  | 1 | 0.948 | 0.833
0.5 | 108.1 | 0.92507 | 0.97376 | 1.1013 |  | 1 | 0.95 | 0.84
0.58333 | 97.5 | 1.0256 | 1.0762 | 1.2138 |  | 1 | 0.953 | 0.845
0.66667 | 88.9 | 1.1249 | 1.1791 | 1.3234 |  | 1 | 0.954 | 0.85
0.75 | 82.5 | 1.2121 | 1.2679 | 1.4193 |  | 1 | 0.956 | 0.854
1 | 67.2 | 1.4881 | 1.5517 | 1.7243 |  | 1 | 0.959 | 0.863
2 | 39.4 | 2.5381 | 2.6247 | 2.8711 |  | 1 | 0.967 | 0.884
3 | 28.2 | 3.5461 | 3.6558 | 3.971 |  | 1 | 0.97 | 0.893
4 | 22.1 | 4.5249 | 4.6552 | 5.0277 |  | 1 | 0.972 | 0.9
5 | 18.2 | 5.4945 | 5.647 | 6.105 |  | 1 | 0.973 | 0.9
6 | 15.6 | 6.4103 | 6.5881 | 7.1225 |  | 1 | 0.973 | 0.9
7 | 13.7 | 7.2993 | 7.5018 | 8.1103 |  | 1 | 0.973 | 0.9
8 | 12 | 8.3333 | 8.547 | 9.1475 |  | 1 | 0.975 | 0.911
9 | 10.8 | 9.2593 | 9.4967 | 10.1638 |  | 1 | 0.975 | 0.911
10 | 9.86 | 10.142 | 10.3914 | 11.0963 |  | 1 | 0.976 | 0.914
20 | 5.29 | 18.9036 | 19.3684 | 20.6823 |  | 1 | 0.976 | 0.914
Enersys Powersafe EON SBS 100F (12V)
Ref (Ah): | 100 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 252.4 | 0.3962 | 0.43112 | 0.51926
0.16667 | 196 | 0.5102 | 0.54684 | 0.64177
0.25 | 161.4 | 0.61958 | 0.65913 | 0.76303
0.33333 | 138 | 0.72464 | 0.76762 | 0.87941
0.41667 | 120.5 | 0.82988 | 0.8754 | 0.99625
0.5 | 108.1 | 0.92507 | 0.97376 | 1.1013
0.58333 | 97.5 | 1.0256 | 1.0762 | 1.2138
0.66667 | 88.9 | 1.1249 | 1.1791 | 1.3234
0.75 | 82.5 | 1.2121 | 1.2679 | 1.4193
1 | 67.2 | 1.4881 | 1.5517 | 1.7243
2 | 39.4 | 2.5381 | 2.6247 | 2.8711
3 | 28.2 | 3.5461 | 3.6558 | 3.971
4 | 22.1 | 4.5249 | 4.6552 | 5.0277
5 | 18.2 | 5.4945 | 5.647 | 6.105
6 | 15.6 | 6.4103 | 6.5881 | 7.1225
7 | 13.7 | 7.2993 | 7.5018 | 8.1103
8 | 12 | 8.3333 | 8.547 | 9.1475
9 | 10.8 | 9.2593 | 9.4967 | 10.1638
10 | 9.86 | 10.142 | 10.3914 | 11.0963
20 | 5.29 | 18.9036 | 19.3684 | 20.6823
Enersys Powersafe EON SBS 170F (12V)
Ref (Ah): | 170 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 300.1 | 0.56648 | 0.61641 | 0.74243
0.16667 | 300.1 | 0.56648 | 0.60716 | 0.71255
0.25 | 253.3 | 0.67114 | 0.71398 | 0.82653
0.33333 | 221.2 | 0.76854 | 0.81413 | 0.93269
0.41667 | 194.4 | 0.87449 | 0.92245 | 1.0498
0.5 | 174.7 | 0.9731 | 1.0243 | 1.1584
0.58333 | 160.8 | 1.0572 | 1.1094 | 1.2511
0.66667 | 146.7 | 1.1588 | 1.2147 | 1.3633
0.75 | 135.6 | 1.2537 | 1.3114 | 1.468
1 | 110.7 | 1.5357 | 1.6013 | 1.7795
2 | 65.6 | 2.5915 | 2.6799 | 2.9315
3 | 47 | 3.617 | 3.7289 | 4.0504
4 | 36.8 | 4.6196 | 4.7526 | 5.1329
5 | 30.3 | 5.6106 | 5.7662 | 6.234
6 | 25.8 | 6.5891 | 6.772 | 7.3213
7 | 22.6 | 7.5221 | 7.7309 | 8.3579
8 | 20 | 8.5 | 8.7179 | 9.3304
9 | 18 | 9.4444 | 9.6866 | 10.3671
10 | 16.4 | 10.3659 | 10.6208 | 11.3412
20 | 8.94 | 19.0157 | 19.4833 | 20.8049
Enersys Powersafe EON SBS 190F (12V)
Ref (Ah): | 190 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 341.3 | 0.55669 | 0.60576 | 0.72961
0.16667 | 341.3 | 0.55669 | 0.59667 | 0.70025
0.25 | 286.9 | 0.66225 | 0.70452 | 0.81558
0.33333 | 248.5 | 0.76459 | 0.80994 | 0.9279
0.41667 | 219.5 | 0.8656 | 0.91308 | 1.0391
0.5 | 196.3 | 0.96791 | 1.0188 | 1.1523
0.58333 | 179.1 | 1.0609 | 1.1132 | 1.2555
0.66667 | 163.3 | 1.1635 | 1.2196 | 1.3688
0.75 | 150.9 | 1.2591 | 1.3171 | 1.4744
1 | 123.1 | 1.5435 | 1.6094 | 1.7885
2 | 73.2 | 2.5956 | 2.6842 | 2.9362
3 | 52.6 | 3.6122 | 3.7239 | 4.045
4 | 41.1 | 4.6229 | 4.756 | 5.1365
5 | 33.9 | 5.6047 | 5.7602 | 6.2275
6 | 28.9 | 6.5744 | 6.7568 | 7.3049
7 | 25.3 | 7.5099 | 7.7183 | 8.3443
8 | 22.5 | 8.4444 | 8.661 | 9.2694
9 | 20.3 | 9.3596 | 9.5996 | 10.274
10 | 18.5 | 10.2703 | 10.5228 | 11.2366
20 | 10.1 | 18.8119 | 19.2745 | 20.5819
Enersys Powersafe EON SBS 320 (2V)
Ref (Ah): | 320 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 210.9 | 1.5173 | 1.651 | 1.9886
0.16667 | 210.9 | 1.5173 | 1.6263 | 1.9086
0.25 | 210.9 | 1.5173 | 1.6142 | 1.8686
0.33333 | 202.2 | 1.5826 | 1.6765 | 1.9206
0.41667 | 193.2 | 1.6563 | 1.7472 | 1.9884
0.5 | 184.7 | 1.7325 | 1.8237 | 2.0625
0.58333 | 177.2 | 1.8059 | 1.8949 | 2.1371
0.66667 | 170.2 | 1.8801 | 1.9708 | 2.2119
0.75 | 163.6 | 1.956 | 2.046 | 2.2904
1 | 146.7 | 2.1813 | 2.2746 | 2.5276
2 | 102.9 | 3.1098 | 3.2159 | 3.5179
3 | 79.1 | 4.0455 | 4.1706 | 4.5302
4 | 64.5 | 4.9612 | 5.1042 | 5.5125
5 | 54.5 | 5.8716 | 6.0345 | 6.524
6 | 47.3 | 6.7653 | 6.9531 | 7.517
7 | 41.8 | 7.6555 | 7.8679 | 8.5061
8 | 37.5 | 8.5333 | 8.7521 | 9.367
9 | 34.1 | 9.3842 | 9.6248 | 10.3009
10 | 31.2 | 10.2564 | 10.5086 | 11.2215
20 | 16.7 | 19.1617 | 19.6329 | 20.9646
Enersys Powersafe EON SBS 400 (2V)
Ref (Ah): | 400 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 263.6 | 1.5175 | 1.6512 | 1.9888
0.16667 | 263.6 | 1.5175 | 1.6264 | 1.9087
0.25 | 263.6 | 1.5175 | 1.6143 | 1.8688
0.33333 | 252.7 | 1.5829 | 1.6768 | 1.921
0.41667 | 241.5 | 1.6563 | 1.7472 | 1.9884
0.5 | 230.9 | 1.7324 | 1.8235 | 2.0623
0.58333 | 221.5 | 1.8059 | 1.8949 | 2.1371
0.66667 | 212.8 | 1.8797 | 1.9703 | 2.2114
0.75 | 204.6 | 1.955 | 2.045 | 2.2893
1 | 183.4 | 2.181 | 2.2743 | 2.5273
2 | 128.6 | 3.1104 | 3.2166 | 3.5186
3 | 98.9 | 4.0445 | 4.1696 | 4.5291
4 | 80.6 | 4.9628 | 5.1057 | 5.5142
5 | 68.1 | 5.8737 | 6.0367 | 6.5264
6 | 59.1 | 6.7682 | 6.956 | 7.5202
7 | 52.3 | 7.6482 | 7.8604 | 8.498
8 | 46.9 | 8.5288 | 8.7475 | 9.362
9 | 42.6 | 9.3897 | 9.6304 | 10.307
10 | 39.1 | 10.2302 | 10.4817 | 11.1928
20 | 20.9 | 19.1388 | 19.6094 | 20.9396
Enersys Powersafe EON SBS 410 (2V)
Ref (Ah): | 409 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 826 | 0.49516 | 0.5388 | 0.64896
0.16667 | 622 | 0.65756 | 0.70478 | 0.82711
0.25 | 500 | 0.818 | 0.87021 | 1.0074
0.33333 | 413 | 0.99031 | 1.0491 | 1.2018
0.41667 | 357 | 1.1457 | 1.2085 | 1.3753
0.5 | 310 | 1.3194 | 1.3888 | 1.5707
0.58333 | 282 | 1.4504 | 1.5219 | 1.7164
0.66667 | 255 | 1.6039 | 1.6813 | 1.887
0.75 | 239 | 1.7113 | 1.7901 | 2.0039
1 | 241 | 1.6971 | 1.7697 | 1.9665
2 | 142 | 2.8803 | 2.9786 | 3.2582
3 | 108.6 | 3.7661 | 3.8826 | 4.2174
4 | 89 | 4.5955 | 4.7279 | 5.1061
5 | 75.1 | 5.4461 | 5.5972 | 6.0512
6 | 58.6 | 6.9795 | 7.1732 | 7.755
7 | 51 | 8.0196 | 8.2421 | 8.9107
8 | 50.1 | 8.1637 | 8.373 | 8.9612
9 | 41.2 | 9.9272 | 10.1817 | 10.897
10 | 40.3 | 10.1489 | 10.3984 | 11.1038
20 | 19 | 21.5263 | 22.0557 | 23.5518
Enersys Powersafe EON SBS 480 (2V)
Ref (Ah): | 480 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 316.4 | 1.5171 | 1.6508 | 1.9883
0.16667 | 316.3 | 1.5175 | 1.6265 | 1.9089
0.25 | 316.3 | 1.5175 | 1.6144 | 1.8689
0.33333 | 303.3 | 1.5826 | 1.6765 | 1.9206
0.41667 | 289.8 | 1.6563 | 1.7472 | 1.9884
0.5 | 277.1 | 1.7322 | 1.8234 | 2.0622
0.58333 | 265.8 | 1.8059 | 1.8949 | 2.1371
0.66667 | 255.3 | 1.8801 | 1.9708 | 2.2119
0.75 | 245.5 | 1.9552 | 2.0452 | 2.2895
1 | 220.1 | 2.1808 | 2.2741 | 2.527
2 | 154.3 | 3.1108 | 3.217 | 3.519
3 | 118.6 | 4.0472 | 4.1724 | 4.5322
4 | 96.7 | 4.9638 | 5.1068 | 5.5153
5 | 81.8 | 5.868 | 6.0308 | 6.52
6 | 70.9 | 6.7701 | 6.958 | 7.5223
7 | 62.8 | 7.6433 | 7.8554 | 8.4926
8 | 56.3 | 8.5258 | 8.7444 | 9.3587
9 | 51.2 | 9.375 | 9.6154 | 10.2909
10 | 46.9 | 10.2345 | 10.4862 | 11.1975
20 | 25.1 | 19.1235 | 19.5938 | 20.9229
Enersys Powersafe EON SBS 580 (2V)
Ref (Ah): | 580 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 382.3 | 1.5171 | 1.6509 | 1.9884
0.16667 | 382.2 | 1.5175 | 1.6265 | 1.9088
0.25 | 382.2 | 1.5175 | 1.6144 | 1.8689
0.33333 | 366.4 | 1.583 | 1.6769 | 1.9211
0.41667 | 350.2 | 1.6562 | 1.747 | 1.9882
0.5 | 334.9 | 1.7319 | 1.823 | 2.0617
0.58333 | 321.2 | 1.8057 | 1.8948 | 2.137
0.66667 | 308.6 | 1.8795 | 1.9701 | 2.2111
0.75 | 296.6 | 1.9555 | 2.0455 | 2.2898
1 | 265.9 | 2.1813 | 2.2745 | 2.5275
2 | 186.5 | 3.1099 | 3.216 | 3.518
3 | 143.4 | 4.0446 | 4.1697 | 4.5293
4 | 116.9 | 4.9615 | 5.1044 | 5.5128
5 | 98.8 | 5.8704 | 6.0333 | 6.5227
6 | 85.7 | 6.7678 | 6.9556 | 7.5198
7 | 75.8 | 7.6517 | 7.864 | 8.5019
8 | 68.1 | 8.5169 | 8.7353 | 9.3489
9 | 61.8 | 9.3851 | 9.6258 | 10.302
10 | 56.7 | 10.2293 | 10.4808 | 11.1918
20 | 30.3 | 19.1419 | 19.6126 | 20.943
Enersys Powersafe EON SBS 680 (2V)
Ref (Ah): | 680 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 448.2 | 1.5172 | 1.6509 | 1.9884
0.16667 | 448.2 | 1.5172 | 1.6261 | 1.9084
0.25 | 448.1 | 1.5175 | 1.6144 | 1.8689
0.33333 | 429.6 | 1.5829 | 1.6768 | 1.921
0.41667 | 410.6 | 1.6561 | 1.747 | 1.9881
0.5 | 392.6 | 1.732 | 1.8232 | 2.062
0.58333 | 376.6 | 1.8056 | 1.8947 | 2.1368
0.66667 | 361.8 | 1.8795 | 1.9701 | 2.2112
0.75 | 347.8 | 1.9551 | 2.0451 | 2.2894
1 | 311.8 | 2.1809 | 2.2741 | 2.5271
2 | 218.7 | 3.1093 | 3.2154 | 3.5173
3 | 168.1 | 4.0452 | 4.1703 | 4.5299
4 | 137.1 | 4.9599 | 5.1028 | 5.511
5 | 115.9 | 5.8671 | 6.0299 | 6.519
6 | 100.5 | 6.7662 | 6.9539 | 7.518
7 | 88.9 | 7.649 | 7.8613 | 8.4989
8 | 79.8 | 8.5213 | 8.7398 | 9.3538
9 | 72.5 | 9.3793 | 9.6198 | 10.2956
10 | 66.5 | 10.2256 | 10.477 | 11.1877
20 | 35.6 | 19.1011 | 19.5708 | 20.8984
Enersys Powersafe EON SBS 780 (2V)
Ref (Ah): | 780 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 514.1 | 1.5172 | 1.6509 | 1.9885
0.16667 | 514.1 | 1.5172 | 1.6262 | 1.9084
0.25 | 514 | 1.5175 | 1.6144 | 1.8689
0.33333 | 492.8 | 1.5828 | 1.6767 | 1.9209
0.41667 | 471 | 1.6561 | 1.7469 | 1.9881
0.5 | 450.4 | 1.7318 | 1.8229 | 2.0617
0.58333 | 432 | 1.8056 | 1.8946 | 2.1368
0.66667 | 415 | 1.8795 | 1.9701 | 2.2112
0.75 | 399 | 1.9549 | 2.0449 | 2.2891
1 | 357.6 | 2.1812 | 2.2745 | 2.5275
2 | 250.8 | 3.11 | 3.2162 | 3.5182
3 | 192.8 | 4.0456 | 4.1708 | 4.5304
4 | 157.2 | 4.9618 | 5.1048 | 5.5131
5 | 132.9 | 5.8691 | 6.0319 | 6.5212
6 | 115.3 | 6.765 | 6.9527 | 7.5166
7 | 102 | 7.6471 | 7.8593 | 8.4967
8 | 91.6 | 8.5153 | 8.7336 | 9.3472
9 | 83.2 | 9.375 | 9.6154 | 10.2909
10 | 76.2 | 10.2362 | 10.4879 | 11.1994
20 | 40.8 | 19.1176 | 19.5878 | 20.9165
Enersys Powersafe EON SBS 900 (2V)
Ref (Ah): | 900 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 593.2 | 1.5172 | 1.6509 | 1.9885
0.16667 | 593.1 | 1.5175 | 1.6264 | 1.9087
0.25 | 593.1 | 1.5175 | 1.6143 | 1.8688
0.33333 | 568.2 | 1.5839 | 1.6779 | 1.9223
0.41667 | 543.1 | 1.6572 | 1.7481 | 1.9894
0.5 | 519.3 | 1.7331 | 1.8243 | 2.0632
0.58333 | 498.1 | 1.8069 | 1.896 | 2.1383
0.66667 | 478.5 | 1.8809 | 1.9716 | 2.2128
0.75 | 460 | 1.9565 | 2.0466 | 2.291
1 | 412.4 | 2.1823 | 2.2756 | 2.5288
2 | 289.3 | 3.111 | 3.2171 | 3.5192
3 | 222.4 | 4.0468 | 4.1719 | 4.5316
4 | 181.4 | 4.9614 | 5.1043 | 5.5127
5 | 153.3 | 5.8708 | 6.0338 | 6.5232
6 | 133 | 6.7669 | 6.9547 | 7.5188
7 | 117.7 | 7.6466 | 7.8587 | 8.4962
8 | 105.7 | 8.5147 | 8.733 | 9.3465
9 | 95.9 | 9.3848 | 9.6254 | 10.3016
10 | 87.9 | 10.2389 | 10.4907 | 11.2023
20 | 47.1 | 19.1083 | 19.5782 | 20.9062
Enersys Powersafe EON SBS B14 (12V)
Ref (Ah): | 61.7 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 193 | 0.31969 | 0.34787 | 0.41899
0.16667 | 143 | 0.43147 | 0.46245 | 0.54273
0.25 | 115 | 0.53652 | 0.57077 | 0.66074
0.33333 | 97 | 0.63608 | 0.67382 | 0.77194
0.41667 | 84.2 | 0.73278 | 0.77297 | 0.87969
0.5 | 74.6 | 0.82708 | 0.87061 | 0.98462
0.58333 | 67.1 | 0.91952 | 0.96487 | 1.0882
0.66667 | 61.1 | 1.0098 | 1.0585 | 1.188
0.75 | 56.1 | 1.0998 | 1.1504 | 1.2878
1 | 42.5 | 1.4518 | 1.5138 | 1.6822
2 | 25.9 | 2.3822 | 2.4635 | 2.6948
3 | 18.3 | 3.3716 | 3.4759 | 3.7756
4 | 14.2 | 4.3451 | 4.4702 | 4.8279
5 | 11.7 | 5.2735 | 5.4198 | 5.8594
6 | 9.88 | 6.2449 | 6.4182 | 6.9388
7 | 8.58 | 7.1911 | 7.3907 | 7.9902
8 | 7.59 | 8.1291 | 8.3376 | 8.9233
9 | 6.8 | 9.0735 | 9.3062 | 9.96
10 | 6.17 | 10 | 10.2459 | 10.9409
20 | 3.22 | 19.1615 | 19.6327 | 20.9644
Enersys Powersafe EON SBS B14F (12V)
Ref (Ah): | 61.7 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 193 | 0.31969 | 0.34787 | 0.41899
0.16667 | 143 | 0.43147 | 0.46245 | 0.54273
0.25 | 115 | 0.53652 | 0.57077 | 0.66074
0.33333 | 97 | 0.63608 | 0.67382 | 0.77194
0.41667 | 84.2 | 0.73278 | 0.77297 | 0.87969
0.5 | 74.6 | 0.82708 | 0.87061 | 0.98462
0.58333 | 67.1 | 0.91952 | 0.96487 | 1.0882
0.66667 | 61.1 | 1.0098 | 1.0585 | 1.188
0.75 | 56.1 | 1.0998 | 1.1504 | 1.2878
1 | 42.5 | 1.4518 | 1.5138 | 1.6822
2 | 25.9 | 2.3822 | 2.4635 | 2.6948
3 | 18.3 | 3.3716 | 3.4759 | 3.7756
4 | 14.2 | 4.3451 | 4.4702 | 4.8279
5 | 11.7 | 5.2735 | 5.4198 | 5.8594
6 | 9.88 | 6.2449 | 6.4182 | 6.9388
7 | 8.58 | 7.1911 | 7.3907 | 7.9902
8 | 7.59 | 8.1291 | 8.3376 | 8.9233
9 | 6.8 | 9.0735 | 9.3062 | 9.96
10 | 6.17 | 10 | 10.2459 | 10.9409
20 | 3.22 | 19.1615 | 19.6327 | 20.9644
Enersys Powersafe EON SBS C11 (12V)
Ref (Ah): | 91.5 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 248 | 0.36895 | 0.40147 | 0.48355
0.16667 | 184 | 0.49728 | 0.53299 | 0.62551
0.25 | 149 | 0.61409 | 0.65329 | 0.75627
0.33333 | 126 | 0.72619 | 0.76927 | 0.8813
0.41667 | 110 | 0.83182 | 0.87745 | 0.99858
0.5 | 97.4 | 0.93943 | 0.98887 | 1.1184
0.58333 | 87.8 | 1.0421 | 1.0935 | 1.2333
0.66667 | 80.1 | 1.1423 | 1.1974 | 1.3439
0.75 | 73.7 | 1.2415 | 1.2987 | 1.4538
1 | 59.7 | 1.5327 | 1.5982 | 1.776
2 | 34.8 | 2.6293 | 2.719 | 2.9743
3 | 24.9 | 3.6747 | 3.7883 | 4.115
4 | 19.6 | 4.6684 | 4.8028 | 5.1871
5 | 16.1 | 5.6832 | 5.8409 | 6.3147
6 | 13.8 | 6.6304 | 6.8144 | 7.3671
7 | 12.1 | 7.562 | 7.7718 | 8.4022
8 | 11.1 | 8.2432 | 8.4546 | 9.0486
9 | 10 | 9.15 | 9.3846 | 10.0439
10 | 9.08 | 10.0771 | 10.3249 | 11.0253
20 | 4.92 | 18.5976 | 19.0549 | 20.3474
Enersys Powersafe EON SBS C11F (12V)
Ref (Ah): | 91.5 | Ref (DegC): | 20oC | Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC) | Kt (1.85V per cell 15oC) | Kt (1.85V per cell 5oC)
0
0.083333 | 248 | 0.36895 | 0.40147 | 0.48355
0.16667 | 184 | 0.49728 | 0.53299 | 0.62551
0.25 | 149 | 0.61409 | 0.65329 | 0.75627
0.33333 | 126 | 0.72619 | 0.76927 | 0.8813
0.41667 | 110 | 0.83182 | 0.87745 | 0.99858
0.5 | 97.4 | 0.93943 | 0.98887 | 1.1184
0.58333 | 87.8 | 1.0421 | 1.0935 | 1.2333
0.66667 | 80.1 | 1.1423 | 1.1974 | 1.3439
0.75 | 73.7 | 1.2415 | 1.2987 | 1.4538
1 | 59.7 | 1.5327 | 1.5982 | 1.776
2 | 34.8 | 2.6293 | 2.719 | 2.9743
3 | 24.9 | 3.6747 | 3.7883 | 4.115
4 | 19.6 | 4.6684 | 4.8028 | 5.1871
5 | 16.1 | 5.6832 | 5.8409 | 6.3147
6 | 13.8 | 6.6304 | 6.8144 | 7.3671
7 | 12.1 | 7.562 | 7.7718 | 8.4022
8 | 11.1 | 8.2432 | 8.4546 | 9.0486
9 | 10 | 9.15 | 9.3846 | 10.0439
10 | 9.08 | 10.0771 | 10.3249 | 11.0253
20 | 4.92 | 18.5976 | 19.0549 | 20.3474

## Calculations (hidden)
NOTE: Column A must be sorted in ascending order!
Monobloc Data |  | Duty Summary |  |  | IEEE 485 Calculation Method (Kt: 1.85V/Cell @ 20degC) | [6 empty] | Switchgear Tripping & Closing
Monobloc Types | Ah Capacity | Description | Current A1…A8 (amps) | Duration M1 ..M8 (hours) | Period | Load (A) | Change in Load (A) | Duration of Period (hours) | Time to end of section (hours) | Capacity Rating Factor Kt | Required Section Size (Ah) | Maximum Tripping Burden (Watts) | Maximum Tripping Duration (hours) | Maximum Closing Burden (Watts) | Maximum Closing Duration (Hours)
Enersys Powersafe EON SBS 170F | 170 | Period 1 | 1.0811 | 72 | Period 1 | [6 empty] | 0 | 0 | 0 | 0
Enersys Powersafe EON SBS B14F | 61.7 | Period 2 | 1.0811 | 0 | 1 | 1.0811 | 1.0811 | 72 | 72 | 66.8012 | 72.2176 | 0 | 0 | 0 | 0
Enersys Powersafe EON SBS C11F | 91.5 | Period 3 | 1.0811 | 0 | [5 empty] | Total (1) | 72.2176 | 0 | 0 | 0 | 0
Enersys Powersafe EON SBS 100 | 100 | Period 4 | 0 | 0 | Period 2 | [6 empty] | 0 | 0 | 0 | 0
Enersys Powersafe EON SBS 100F | 100 | Period 5 | 0 | 0 | 1 | 1.0811 | 1.0811 | 72 | 72 | 66.8012 | 72.2176
Enersys Powersafe EON SBS 170F | 170 | Period 6 | 0 | 0 | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
Enersys Powersafe EON SBS 190F | 190 | Period 7 | 0 | 0 | [5 empty] | Total (2) | 72.2176
Enersys Powersafe EON SBS 320 | 320 | Period 8 | 0 | 0 | Period 3
Enersys Powersafe EON SBS 400 | 400 |  |  |  | 1 | 1.0811 | 1.0811 | 72 | 72 | 66.8012 | 72.2176
Enersys Powersafe EON SBS 410 | 409 |  |  |  | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
Enersys Powersafe EON SBS 480 | 480 |  |  |  | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
Enersys Powersafe EON SBS 580 | 580 | [8 empty] | Total (3) | 72.2176
Enersys Powersafe EON SBS 680 | 680 |  |  |  | Period 4
Enersys Powersafe EON SBS 780 | 780 |  |  |  | 1 | 1.0811 | 1.0811 | 72 | 72 | 66.8012 | 72.2176
Enersys Powersafe EON SBS 900 | 900 |  |  |  | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
Enersys Powersafe EON SBS B14 | 61.7 |  |  |  | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
Enersys Powersafe EON SBS B14F | 61.7 |  |  |  | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
Enersys Powersafe EON SBS C11 | 91.5 | [8 empty] | Total (4) | 72.2176
Enersys Powersafe EON SBS C11F | 91.5 |  |  |  | Period 5
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 66.8012 | 72.2176
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (5) | 72.2176
Period 6
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 66.8012 | 72.2176
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (6) | 72.2176
Period 7
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 66.8012 | 72.2176
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (7) | 72.2176
Period 8
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 66.8012 | 72.2176
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 8 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (8) | 72.2176
IEEE 485 Calculation Method (Kt: 1.85V/Cell @ 15degC)
[5 empty] | Period | Load (A) | Change in Load (A) | Duration of Period (hours) | Time to end of section (hours) | Capacity Rating Factor Kt | Required Section Size (Ah)
Period 1
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 68.4439 | 73.9934
[10 empty] | Total (1) | 73.9934
Period 2
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 68.4439 | 73.9934
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (2) | 73.9934
Period 3
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 68.4439 | 73.9934
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (3) | 73.9934
Period 4
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 68.4439 | 73.9934
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (4) | 73.9934
Period 5
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 68.4439 | 73.9934
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (5) | 73.9934
Period 6
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 68.4439 | 73.9934
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (6) | 73.9934
Period 7
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 68.4439 | 73.9934
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (7) | 73.9934
Period 8
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 68.4439 | 73.9934
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 8 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (8) | 73.9934
IEEE 485 Calculation Method (Kt: 1.85V/Cell @ 5degC)
[5 empty] | Period | Load (A) | Change in Load (A) | Duration of Period (hours) | Time to end of section (hours) | Capacity Rating Factor Kt | Required Section Size (Ah)
Period 1
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 73.0867 | 79.0126
[10 empty] | Total (1) | 79.0126
Period 2
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 73.0867 | 79.0126
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (2) | 79.0126
Period 3
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 73.0867 | 79.0126
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (3) | 79.0126
Period 4
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 73.0867 | 79.0126
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (4) | 79.0126
Period 5
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 73.0867 | 79.0126
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (5) | 79.0126
Period 6
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 73.0867 | 79.0126
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (6) | 79.0126
Period 7
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 73.0867 | 79.0126
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (7) | 79.0126
Period 8
[5 empty] | 1 | 1.0811 | 1.0811 | 72 | 72 | 73.0867 | 79.0126
[5 empty] | 2 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 1.0811 | 0 | 0 | 0 | 0 | 0
[5 empty] | 8 | 1.0811 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (8) | 79.0126